## Sheet1 (hidden)
COMPARATIVE STATEMENT OF RATES FROM YEAR 2016-17 to 2017-18
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2016-17 | 2017-18 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
PART-I, 33 kV LINES AND D.P. STRUCTURES
(A) |  | 33 kV line on PCC Pole / H-Beam poles with Raccoon conductor.
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-1(i) | Per Km | 290208 | 294651 | 1.531
| ii | On H-Beam 152 x 152 mm 37.1 Kg/ Mtr 13 Mtr long | A-1(ii) | Per Km | 459820 | 457540 | -0.49585
| iii | On 365 Kg 11 Mtrs long PCC poles | A-1(iii) | Per Km | 332390 | 327410 | -1.4982
(B) |  | 33 kV Four Pole structure on PCC / H-Beam Pole | A-2 (A)
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-2 (A) (i) | Each | 234974 | 229401 | -2.3718
| ii | H-Beam Pole | A-2 (A) (ii) | Each | 292201 | 287977 | -1.4456
(C) |  | 33 kV DP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-2 (B)(i) | Each | 57588 | 54683 | -5.0445
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-2 (B)(ii) | Each | 88088 | 86977 | -1.2612
| iii | On 365 Kg 11 Mtrs long PCC poles | A-2 (B)(iii) | Each | 62662 | 61014 | -2.63
(D) |  | 33 kV line on PCC Pole / H-Beam Pole with Dog conductor.
| i | On 280 Kg, 9.1 Mtrs long PCC poles | A-3(i) | Per Km | 335828 | 346806 | 3.2689
| ii | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3(ii) | Per Km | 507332 | 509694 | 0.46557
| iii | On 365 Kg 11 Mtrs long PCC poles | A-3(iii) | Each | 378854 | 378457 | -0.10479
(E) |  | Augmentation of 1 km. of 33 kV line from Raccoon to Dog conductor. | A-3 (A) | Per Km | 217937 | 223794 | 2.6875
(F) |  | Additional (Mid Span) Pole for 33 kV Line | A-3 (B)
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3 (B)(i) | Per No. | 28510 | 28207 | -1.0628
(G) |  | 33 kV line on H-Beam supports suspension type with Panther Conductor (Maximum span of 50 Mtrs) | A-4
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-4 (i) | Per Km | 1418591 | 1401138 | -1.2303
(H) |  | 33 kV DP Structure on H-Beam supports with Panther Conductor | A-5
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-5 (i) | Each | 102479 | 101776 | -0.68599
(I) |  | 33 kV Under ground cable crossing under existing Railway track / Road for 60 Mtr long Corridor / route length of HDPE pipe under 2.5 M. deep for ground level single feeder line | A-6 | 60 Mtr
| a | Using HDD Technique
| i | With 3 core U/G XLPE 240 sqmm Cable | A-6(i) | 60 Mtr | 1036752 | 1078165 | 3.9945
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-6(ii) | 60 Mtr | 1158328 | 1200627 | 3.6517
| b | Using Pipe Pushing Method.
| i | With 3 core U/G XLPE 240 sqmm Cable | A-6(iii) | 60 Mtr | 2526667 | 2655984 | 5.1181
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-6(iv) | 60 Mtr | 2648242 | 2778446 | 4.9166
(J) |  | 33 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level single feeder line | A-6 (A) | 50 Mtr | 621183 | 622997 | 0.29202
(K) |  | Last span cabling of 33 kV H.T. Connection
|  | Using H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-7
| i | With 3x185 sq.mm AB XLPE Cable | A-7(i) | 50 Mtr | 181872 | 186985 | 2.8113
| ii | With 3x240 sq.mm AB XLPE Cable | A-7(ii) | 50 Mtr | 204432 | 209751 | 2.6018
(L) |  | 33 kV MEDP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-8 (i) | Each | 81715 | 79259 | -3.0056
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-8 (ii) | Each | 106547 | 106353 | -0.18208
(M) |  | Last span cabling of 33 kV line using Covered Conductor of size
| i | 70 sq.mm (207 Amp) | A-9 (i) | 50 Mtr | 124984 | 129377 | 3.5148
| ii | 99 sq.mm (258 Amp) | A-9 (ii) | 50 Mtr | 129998 | 134391 | 3.3793
(N) |  | Schedule for 33 kV Underground Cable crossing under Railway Track / Road for 60 Mtr. Long Corridor / Route Length of HDPE Pipe, under 2.5 Mtr. Deep from Ground Level Single Feeder Line Using Open Trench Method. | A-10 (i)
| i | With 3 core U/G XLPE 240 sqmm Cable | A-10(i) | 60 Mtr | 906066.3082 | 939768 | 3.7196
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-10(ii) | 60 Mtr | 1027642.0326 | 1062230 | 3.3658
Part-II, 33/11 kV SUB-STATIONS
(A) |  | New Sub-stations:
| i | 1.6 MVA, 33/11 kV S/s expandable to 2 x 1.6 MVA with control room | B-1(i) | Each | 6866103 | 6913029 | 0.68344
| ii | 3.15 MVA, 33/11 kV S/s expandable to 2 x 3.15 MVA with control room | B-1(ii) | Each | 8595749 | 8571098 | -0.28678
| iii | 5 MVA, 33/11 kV S/s expandable to 2 x 5 MVA with control room | B-1(iii) | Each | 10290155 | 10257514 | -0.31721
(B) |  | 33/11 kV Power Transformer
| i | 1.6 MVA | B-2(i) | Each | 933187 | 892025 | -4.4109
| ii | 3.15 MVA | B-2(ii) | Each | 2283793 | 2177129 | -4.6705
| iii | 5.0 MVA | B-2(iii) | Each | 3239383 | 3100279 | -4.2942
(C) |  | Installation of additional transformer for parallel operation with one additional bay on 11 kV side
| i | 1.6 MVA | B-3(i) | Each | 2893992 | 3379693 | 16.7831
| ii | 3.15 MVA | B-3(ii) | Each | 4572396 | 4999595 | 9.343
| iii | 5.0 MVA | B-3(iii) | Each | 5527838 | 5922555 | 7.1405
(D) |  | 11 kV Out door yard extension for additional bay with circuit breaker. | B-4 | Each | 483256 | 490515 | 1.5021
(E) |  | 33 kV Out door yard extension for additional bay without circuit breaker. | B-5 | Each | 212243 | 214257 | 0.94891
(F) |  | Installation of 33 kV VCB | B-6 | Each | 417910 | 418353 | 0.106
(G) |  | Augmentation of Power Transformer
| i | 1.6 to 3.15 MVA | B-8(i) | Each | 2660176 | 2562548 | -3.67
| ii | 3.15 to 5.0 MVA without 33 kV VCB | B-8(ii) | Each | 3251545 | 3113230 | -4.2538
| iii | 3.15 to 5.0 MVA with 33 kV VCB | B-8(iii) | Each | 3642023 | 3503832 | -3.7943
H) |  | Installation of 1.6 MVA 33/11 kV Sub-Station ON LINE | B-9 | Each | 1265650 | 1232202 | -2.6428
PART-III, 11 kV LINES AND D.P.STRUCTURES
(A) |  | 11 kV line on 140 Kg 8.0 Mtr long PCC poles with
| i | Rabbit conductor | C-1(I) | Per Km | 225086 | 224725 | -0.16038
| ii | Weasel conductor | C-1(II) | Per Km | 182425 | 183048 | 0.34151
(B) |  | 11 kV DP structure on 140 Kg, 8.0 Mtr long PCC poles | C-2 | Each | 35616 | 34966 | -1.825
PART-IV, 11 kV LINES AND D.P.STRUCTURES ON RAIL & H-BEAM
(A) |  | 11 kV line on H-Beam / PCC Pole with Rabbit conductor
| i | On H-Beam 11 meter long | C-3(i) | Per Km | 400368 | 394185 | -1.5443
| ii | On 365 Kg 11 Mtrs long PCC poles | C-3(ii) | Per Km | 284712 | 275498 | -3.2363
(B) | ii | Additional (Mid span) Poles for 11 kV Line on H-Beam | C-3 (A) | Per No. | 22159 | 21448 | -3.2086
(C) | iii | 11 kV Line on A.B.Cable | C-3 (B)
| a | Using H-Beam 152x152 mm, 37.1Kg/mtr 11 Mtrs long supports.
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[i] | Per Km | 1200223 | 1191557 | -0.72203
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[ii] | Per Km | 1335256 | 1328211 | -0.52761
| b | Using 200 Kg; 9.0 Mtr long PCC Pole
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[iii] | Per Km | 748914 | 772395 | 3.1353
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[iv] | Per Km | 883946 | 909049 | 2.8399
(D) | iv | Augmentation of 11 kV Line from Weasel to Raccoon Conductor | C-3 (C) | Per Km | 161933 | 165350 | 2.1101
(E) | v | Augmentation of 11 kV Line from Weasel to Rabbit Conductor | C-3 (D) | Per Km | 115754 | 118860 | 2.6833
(F) | vi | 11 kV Overhead XLPE Cable Line on H-Beam Pole with average span 30 Mtrs. | C-3 (E) | Per Km | 2396943 | 2430693 | 1.408
(G) |  | 11 kV DP structure on
| i | H-Beam 11 meter long | C-4(i) | Each | 67035 | 65741 | -1.9303
| ii | On 365 Kg 11 Mtrs long PCC poles | C-4(ii) | Each | 47583 | 45755 | -3.8417
(H) |  | 11 kV line on RS Joist (175X85 mm) 11.0 Meters long with
| i | Rabbit conductor | C-5(I) | Per Km | 300939 | 300432 | -0.16847
| ii | Weasel conductor | C-5(II) | Per Km | 260829 | 261456 | 0.24039
(I) |  | 11 kV DP structure on RS Joist 175X85 mm 11.0 Mtr. long | C-6 | Each | 50509 | 49946 | -1.1147
(J) |  | 11 kV line on PCC pole
| a | On 365 Kg 11 Mtrs long PCC poles
| i | Using Raccoon conductor | C-8(I) | Per Km | 327385 | 318489 | -2.7173
| ii | Using Dog conductor | C-8(II) | Per Km | 371815 | 366833 | -1.3399
(K) |  | 11 kV line on H-Beam (152x152 mm) 13 meter long with
| i | Raccoon conductor | C-9(I) | Per Km | 474359 | 468479 | -1.2396
| ii | Dog conductor | C-9(II) | Per Km | 518789 | 516824 | -0.37877
(L) |  | Additional (Mid Span) Poles for new 11 kV Line with Raccoon Conductor | C-9(A) | Per No. | 24793 | 24082 | -2.8677
(M) |  | 11 kV under ground cable crossing under railway track for 60 mtr length, under 2.5 mtr deep for ground level | C-12
| i | Using HDD Technique | C-12 (i) | 60 Mtr | 781977 | 819848 | 4.843
| ii | Using Pipe Pushing Method. | C-12 (ii) | 60 Mtr | 2271892 | 2397667 | 5.5361
(N) |  | 11 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level | C-12 (A) | 50 Mtr | 333362 | 334544 | 0.35457
(O) |  | Laying of 1 Km 11 kV Line using
| i | 3 Core 95 Sqmm underground cable | C-15(I) | Per Km | 926447 | 1061168 | 14.5417
| ii | 3 Core 240 Sqmm underground cable | C-15(II) | Per Km | 1407717 | 1555528 | 10.5001
| iii | 3 Core 400 Sqmm underground cable | C-15(III) | Per Km | 1982562 | 2146102 | 8.2489
(P) |  | D.T. Capacitors on existing DTR's (Retained & shifted) | C-16
| i | LT Capacitor for 25 kVA DT | C-16 (i) | Per No. | 1984 | 1984 | 0
| ii | LT Capacitor for 63 kVA DT | C-16 (ii) | Per No. | 3766 | 3766 | 0
| iii | LT Capacitor for 100 kVA DT | C-16 (iii) | Per No. | 4486 | 4486 | 0
| iv | LT Capacitor for 200 kVA DT | C-16 (iv) | Per No. | 4486 | 4486 | 0
| v | LT Capacitor for 315 kVA DT | C-16 (v) | Per No. | 4486 | 4486 | 0
(Q) |  | 11 kV MEDP Structure on H-Beam Pole
| i | 37.1 Kg /Mtrs 11 Mtrs long H-Beam supports | C-17 (i) | Each | 73838 | 72854 | -1.3326
(R) |  | New Automated 11 kV Capacitor Bank at 33/11 kV Sub-stations
| i | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. | C-18 (i) | Each | 1051129 | 1124599 | 6.9896
| ii | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . | C-18 (ii) | Each | 872674 | 946173 | 8.4223
(S) |  | Schedule for installation of compact R.M.U. 11 kV Class SF6 / VCB type (1 Incoming + 2 Breaker + 1 Outgoing) | C-19 | Each | 1166351 | 1166226 | -0.010717
(T) |  | Schedule for Chemical Earthing of Metering Equipment installed in the premises of HT consumers in normal / hard rock soil. | C-20 | Each | 12140 | 12854 | 5.8814
PART-V, 11/0.4 kV Transformer S/s.
A (A-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(I) | Each | 119446 | 113690 | -4.8189
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(II) | Each | 172454 | 169813 | -1.5314
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(III) | Each | 251071 | 241686 | -3.738
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(IV) | Each | 378952 | 373318 | -1.4867
(B-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(I) | Each | 143836 | 137866 | -4.1506
| ii | 63 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(II) | Each | 196844 | 193989 | -1.4504
| iii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11mtr long | C-7(B-1)(III) | Each | 250890 | 241328 | -3.8112
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(IV) | Each | 379297 | 373557 | -1.5133
(B-1) A |  | Relocation of 11/0.4 kV Out-door type Transformer Sub-station using H-Beam Pole and 3.5 Core PVC Cable [Based on Cost Schedule C-7 (B-1) except X-mer Cost]
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (I) | Each | 89146 | 86714 | -2.7281
| ii | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (II) | Each | 105263 | 103139 | -2.0178
| iii | 100 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (III) | Each | 123707 | 121207 | -2.0209
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr,11 mtr long | C-7(B-1) A (IV) | Each | 156292 | 153161 | -2.0033
(B-1) B |  | Renovation of Existing Distribution Transformer
| i | 25 kVA Transformer | C-7(B-1) B (I) | Each | 19827 | 22140 | 11.6659
| ii | 63 kVA Transformer | C-7(B-1) B (II) | Each | 35897 | 38302 | 6.6997
| iii | 100 kVA Transformer | C-7(B-1) B (III) | Each | 45084 | 47174 | 4.6358
| iv | 200 kVA Transformer | C-7(B-1) B (IV) | Each | 76498 | 77886 | 1.8144
| v | 315 kVA Transformer | C-7(B-1) B (V) | Each | 88994 | 90321 | 1.4911
(A-2) |  | 11/0.4 kV Out-door type Transformer sub-station using 1 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(I) | Each | 119679 | 113817 | -4.8981
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(II) | Each | 172408 | 169440 | -1.7215
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(III) | Each | 249131 | 240586 | -3.4299
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(IV) | Each | 368657 | 364826 | -1.0392
(B-2) | v | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(I) | Each | 144069 | 137992 | -4.2181
| vi | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(II) | Each | 196797 | 193616 | -1.6164
| vii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(III) | Each | 249394 | 240227 | -3.6757
| viii | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(IV) | Each | 369446 | 365065 | -1.1858
(B) |  | Augmentation of 11/.4 kV S/s capacity (Assuming 25 years of life & 10 years in service)
| i | 25 kVA to 63 kVA | C-10 (I) | Each | 130670 | 132602 | 1.4785
| ii | 63 kVA to 100 kVA | C-10 (II) | Each | 209641 | 208698 | -0.44982
| iii | 100 kVA to 200 kVA | C-10 (III) | Each | 339624 | 342792 | 0.9328
(C) | i | 11/.4 kV Out door Sub-station (16 kVA Transformer) | C-11 | Each | 115010 | 112364 | -2.3007
(D) |  | Single pole mounted low capacity Single phase / Three phase 11/.4 kV Distribution Transformer Sub-station
| i | 16 kVA Three phase | C-13(III) | Each | 92936 | 93434 | 0.53585
(E) |  | Plinth mounted 11/.4 kV Outdoor Sub-station
| i | 63 kVA Transformer | C-14(I) | Each | 223352 | 211937 | -5.1108
| ii | 100 kVA Transformer | C-14(II) | Each | 277122 | 258939 | -6.5614
| iii | 200 kVA Transformer | C-14(III) | Each | 427457 | 412870 | -3.4125
PART-VI, L.T. LINES
(A) |  | 3 phase, 5 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 4 Rabbit + 1 Squirrel | D-1(I) | Per Km | 265563 | 268958 | 1.2784
| ii | 3 Rabbit + 2 Squirrel | D-1(II) | Per Km | 245947 | 250089 | 1.6841
| iii | 4 Weasel + 1 Squirrel | D-1(III) | Per Km | 213106 | 218059 | 2.3242
| iv | 3 Weasel + 2 Squirrel | D-1(IV) | Per Km | 206605 | 211915 | 2.5701
| v | 5 Squirrel | D-1(V) | Per Km | 187100 | 193485 | 3.4126
(B) |  | 3 phase, 4 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 3 Rabbit + 1 Squirrel | D-2(I) | Per Km | 228470 | 231205 | 1.1971
| ii | 3 Weasel + 1 Squirrel | D-2(II) | Per Km | 189127 | 193031 | 2.0642
| iii | 4 Squirrel | D-2(III) | Per Km | 169622 | 174601 | 2.9354
(C) |  | 1 phase, 3 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-3(I) | Per Km | 177557 | 179745 | 1.2323
| ii | 2 Weasel + 1 Squirrel | D-3(II) | Per Km | 164442 | 167020 | 1.5677
| iii | 3 Squirrel | D-3(III) | Per Km | 151439 | 154733 | 2.1751
(D) |  | 3 Phase, 5 Wire LT line on 125 x 70 mm, 9.3 Mtrs long R.S. Joist with 3 Rabbit & 2 Weasel conductors (Span upto 45 Meters) | D-4(I) | Per Km | 362955 | 360452 | -0.68962
(E) |  | 3 Phase, 5 Wire LT line on 175 x 85 mm, 9.3 Mtrs long R.S. Joist with 3 Raccoon & 2 Weasel conductors (Span upto 65 Meters) | D-4(II) | Per Km | 395690 | 395890 | 0.050545
(F) |  | 1 Phase, 3 Wire LT line on 9.3 Mtrs long 125x70 mm R.S. Joist with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-5(I) | Per Km | 261626 | 254915 | -2.5651
| ii | 2 Weasel + 1 Squirrel | D-5(II) | Per Km | 248512 | 242190 | -2.5439
| iii | 3 Squirrel | D-5(III) | Per Km | 235509 | 229904 | -2.38
(G) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (i) | Per Km | 339492 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (ii) | Per Km | 273723 | 264172 | -3.4893
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (iii) | Per Km | 461479 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (iv) | Per Km | 395711 | 387798 | -1.9997
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (v) | Per Km | 589306 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (vi) | Per Km | 523537 | 510840 | -2.4252
(H ) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (i) | Per Km | 433821 | 369101 | -14.9186 | Cable rate reduced by 23%
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| ii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (ii) | Per Km | 556663 | 493582 | -11.332
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| iii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (iii) | Per Km | 684490 | 616623 | -9.915
(I) |  | 1 phase 3 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x25+1x16+1x25 sq.mm. | D-6 [3] | Per Km | 245263 | 239794 | -2.2299
(J) |  | 3 phase 4 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 3x16+1x25 sq.mm. | D-6 [4] | Per Km | 280146 | 274079 | -2.1657
(K) |  | 3 phase 5 Wire L.T. Line on R.S.Joist (175x85) mm, 9.3 Mtr. Long (By replacement of existing bare LT conductor) for Urban area using AB XLPE Cable of size
| i | 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6(A) (i) | Per Km | 273057 | DELETED
(L) |  | Additional pole of R.S. Joist (125x70) mm (Mid span) for L.T.Line with A.B.Cable. | D-6(B) | Per No. | 9780 | 9209 | -5.8384
(M) |  | HVDS system of 200 kVA parent DTR taking 4 KM LT to be converted | D-7 | 4 Km | 1917922 | 1945906 | 1.4591
(N) |  | HVDS system of 100 kVA parent DTR taking 3 KM LT to be converted | D-8 | 3Km | 960861 | 935426 | -2.6471
(O) |  | HVDS system of 63 kVA parent DTR taking 2 KM LT to be converted | D-9 | 2Km | 692611 | 676802 | -2.2825
(P) |  | Conversion of 1 Km LT line into 11 kV line | D-10 | Per Km | 78149 | 76543 | -2.055
(Q) |  | LT line conversion using Rabbit conductor maximum span of 45 mtrs
| i | 1 phase 2 wire to 1 phase 3 wire conversion | D-11(I) |  | 66251 | 68984 | 4.1252
| ii | 1 phase 2 wire to 3 phase 4 wire conversion | D-11(II) |  | 106799 | 110491 | 3.457
| iii | 1 phase 3 wire to 3 phase 4 wire conversion | D-11(III) |  | 68889 | 71635 | 3.9861
| iv | 1 phase 3 wire to 3 phase 5 wire conversion | D-11(IV) |  | 109350 | 113054 | 3.3873
(R) |  | Conversion of 1 Km 1 Phase 3 wire LT line into 11 kV line | D-12 | Per Km | 194760 | 197052 | 1.1768
(S) |  | Conversion of 1 Km 3 Phase 5 wire LT line into 11 kV line | D-13 | Per Km | 220985 | 223565 | 1.1675
(T) |  | Distribution Box on existing LT Lines for Service Connections.
| i | Single phase Distn. Box for 09 Connections | D-14 (i) | Per No. | 1350 | 1091 | -19.1852
| ii | Three phase Distn. Box for 05 Connections | D-14 (ii) | Per No. | 1577 | 1295 | -17.8821
(U) |  | 1 phase 2 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x16+1x25 sq.mm. | D-15 | Per Km | 253584 | DELETED
PART-VII, METERING
(A) |  | Metering of 11/0.4 kV Distribution X'mer
| i | 25 kVA Transformer | E-1(I) | Each | 8957 | 9574 | 6.8885
| ii | 63 kVA Transformer | E-1(II) | Each | 8957 | 9574 | 6.8885
| iii | 100 kVA Transformer | E-1(III) | Each | 8957 | 9574 | 6.8885
| iv | 200 kVA Transformer | E-1(IV) | Each | 8678 | 9282 | 6.9601
Meter modernisation- Replacing the existing meters with electronic meters which are highly capable of improving billing efficiency.
(B) | i | Cost of meter replacement of single phase consumer along with shifting of meter outside the premises. | E-2 | Each
| i | With Armoured service cable | E-2(i) | Each | 2629 | 2653 | 0.91289
| ii | With Unarmoured service cable | E-2(ii) | Each | 2335 | 2359 | 1.0278
(C) | ii | Cost of meter replacement of three phase consumer along with shifting of meter outside the premises. | E-3 | Each
| i | With Armoured service cable | E-3(i) | Each | 4947 | 5011 | 1.2937
| ii | With Unarmoured service cable | E-3(ii) | Each | 4718 | 4782 | 1.3565
(D) | iii | Cost of meter replacement of three phase consumer CT Operated meter along with shifting of meter outside the premises. | E-4 | Each | 2600 | 2618 | 0.69231
(E) | iv | Meter shifting of Single phase consumer to outside of premises with New Service Cable. | E-5 | Each
| i | With Armoured service cable | E-5(i) | Each | 1649 | 1673 | 1.4554
| ii | With Unarmoured service cable | E-5(ii) | Each | 1355 | 1379 | 1.7712
(F) | v | Meter shifting of Three phase consumer to outside of premises with New Service Cable. | E-6 | Each
| i | With Armoured service cable | E-6(i) | Each | 2767 | 2831 | 2.313
| ii | With Unarmoured service cable | E-6(ii) | Each | 2538 | 2602 | 2.5217
[5 empty] | Total Hike in % |  | 0.1

## COMPARATIVE
COMPARATIVE STATEMENT OF RATES FROM YEAR 2017-18 (REVISED) to 2018-19
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2017-18 (REV.) | 2018-19 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
PART-I, 33 kV LINES AND D.P. STRUCTURES
(A) |  | 33 kV line on PCC Pole / H-Beam poles with Raccoon conductor.
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-1(i) | Per Km | 308267 | 356392 | 15.6115
| ii | On H-Beam 152 x 152 mm 37.1 Kg/ Mtr 13 Mtr long | A-1(ii) | Per Km | 469985 | 579006 | 23.1967
| iii | On 365 Kg 11 Mtrs long PCC poles | A-1(iii) | Per Km | 345596 | 409377 | 18.4554
(B) |  | 33 kV Four Pole structure on PCC / H-Beam Pole | A-2 (A)
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-2 (A) (i) | Each | 240386 | 252957 | 5.2295
| ii | H-Beam Pole | A-2 (A) (ii) | Each | 297180 | 334277 | 12.483
(C) |  | 33 kV DP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-2 (B)(i) | Each | 59412 | 62901 | 5.8726
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-2 (B)(ii) | Each | 91312 | 106979 | 17.1577
| iii | On 365 Kg 11 Mtrs long PCC poles | A-2 (B)(iii) | Each | 66598 | 73218 | 9.9402
(D) |  | 33 kV line on PCC Pole / H-Beam Pole with Dog conductor.
| i | On 280 Kg, 9.1 Mtrs long PCC poles | A-3(i) | Per Km | 359934 | 416152 | 15.619
| ii | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3(ii) | Per Km | 521652 | 638767 | 22.4508
| iii | On 365 Kg 11 Mtrs long PCC poles | A-3(iii) | Each | 395864 | 467735 | 18.1555
(E) |  | Augmentation of 1 km. of 33 kV line from Raccoon to Dog conductor. | A-3 (A) | Per Km | 225507 | 263370 | 16.7902
(F) |  | Additional (Mid Span) Pole for 33 kV Line | A-3 (B)
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3 (B)(i) | Per No. | 29224 | 37059 | 26.8102
(G) |  | 33 kV line on H-Beam supports suspension type with Panther Conductor (Maximum span of 50 Mtrs) | A-4
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-4 (i) | Per Km | 1449447 | 1688417 | 16.487
(H) |  | 33 kV DP Structure on H-Beam supports with Panther Conductor | A-5
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-5 (i) | Each | 106516 | 121424 | 13.996
(I) |  | 33 kV Under ground cable crossing under existing Railway track / Road for 60 Mtr long Corridor / route length of HDPE pipe under 2.5 M. deep for ground level single feeder line | A-6 | 60 Mtr
| a | Using HDD Technique for Railway works with 3 core U/G XLPE 400 sqmm Cable | A-6(i) | 60 Mtr | 1358206 | 1320891 | -2.7474
| b | Using HDD Technique for Road crossing works with 3 core U/G XLPE 400 sqmm Cable | A-6(ii) | 60 Mtr |  | 1293641
(J) |  | 33 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level single feeder line | A-6 (A) | 50 Mtr | 622997 |  |  | DELETED
(K) |  | Last span cabling of 33 kV H.T. Connection
|  | Using H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-7
| i | With 3x185 sq.mm AB XLPE Cable | A-7(i) | 50 Mtr | 207261 | 215630 | 4.0379
| ii | With 3x240 sq.mm AB XLPE Cable | A-7(ii) | 50 Mtr | 232184 | 240307 | 3.4985
(L) |  | 33 kV MEDP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-8 (i) | Each | 84636 | 91528 | 8.1431
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-8 (ii) | Each | 110994 | 129728 | 16.8784
(M) |  | Last span cabling of 33 kV line using Covered Conductor of size
| i | 70 sq.mm (207 Amp) | A-9 (i) | 50 Mtr | 142427 | 151464 | 6.345
| ii | 99 sq.mm (258 Amp) | A-9 (ii) | 50 Mtr | 147625 | 156662 | 6.1216
(N) |  | Schedule for 33 kV Underground Cable crossing under Railway Track / Road for 60 Mtr. Long Corridor / Route Length of HDPE Pipe, under 2.5 Mtr. Deep from Ground Level Single Feeder Line Using Open Trench Method. | A-10 (i)
| i | With 3 core U/G XLPE 240 sqmm Cable | A-10(i) | 60 Mtr | 1049506 | 1031650 | -1.7014
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-10(ii) | 60 Mtr | 1181362 | 1144048 | -3.1586
(O) |  | Schedule for laying of 1 km. 33 kV Cable Direct in Ground Single Cable Line using Open Trench Method. | A-11 |  |  |  |  | NEW ADDED
| i | With 3 core U/G XLPE 240 sqmm Cable | A-11(i) | Per Km |  | 3708835
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-11(ii) | Per Km |  | 3955051
Part-II, 33/11 kV SUB-STATIONS
(A) |  | New Sub-stations:
| i | 1.6 MVA, 33/11 kV S/s expandable to 2 x 1.6 MVA with control room | B-1(i) | Each | 7089743 | 7310256 | 3.1103
| ii | 3.15 MVA, 33/11 kV S/s expandable to 2 x 3.15 MVA with control room | B-1(ii) | Each | 8789227 | 9318229 | 6.0188
| iii | 5 MVA, 33/11 kV S/s expandable to 2 x 5 MVA with control room | B-1(iii) | Each | 10519397 | 11163138 | 6.1196
(B) |  | 33/11 kV Power Transformer
| i | 1.6 MVA | B-2(i) | Each | 929777 | 919511 | -1.1041
| ii | 3.15 MVA | B-2(ii) | Each | 2237843 | 2532958 | 13.1875
| iii | 5.0 MVA | B-2(iii) | Each | 3179964 | 3558199 | 11.8943
(C) |  | Installation of additional transformer for parallel operation with one additional bay on 11 kV side
| i | 1.6 MVA | B-3(i) | Each | 3521311 | 3709955 | 5.3572
| ii | 3.15 MVA | B-3(ii) | Each | 5177819 | 5676488 | 9.6309
| iii | 5.0 MVA | B-3(iii) | Each | 6119750 | 6701535 | 9.5067
(D) |  | 11 kV Out door yard extension for additional bay with circuit breaker. | B-4 | Each | 515204 | 562251 | 9.1317
(E) |  | 33 kV Out door yard extension for additional bay without circuit breaker. | B-5 | Each | 223704 | 235119 | 5.1027
(F) |  | Installation of 33 kV VCB | B-6 | Each | 440153 | 446574 | 1.4588
(G) |  | Augmentation of Power Transformer
| i | 1.6 to 3.15 MVA | B-8(i) | Each | 2639542 | 2942211 | 11.4667
| ii | 3.15 to 5.0 MVA without 33 kV VCB | B-8(ii) | Each | 3192109 | 3569910 | 11.8355
| iii | 3.15 to 5.0 MVA with 33 kV VCB | B-8(iii) | Each | 3600669 | 3985388 | 10.6847
H) |  | Installation of 1.6 MVA 33/11 kV Sub-Station ON LINE | B-9 | Each | 1283689 | 1316266 | 2.5378
PART-III, 11 kV LINES AND D.P.STRUCTURES
(A) |  | 11 kV line on 140 Kg 8.0 Mtr long PCC poles with
| i | Rabbit conductor | C-1(I) | Per Km | 237891 | 270023 | 13.507
| ii | Weasel conductor | C-1(II) | Per Km | 196040 | 220616 | 12.5362
(B) |  | 11 kV DP structure on 140 Kg, 8.0 Mtr long PCC poles | C-2 | Each | 38386 | 41094 | 7.0547
PART-IV, 11 kV LINES AND D.P.STRUCTURES ON RAIL & H-BEAM
(A) |  | 11 kV line on H-Beam / PCC Pole with Rabbit conductor
| i | On H-Beam 11 meter long | C-3(i) | Per Km | 408116 | 506596 | 24.1304
| ii | On 365 Kg 11 Mtrs long PCC poles | C-3(ii) | Per Km | 297532 | 355149 | 19.365
(B) | ii | Additional (Mid span) Poles for 11 kV Line on H-Beam | C-3 (A) | Per No. | 22252 | 28746 | 29.1839
(C) | iii | 11 kV Line on A.B.Cable | C-3 (B)
| a | Using H-Beam 152x152 mm, 37.1Kg/mtr 11 Mtrs long supports.
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[i] | Per Km | 1281996 | 1459762 | 13.8663
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[ii] | Per Km | 1434429 | 1610262 | 12.258
| b | Using 200 Kg; 9.0 Mtr long PCC Pole
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[iii] | Per Km | 863200 | 882525 | 2.2388
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[iv] | Per Km | 1015632 | 1033025 | 1.7125
(D) | iv | Augmentation of 11 kV Line from Weasel to Raccoon Conductor | C-3 (C) | Per Km | 166702 | 195588 | 17.3279
(E) | v | Augmentation of 11 kV Line from Weasel to Rabbit Conductor | C-3 (D) | Per Km | 120871 | 140589 | 16.3133
(F) | vi | 11 kV Overhead XLPE Cable Line on H-Beam Pole with average span 30 Mtrs. | C-3 (E) | Per Km | 2652028 | 3222793 | 21.5218
(G) |  | 11 kV DP structure on
| i | H-Beam 11 meter long | C-4(i) | Each | 69176 | 83694 | 20.987
| ii | On 365 Kg 11 Mtrs long PCC poles | C-4(ii) | Each | 50558 | 58219 | 15.1529
(H) |  | 11 kV line on RS Joist (175X85 mm) 11.0 Meters long with
| i | Rabbit conductor | C-5(I) | Per Km | 316496 | 372572 | 17.7178
| ii | Weasel conductor | C-5(II) | Per Km | 279145 | 326617 | 17.0062
(I) |  | 11 kV DP structure on RS Joist 175X85 mm 11.0 Mtr. long | C-6 | Each | 53737 | 61153 | 13.8005
(J) |  | 11 kV line on PCC pole
| a | On 365 Kg 11 Mtrs long PCC poles
| i | Using Raccoon conductor | C-8(I) | Per Km | 339818 | 405877 | 19.4395
| ii | Using Dog conductor | C-8(II) | Per Km | 387603 | 461671 | 19.1092
(K) |  | 11 kV line on H-Beam (152x152 mm) 13 meter long with
| i | Raccoon conductor | C-9(I) | Per Km | 481367 | 602016 | 25.0638
| ii | Dog conductor | C-9(II) | Per Km | 529152 | 657810 | 24.314
(L) |  | Additional (Mid Span) Poles for new 11 kV Line with Raccoon Conductor | C-9(A) | Per No. | 24867 | 32500 | 30.6953
(M) |  | 11 kV under ground cable crossing under existing Railway track / Road for 60 mtr long Rail / Road corridor route length of HDPE pipe, under 2.5 mtr deep for ground level single feeder line | C-12
| a | Using HDD Technique for Railway works on 3x240 sqmm. U/G XLPE Cable | C-12 (i) | 60 Mtr | 944173 | 970821 | 2.8224
| b | Using HDD Technique for Road crossing works on 3x240 sqmm. U/G XLPE Cable | C-12 (ii) | 60 Mtr |  | 943571
(N) |  | 11 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level | C-12 (A) | 50 Mtr | 334544 |  |  | DELETED
(O) |  | Laying of 1 Km 11 kV Cable direct in ground single cable Line using open trench method
| i | 3 Core 95 Sqmm underground cable | C-15(I) | Per Km | 1216051 | 1470358 | 20.9125
| ii | 3 Core 240 Sqmm underground cable | C-15(II) | Per Km | 1766837 | 1972972 | 11.6669
(P) |  | D.T. Capacitors on existing DTR's (Retained & shifted) | C-16
| i | LT Capacitor for 25 kVA DT | C-16 (i) | Per No. | 2034 | 1902 | -6.4897
| ii | LT Capacitor for 63 kVA DT | C-16 (ii) | Per No. | 3868 | 3603 | -6.8511
| iii | LT Capacitor for 100 kVA DT | C-16 (iii) | Per No. | 4607 | 4289 | -6.9025
| iv | LT Capacitor for 200 kVA DT | C-16 (iv) | Per No. | 4607 | 4289 | -6.9025
| v | LT Capacitor for 315 kVA DT | C-16 (v) | Per No. | 4607 | 4289 | -6.9025
(Q) |  | 11 kV MEDP Structure on H-Beam Pole
| i | 37.1 Kg /Mtrs 11 Mtrs long H-Beam supports | C-17 (i) | Each | 76456 | 91101 | 19.1548
(R) |  | New Automated 11 kV Capacitor Bank at 33/11 kV Sub-stations
| i | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. | C-18 (i) | Each | 1165109 | 1162470 | -0.2265
| ii | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . | C-18 (ii) | Each | 981157 | 976669 | -0.45742
(S) |  | Schedule for installation of compact R.M.U. 11 kV Class SF6 / VCB type (1 Incoming + 2 Breaker + 1 Outgoing) | C-19 | Each | 1201305 | 1201222 | -0.0069092
(T) |  | Schedule for Chemical Earthing of Metering Equipment installed in the premises of HT consumers in normal / hard rock soil. | C-20 | Each | 12614 | 12703 | 0.70557
PART-V, 11/0.4 kV Transformer S/s.
A (A-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(I) | Each | 122057 | 128546 | 5.3164
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(II) | Each | 179594 | 192886 | 7.4011
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(III) | Each | 252605 | 276788 | 9.5734
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(IV) | Each | 389069 | 423998 | 8.9776
(B-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(I) | Each | 145284 | 162958 | 12.1651
| ii | 63 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(II) | Each | 202821 | 227299 | 12.0688
| iii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11mtr long | C-7(B-1)(III) | Each | 251484 | 277302 | 10.2663
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(IV) | Each | 388348 | 425192 | 9.4874
(B-1) A |  | Relocation of 11/0.4 kV Out-door type Transformer Sub-station using H-Beam Pole and 3.5 Core PVC Cable [Based on Cost Schedule C-7 (B-1) except X-mer Cost]
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (I) | Each | 92936 | 109049 | 17.3377
| ii | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (II) | Each | 109779 | 130057 | 18.4717
| iii | 100 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (III) | Each | 128809 | 149338 | 15.9376
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr,11 mtr long | C-7(B-1) A (IV) | Each | 162999 | 184572 | 13.2351
(B-1) B |  | Renovation of Existing Distribution Transformer
| i | 25 kVA Transformer | C-7(B-1) B (I) | Each | 25627 | 28748 | 12.1786
| ii | 63 kVA Transformer | C-7(B-1) B (II) | Each | 42396 | 46852 | 10.5104
| iii | 100 kVA Transformer | C-7(B-1) B (III) | Each | 52257 | 57469 | 9.9738
| iv | 200 kVA Transformer | C-7(B-1) B (IV) | Each | 85139 | 91200 | 7.1189
| v | 315 kVA Transformer | C-7(B-1) B (V) | Each | 97926 | 85285 | -12.9087
(A-2) |  | 11/0.4 kV Out-door type Transformer sub-station using 1 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(I) | Each | 122180 | 128546 | 5.2103
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(II) | Each | 179145 | 189669 | 5.8746
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(III) | Each | 251513 | 272534 | 8.3578
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(IV) | Each | 379506 | 412495 | 8.6926
(B-2) | v | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(I) | Each | 145406 | 162958 | 12.071
| vi | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(II) | Each | 202372 | 224082 | 10.7278
| vii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(III) | Each | 250195 | 273048 | 9.1341
| viii | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(IV) | Each | 378784 | 413689 | 9.215
(B) |  | Augmentation of 11/.4 kV S/s capacity (Assuming 25 years of life & 10 years in service)
| i | 25 kVA to 63 kVA | C-10 (I) | Each | 139938 | 145726 | 4.1361
| ii | 63 kVA to 100 kVA | C-10 (II) | Each | 218812 | 237080 | 8.3487
| iii | 100 kVA to 200 kVA | C-10 (III) | Each | 356753 | 386625 | 8.3733
(C) | i | 11/.4 kV Out door Sub-station (16 kVA Transformer) | C-11 | Each | 120833 | 127611 | 5.6094
(D) |  | Single pole mounted low capacity Single phase / Three phase 11/.4 kV Distribution Transformer Sub-station
| i | 16 kVA Three phase | C-13(III) | Each | 98430 | 105348 | 7.0283
(E) |  | Plinth mounted 11/.4 kV Outdoor Sub-station
| i | 63 kVA Transformer | C-14(I) | Each | 226361 | 242860 | 7.2888
| ii | 100 kVA Transformer | C-14(II) | Each | 274879 | 291894 | 6.19
| iii | 200 kVA Transformer | C-14(III) | Each | 432920 | 470402 | 8.658
PART-VI, L.T. LINES
(A) |  | 3 phase, 5 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 4 Rabbit + 1 Squirrel | D-1(I) | Per Km | 284622 | 324077 | 13.8622
| ii | 3 Rabbit + 2 Squirrel | D-1(II) | Per Km | 266104 | 301755 | 13.3974
| iii | 4 Weasel + 1 Squirrel | D-1(III) | Per Km | 236132 | 264152 | 11.8662
| iv | 3 Weasel + 2 Squirrel | D-1(IV) | Per Km | 229736 | 256812 | 11.7857
| v | 5 Squirrel | D-1(V) | Per Km | 210548 | 234790 | 11.5138
(B) |  | 3 phase, 4 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 3 Rabbit + 1 Squirrel | D-2(I) | Per Km | 246745 | 279348 | 13.2132
| ii | 3 Weasel + 1 Squirrel | D-2(II) | Per Km | 210378 | 234404 | 11.4204
| iii | 4 Squirrel | D-2(III) | Per Km | 191189 | 212383 | 11.0854
(C) |  | 1 phase, 3 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-3(I) | Per Km | 195596 | 218482 | 11.7006
| ii | 2 Weasel + 1 Squirrel | D-3(II) | Per Km | 183473 | 203501 | 10.916
| iii | 3 Squirrel | D-3(III) | Per Km | 170681 | 188820 | 10.6274
(D) |  | 3 Phase, 5 Wire LT line on 125 x 70 mm, 9.3 Mtrs long R.S. Joist with 3 Rabbit & 2 Weasel conductors (Span upto 45 Meters) | D-4(I) | Per Km | 382008 | 442164 | 15.7473
(E) |  | 3 Phase, 5 Wire LT line on 175 x 85 mm, 9.3 Mtrs long R.S. Joist with 3 Raccoon & 2 Weasel conductors (Span upto 65 Meters) | D-4(II) | Per Km | 413371 | 486295 | 17.6413
(F) |  | 1 Phase, 3 Wire LT line on 9.3 Mtrs long 125x70 mm R.S. Joist with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-5(I) | Per Km | 271949 | 316232 | 16.2836
| ii | 2 Weasel + 1 Squirrel | D-5(II) | Per Km | 259826 | 301250 | 15.943
| iii | 3 Squirrel | D-5(III) | Per Km | 247034 | 286569 | 16.0039
(G) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (ii) | Per Km | 297908 | 308175 | 3.4464
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (iv) | Per Km | 425372 | 471253 | 10.7861
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (vi) | Per Km | 545616 | 648023 | 18.7691
(H ) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (i) | Per Km | 413905 | 403041 | -2.6248
3 phase line on RS Joist 175x85 mm, 19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| ii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (ii) | Per Km | 542253 | 567003 | 4.5643
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| iii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (iii) | Per Km | 662497 | 743772 | 12.268
(I) |  | 1 phase 3 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x25+1x16+1x25 sq.mm. | D-6 [3] | Per Km | 270604 | 261809 | -3.2501
(J) |  | 3 phase 4 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 3x16+1x25 sq.mm. | D-6 [4] | Per Km | 307454 | 318657 | 3.6438
(K) |  | Additional pole of R.S. Joist (125x70) mm (Mid span) for L.T.Line with A.B.Cable. | D-6(B) | Per No. | 10023 | 11371 | 13.4491
(L) |  | HVDS system of 200 kVA parent DTR taking 4 KM LT to be converted | D-7 | 4 Km | 2090145 | 2087220 | -0.13994
(M) |  | HVDS system of 100 kVA parent DTR taking 3 KM LT to be converted | D-8 | 3Km | 996839 | 1039387 | 4.2683
(N) |  | HVDS system of 63 kVA parent DTR taking 2 KM LT to be converted | D-9 | 2Km | 721953 | 755719 | 4.677
(O) |  | Conversion of 1 Km LT line into 11 kV line | D-10 | Per Km | 85217 | 91372 | 7.2227
(P) |  | LT line conversion using Rabbit conductor maximum span of 45 mtrs
| i | 1 phase 2 wire to 1 phase 3 wire conversion | D-11(I) |  | 71465 | 81667 | 14.2755
| ii | 1 phase 2 wire to 3 phase 4 wire conversion | D-11(II) |  | 113743 | 130893 | 15.0779
| iii | 1 phase 3 wire to 3 phase 4 wire conversion | D-11(III) |  | 74124 | 84886 | 14.5189
| iv | 1 phase 3 wire to 3 phase 5 wire conversion | D-11(IV) |  | 116312 | 134009 | 15.2151
(Q) |  | Conversion of 1 Km 1 Phase 3 wire LT line into 11 kV line | D-12 | Per Km | 213524 | 233577 | 9.3915
(R) |  | Conversion of 1 Km 3 Phase 5 wire LT line into 11 kV line | D-13 | Per Km | 240485 | 265819 | 10.5345
(S) |  | Distribution Box on existing LT Lines for Service Connections.
| i | Single phase Distn. Box for 09 Connections | D-14 (i) | Per No. | 1146 | 1215 | 6.0209
| ii | Three phase Distn. Box for 05 Connections | D-14 (ii) | Per No. | 1353 | 1436 | 6.1345
PART-VII, METERING
(A) |  | Metering of 11/0.4 kV Distribution X'mer
| i | 25 kVA Transformer | E-1(I) | Each | 9893 | 9457 | -4.4072
| ii | 63 kVA Transformer | E-1(II) | Each | 9893 | 9457 | -4.4072
| iii | 100 kVA Transformer | E-1(III) | Each | 9893 | 9457 | -4.4072
| iv | 200 kVA Transformer | E-1(IV) | Each | 9593 | 9157 | -4.545
Meter modernisation- Replacing the existing meters with electronic meters which are highly capable of improving billing efficiency.
(B) | i | Cost of meter replacement of single phase consumer along with shifting of meter outside the premises. | E-2 | Each
| i | With Armoured service cable | E-2(i) | Each | 2908 | 2642 | -9.1472
| ii | With Unarmoured service cable | E-2(ii) | Each | 2503 | 2316 | -7.471
(C) | ii | Cost of meter replacement of three phase consumer along with shifting of meter outside the premises. | E-3 | Each
| i | With Armoured service cable | E-3(i) | Each | 5435 | 4927 | -9.3468
| ii | With Unarmoured service cable | E-3(ii) | Each | 5176 | 4672 | -9.7372
(D) | iii | Cost of meter replacement of three phase consumer CT Operated meter along with shifting of meter outside the premises. | E-4 | Each | 2747 | 2283 | -16.8912
(E) | iv | Meter shifting of Single phase consumer to outside of premises with New Service Cable. | E-5 | Each
| i | With Armoured service cable | E-5(i) | Each | 1910 | 1884 | -1.3613
| ii | With Unarmoured service cable | E-5(ii) | Each | 1504 | 1558 | 3.5904
(F) | v | Meter shifting of Three phase consumer to outside of premises with New Service Cable. | E-6 | Each
| i | With Armoured service cable | E-6(i) | Each | 3212 | 3160 | -1.6189
| ii | With Unarmoured service cable | E-6(ii) | Each | 2953 | 2904 | -1.6593

## SOR RATE
RATE OF STOCK MATERIALS IN SoR OF 2018-19
| RATE OF ALL MATERIALS AR INCLUSIVE OF G.S.T. UNLESS MENTIONED SPECIFICALLY IN REMARKS COLUMN | [5 empty] | Updated SoR 2017-18 | Value
Material Code | Description | Unit | Unit rate for 2018-19 | SAP DESCRIPTION | REMARKS |  | Material Code | Value
7130200201 | 1:1.5:3 Ratio | Cmt | 3298 |  |  | Earlier Total cost consisted of material and labour as a whole, now only material cost (excluding labour & G.S.T.) is taken.
7130200202 | 1:3:6 Ratio | Cmt | 2510.8 |  | * | Earlier Total cost consisted of material and labour as a whole, now only material cost (excluding labour & G.S.T.) is taken.
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 176.87 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 240.64 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Each | 33
7130210809 | Aluminium Paint | Ltr. | 327.94 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 251.07
7130211158 | Red Oxide Paint | Ltr. | 146.77 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 155833.08 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5 | ISI MARK
7130310007 | 70 Sqmm. | Km. | 50410.97 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V | ISI MARK
7130310008 | 120 Sqmm. | Km. | 90389.05 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100 | ISI MARK
7130310020 | 3x400 Sq.mm. | km | 2150624.22 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 28156.59 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V | ISI MARK
7130310022 | 50 Sqmm. | Km. | 36754.4 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V | ISI MARK
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 70032.16 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM | ISI MARK
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 76711.73 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM | ISI MARK
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 88905.8 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM | ISI MARK
7130310038 | 2.5 Sqmm. | Per Mtr. | 6.89 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 29.08 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 60.26 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 102715.58 | 11KV PVC INSULATED 150SQMM SINGLE CORE X | ISI MARK
7130310042 | 16.0 Sqmm. | km | 39339.51 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 55892.5 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310048 | 25 Sq.mm. | Mtr. | 88826.17
7130310049 | 120 Sq.mm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310050 | 400 Sqmm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310051 | 3x95 Sq.mm. | km | 920903.65 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1130461.76
7130310053 | 3x185 Sq.mm. | km | 1292072.61 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 1643003.83 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 17826.52
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 25466.45
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 314067.63 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 444325.88
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 664391.87
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 626686.74
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 3890.71 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 4094.35 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 41184.18 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 112761 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM | ISI MARK
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 123896.74 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 50684.56 | LT AB CABLEB 3X16+1X25 SQMM | ISI MARK
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 57407.11 | LT AB CABLEB 3X25+1X25 SQMM | ISI MARK
7130310075 | 3x240 Sq.mm. | km | 1967969.25 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 525190.66
7130310077 | 95 Sq.mm | km | 531363.19 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 792369.6 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 960042.67 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 1479179.02 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310652 | 2 Core (UNARMOURED) | Km. | 36259.28 | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310654 | 4 Core (UNARMOURED) | Km. | 62758.54 | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310658 | 8 Core (UNARMOURED) | Km. | 119188.38 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310681 | 10 Core (UNARMOURED) | Km. | 148732.16 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC |  | BIN CODE Changed. Old Bin 7130310660
7130310660 | 10 Core (ARMOURED) | Km. | 205733.24 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 161612.87 | CONTROL CABLE COP 12 CORE 2.5 SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 18174.64 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 42707.22 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 57599 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 110492.79 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 215644.03 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 267750.7 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC |  | ITEM DELETED: NOT TO BE USED
7130311057 | 150 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV |  | ITEM DELETED: NOT TO BE USED
7130311061 | 300 Sqmm. | km |  | Power Cable ARM ALU 3.5CORE 300/150SQMM |  | ITEM DELETED: NOT TO BE USED
7130311084 | 16.0 Sqmm. | km | 58813.87 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 10186.59
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 12733.23 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 15279.87 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 17826.52 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 19099.85
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 22919.81
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 801.73 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 866.03
7130320045 | Cable tie for AB Cable | Each | 25.72
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | Set | 3863.4 | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 2464.11 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 2595.95
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 5.38 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 34129.38 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 826.38
7130352031 | 16 Sq.mm, 4 Core | Set | 826.38 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 887.47
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1247.6
7130352034 | 150 Sq.mm, 3.5 Core | Set | 1859.61
7130352035 | 300 Sq.mm, 3.5 Core | Set | 3005.39
7130352036 | 400 Sq.mm, 3.5 Core | Set | 3840.33
7130352037 | End terminating jointing kit upto 240 sqmm XLPE cable | Set | 23009.06 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x50 Sq.mm | Set | 13753.61
7130352039 | 3x95 Sq.mm | Set | 13753.61 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 18210.23 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 19916.04 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 19916.04 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 7149.38 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 8630.52 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 8878.79 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box (with 10 No. connectors) | No. | 3036.33 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 2.17 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 2.17 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 4.34
7130354277 | 32 Sq mm | Nos. | 5.42
7130354278 | 50 Sq mm | Nos. | 8.69 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 13.03 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 16.29 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 22.81 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 26.06 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 41.26
7130354284 | 225 Sq mm | Nos. | 46.69
7130354285 | 240 Sq mm | Nos. | 67.32
7130354286 | 300 Sq mm | Nos. | 79.27 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 102.07
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 661.1 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 84.3 | INSULATING PIERCING CONNECTOR AB CABLE(S
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 109.82 | INSULATING PIERCING CONNECTOR FOR AB CAB
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 153.07 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 119.8 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 169.29 | STRAIGHT THROUGH JOINT
7130390019 | End cap for 50/70 Sq.mm | Nos. | 28.93 | END CLAMP CAP FOR 50/70 SQMM
7130600023 | 50 x 50 x 6 mm | MT | 41788.76 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 41788.76 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 41788.76 | M S ANGLE 75X75X6 MM
7130600166 | 75x40 mm | MT | 41788.76 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 45476.44 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 41788.76 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 45476.44 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT | 39505.14 | R.S.JOIST 125 x 70 mm
7130600675 | 175 x 85 mm | MT | 44915.52 | R S JOIST 175X85 MM | ISI MARK
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 50674.4 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 50674.4 | RAIL 60 KG PER METER
7130601958 | 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 46403.88 | H BEAMS 152X152MM; 37.1 KG/MTR. | ISI MARK
7130601965 | 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 46403.88 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR | ISI MARK
7130610206 | Barbed wire | MT | 76075.03 | G.I. WIRES: - Barbed wire.
7130620013 | I-Bolt (big size) | No | 124.12 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 69.38
7130620133 | 16x40 mm | Kg | 95.97 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 95.97 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 69.38 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 70.53 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 70.53 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 69.38 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 68.22 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 68.22 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 67.06 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt | No | 415.5 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 149.07 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | RM | 1079.16 | G.I. PIPE 200MM FOR 400MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 935.03 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 3618.29 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | Caping of RCC Pipe on both end of pipe with Concreting and Bricks work | Cmt | 3618.67 |  |  | NEW BIN CODE ALLOTED
7130640031 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 600 mm | Each | 2617 |  |  | BIN CODE Changed. Old Bin 7130640030
7130640036 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 900 mm | Each | 5032 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG)
7130640037 | M.S.Pipe 200 mm dia with collars | RM (medium) | 1326.73 |  |  | NEW BIN CODE ALLOTED
7130640038 | M.S.Pipe 200 mm dia with collars | RM (light) | 1036.11 | M.S. PIPE 200 MM DIA WITH COLLARS |  | BIN CODE Changed. Old Bin 7130640037
7130640171 | G.I. Bend 40 mm | Each | 104.16 |  |  | NEW BIN CODE ALLOTED
7130641396 | Gl Pipe 40 mm | Per Mtr | 215.22 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | No | 849.08 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 4315.55 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing (TATA Make) 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. T&D/DRG/MISC/2 Revision -2 | Sq.mtr | 2024.88
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 133.73
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 590.97 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 428.94 | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 2255.2 | PCC POLE 140 KG; 8,0 MTR LONG
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 280 Kg; 9.1 Mtr long | Each | 4402.65 | PCC POLE 280 KG; 9,1 MTR LONG
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each |  | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT |  | ITEM DELETED: NOT TO BE USED
7130800672 | 350 Kg; 7.0 Mtr long | Each |  | PCC POLE 350 KG; 7,0 MTR LONG |  | ITEM DELETED: NOT TO BE USED
7130810005 | Through Bolt | No | 87.31 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr 100 x 50 mm. | Set | 6872.65 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810026 | Stay clamp for 140 kG PCC Pole | Pair | 155.99 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 291.13 | Stay clamp LT/Pair
7130810060 | LT U CLAMP | No. | 78 | LT U CLAMP
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 70.96 | Strain Plate
7130810077 | Pole Clamp | No. | 433.92 | POLE CLAMP
7130810102 | Service Ring | No. | 344.82 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 291.13 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 309.8 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 309.8 | HT STAY CLAMP R S JOIST A TYPE
7130810251 | Stay Clamp Rail "B" type | Pair | 309.8 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 309.8 | 33 KV TOP CLAMP SEMIFINISHED
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 623.86 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 742.99 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 862.11 | LT FIVE PIN CROSS ARM
7130810495 | 11 kV Cross Arm Cleat type | No. | 1057.95 | 11 KV V CROSS ARM
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 1676.77 | D.O. / LA Mounting channel 75x40 mm.
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2508.6 | 1.1 MTR DPDC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 3977.41 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 2889.17 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 4060.2 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 4590.18 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 2354.14 | 33 KV V CROSS ARM
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 5428.06 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 93.9 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 391.69 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 296.79 | 11 kV top clamp
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 3257.64 | 11 kV Cut point channel paint
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 8537.3 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 322.98 | Stay clamp for 'H' Beam
7130820008 | 11 kV Pin insulator with Pin | Each | 142.14 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 351.44 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 128.45 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 236.53 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 4.05 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 448.04 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 1832.27 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 32.16
7130820030 | Disc insulator | Each | 215.81 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 43.03 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 217.7 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 11.31 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 12.82 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 10.78 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 71.32 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 237.31 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 35.61 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 35.7 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 40.64 | HARDWARE FOR 75X90 MM LT SHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 119.62 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 248.51 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2129.35 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 155.45 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km |  | CONDUCTOR AAA SQURREL |  | ITEM DELETED: NOT TO BE USED
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km |  | CONDUCTOR AAA WEASEL |  | ITEM DELETED: NOT TO BE USED
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km |  | CONDUCTOR AAA RABBIT |  | ITEM DELETED: NOT TO BE USED
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km |  | CONDUCTOR AAA RACOON |  | ITEM DELETED: NOT TO BE USED
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 36.14 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 141.07 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 650.6
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 14066.3 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq) | ISI MARK
7130830054 | Bimetallic clamp for VCB | Each | 379.95
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 20604.63 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq) | ISI MARK
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 379.95
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 33948.58 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q) | ISI MARK
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 193.15
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 50185.79 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E | ISI MARK
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 66185.04 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq) | ISI MARK
7130830070 | 0.2 Sq inch ( 130 Sqmm Al.Eq.)(Panther) | Km | 147387.66 | CONDUCTOR ACSR PANTHER 130 sq mm | ISI MARK
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km |  | CONDUCTOR AAA DOG |  | ITEM DELETED: NOT TO BE USED
7130830585 | T-Clamp for Dog Conductor. | Each | 266.98 | T-CLAMPS FOR ACSR CONDUCTOR Dog Condutor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 213.35 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830586 | T-Clamp for Panther Conductor. | Each | 312.45 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 283.36 | Bimetallic clamps for transformer & kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 29.14 | SLEEVE JOINTING ALUMINIUM FOR 0.03 SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 218.02 | SLEEVE REPAIR ALUMINIUM FOR .2 SQ INCH AC
7130840021 | 33 kV Polymer Lightning Arrestor | Each | 4545.92 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 504.66 | LIGHTNING ARRESTORS 11 KV gapless type.
7130850198 | GI Structure for complete Equipment | Kg | 82.25 |  |  | NEW BIN CODE ALLOTED
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 4590.18 | Transformer mounting 100 x 50 mm channel
7130850201 | Transformer Mounting with Belting for Addl. X-Arm | No. | 4434.72 | Transformer mounting 100 x 50 mm channel
7130860017 | I-Bolt - 16 mm | No. | 105.19 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 441.23 | STAY SET WITHOUT STAY WIRE 16 mm Paint 11 KV
7130860033 | Stay Set 20 mm (Painted) | Each | 803.97 | STAY SET WITHOUT STAY WIRE 20 mm (Painted)
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 69756.41 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 70439.64 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 764.89
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 114.85 | EARTHING COIL 8SWG GI WIRE 50 MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 358.38 | Earthing rod 25mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 63044.96 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 62999.96 | G.I. WIRES: - 4,0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 62999.96 | G.I. WIRES: - 5,0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 2183.26
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 978.57 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 2334.43 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2075.04 | Jointing Kit&HW LT ABC CableStraight Sus
7130880006 | Cable marker for U/G cable | No. | 126.51 | CABLE MARKER FOR U/G CABLE
7130880006 | Pad Connector (for Panther conductor) | No. | 139.39 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 89.74 | Danger boards 33 KV & 11 KV.
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 5151.35 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 6499.75
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 14741.43 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 15443.4 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 57.31 | LT LINE SPACERS
7130890973 | Stainless steel strap with buckle (for installation of Service Distribution Box) | Set | 58.95
7131961526 | GSM Modem | Nos. | 3696.94 | GSM MODEM
7130893004 | Eye Hook | No. | 176.78 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 3346.47 | 33 KV guarding channel 100x50 mm.
7131210001 | Panel lndication lamps | Nos. | 119.53
7131210010 | LED 7 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210018 | LED 12 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210019 | LED 14 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210020 | LED 15 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210021 | LED Lamps with COMPLETE FITTING - 15 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210022 | LED LAMPS WITH COMPLETE FITTING - 20 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210852 | CFL 7 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210881 | 250 Watt Metal Halide | Each |  | METAL HALIDE LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131220182 | Tube Light Rod (T5 type) | Each |  | LAMPS: -Tube Light (40 Watts.) |  | ITEM DELETED: NOT TO BE USED
7131230003 | 250 Watt Sodium Vapour | Each |  | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER |  | ITEM DELETED: NOT TO BE USED
7131230116 | 250 Watt Mercury Vapour | Each |  | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO |  | ITEM DELETED: NOT TO BE USED
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each |  | S/ V HIGH PRESSURE LAMP 400W 230/250V |  | ITEM DELETED: NOT TO BE USED
7131280006 | CFL 15 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280007 | CFL 20 Watts | Each |  | CFL 20 WATTS LAMP |  | ITEM DELETED: NOT TO BE USED
7131280008 | CFL 23 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280009 | 125 Watt Mercury Vapour | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280010 | Halogen Filament (1000 Watts) | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280012 | Street Light fitting with tube light | Each |  | STREET LIGHT FITTING WITH TUBE LIGHT |  | ITEM DELETED: NOT TO BE USED
7131280013 | Street Light fitting with CFL | Each |  | STREET LIGHT FITTING WITH CFL |  | ITEM DELETED: NOT TO BE USED
7131280014 | HPSV lamp 150 watt | Each |  | HPSV LAMP 150 WATT |  | ITEM DELETED: NOT TO BE USED
7131280015 | HPSV Choke 250 watt | Each |  | HPSV LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each |  | 150 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each |  | 250 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280882 | CFL 11 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 1621.45 | ENERGY METER ENECTRONIC 10-60 AMPS | ISI MARK
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for __/110 Volts; __/1 Amps; or __/5 Amps) | Each | 1081589.85 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 169.52 |  |  | RATE EXCLUDING G.S.T.
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 728.23 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 695.5 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A | ISI MARK
7131300881 | CMRI (Common Meter Reading Instrument) | Each | 26218.87 | Common Meter Reading Instrument CMRI
7131310013 | 3 Ø 4 Wire 0.5S Consumer meter | Each | 3829.1 | HT TRIVECTOR METER 5 AMPS | ISI MARK
7131310015 | CT operated electronic static meters with AMR (Composite Unit) with LTCTs / Modem / Meter / Meter Box. | Each | 11958.83 | ELECTORNIC LTCT METER 3X4 100/5 A | ISI MARK
7131310033 | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | Each | 3500.23 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310034 | 3 Ø 4 Wire 0.5S with DLMS Protocol category B | Each | 3500.23 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310035 | 3 Ø 3 Wire 0.2S bulk consumer meter | Each | 16457.11 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310036 | 3 Ø 4 Wire 0.2S bulk consumer meter | Each | 16457.11 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310042 | 3 Ø 4 Wire 0.2S 5A bulk consumer meter | Each | 16457.11 |  | ISI MARK
7131310037 | Test terminal Box (TTB) | Each | 894.97 | TTB
7131310997 | CT operated electronic static meters 100/5 Amp. With data storage. | Each | 1639.61 | 3 PHASE 4 WIRE LTCT OPERATED METER | ISI MARK
7131320009 | Digital Multimeter Electronic Type | Nos. | 3034.29 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) | Nos. | 3752.28 |  |  | RATE EXCLUDING G.S.T.
7131324780 | Megger 500 V | Nos. | 3641.14
7131324806 | Megger up to 2.5 kV | Nos. | 5487.76 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 6159.6
7131334001 | Set of 3 O.C. relays instantaneous high set feature | Nos. | 7516.15 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH
7131334002 | Set of 2 O.C.+ 1 earth fault relay without instantaneous high set feature | Nos. | 7576.27 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO
7131399007 | Master trip relays | Nos. | 1598.39
7131338004 | Transformer Oil Dielectric Breakdown testkit | Nos. | 61560 |  |  | RATE EXCLUDING G.S.T.
7131338025 | Neon tester | Nos. | 57.4 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 242.74
7131387502 | Thermometer (Wall Mounted) | Nos. | 480.25 | THERMOMETER (WALL MOUNTED)
7131390014 | Earthing Coil for messenger wire | Nos. | 185.97
7131390015 | Anchor sleeve for messenger wire | Nos. | 32.16
7131390016 | Universal hook & Bolts & nuts | Nos. | 450.51
7131820031 | LT Single Phase MCB 5 Amps. | Each | 103.08
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 103.08 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 436.86
7131820034 | LT Three Phase MCB 32 Amps. | Each | 436.86
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 2910.04
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 3152.97
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 3152.97
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2303.75
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 5275.03 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900004 | Locally fabricated - 3 Phase fuse units (Robust fuse for circuit base). | Each | 722.16 | LT ROBUST POLE FUSE UNIT |  | BIN CODE Changed. Old Bin 7131900005
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 7.46 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 299.63 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 460.65 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 12.78 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 13.85 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 295.38 | H.R.C. FUSE UNITS: -100 Amps.
7131900876 | H.R.C. Fuse 100 Amps. | Each | 115.17 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 742.17 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 821.08 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 577.24 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 10 SWG
7131900974 | T.C. Fuse Wire 8 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 8 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 44.41 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 87.76 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 25.38 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 246.62 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 474.95 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 1052.32 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920112 | 11 kV Kiosk VCB | Each | 315791 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 755.6 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 1814.36 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  |  |  |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 3509.55 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  |  |  |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 4927.03 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  |  |  |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 6684.69 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  |  |  |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 10097.04 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  |  |  |  | 51.2435
7131930109 | 33 kV ; 600 Amps with earth switch. | Each |  | 33 KV 600 AMPS WITH EARTH SWITCH ISOLATO |  | ITEM DELETED: NOT TO BE USED
7131930221 | 11 kV Porcelain A.B. Switch | Each | 8496 | AB Switch with complete fitting 11 KV
7131930321 | 33 kV Porcelain A.B. Switch | Each | 18863.48 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1177.88 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 2886.87 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 22623.4 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 39152.26 | 33 KV Isolator 800A without earth switch
7131931091 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure | Set | 27806.59 |  |  | NEW BIN CODE ALLOTED
7131931095 | Mounting GI structure for above isolator | Set | 14225.81 |  |  | NEW BIN CODE ALLOTED
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 2425.2 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 23039.46 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 23039.46
7131940871 | Indoor Type Automatic Control Unit along with APFC Relay | No. | 46692.4 |  |  | NEW BIN CODE ALLOTED
7131941762 | 11 kV VCB without control panel & CT's. | Each | 117747.13 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 235869.4 | 33KV VCB FOR 30 VOLT DC
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 990.47 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1193.13 | DISTRIBUTION BOX 3 PH 4 CONNECTOR
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 40920.98
7131950016 | 11 kV Sectionalizer. | Each | 351072.13
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 15292.16 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 19116 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 38230.4 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 32804 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 26222.61 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 28818.87 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 25950.06 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 27166.71 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960010 | 11 kV Control & Relay Panel for Capacitor Bank | Each | 83478.19 |  |  | NEW BIN CODE ALLOTED
7131960520 | 2 Feeder Control (Static Relays) | Each | 38863.78 | 11KV MULTICIRCUIT (2F) CONTROL PANELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 38863.78 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 38863.78 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm;3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 207.33
7132004003 | Hack saw frames + B185 | Nos. | 133.73
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 11.23
7132011171 | Cable Cutter | Nos. | 493.04 |  |  | NEW BIN CODE ALLOTED
7132013331 | Discharge Rod | Nos. | 477.62 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 3034.29
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 1111.44
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 343.89
7132061858 | Combination Plier | Nos. | 229.58 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 73.8 | SCREW DRIVER 250MM
7132072007 | Screw driver 200 mm | Nos. | 69.11 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 64.43 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. |  | SCREW DRIVER INSULATED 255 MM |  | ITEM DELETED: NOT TO BE USED
7132074032 | Ring Spanners (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 1607.09 | RING SPANNER
7132074033 | Tube Spanners | Set. | 664.15
7132074034 | Double end spanner (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 760.2 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 493.13
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F& tommy Bar) | Set. | 1464.18 | BOX SPANNER
7132088614 | Pipe Wrench 24 inches size | Nos. | 1220.46
7132088615 | Pipe Wrench 18 inches size | Nos. | 669.79
7132200014 | 1089 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 | Each | 141355.63 | 11 KV CAPACITOR 600KVAR
7132200812 | 5 kVAR | Each | 1561.71 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 3122.45 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 3751.83 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200815 | 20 kVAR | Each | 6226.32 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 186917.23 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each |  | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 25KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 63KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 100KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 200KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210012 | 315 kVA (CEA Design) Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | XMER 315KVA 11/0.43KV CEA REG. CU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210015 | 500 kVA [CEA Design] Copper Wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | 500 kVA [CEA Design] (4 Star) Copper Wound Transformer |  | ITEM DELETED: NOT TO BE USED
7132210106 | 0.2% Reactor suitable for 363 kVAR step | Set | 6864.39 |  |  | NEW BIN CODE ALLOTED
7132210108 | 0.2% Reactor suitable for 726 kVAR step | Set | 8380.18 |  |  | NEW BIN CODE ALLOTED
7132210215 | 50 kVA (Copper winding) | Each | 132374.78 | TRANSFORMER 33/.4KV 50KVA
7132220091 | Power Transformer 1600 kVA | Each | 780829.7 | TRANSFORMER 33/11KV 1.6 MVA POWER
7132220095 | Power Transformer 3150 kVA | Each | 2241066.5 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 5000 kVA | Each | 3165338.45 | TRANSFORMER 33/11KV 5 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 229882.12 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 345.07 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 212181.48 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 345.07 | L.T. C.T.200/5 Amps.
7132230021 | L.T.C.T. 300/5 Amps. | Each | 276.27 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 276.27 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1-1A | No. | 584046.53 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 24401.32 | 33KV CT 400-200/5-5A
7132230065 | 132 kV C.T. 600-300/1-1A | No. | 316935.3 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV
7132230075 | 132 kV C.T. 150-75/1-1A | No. | 361851.93 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1-1A | No. | 797258.43 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1-1A | No. | 521788.66 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1-1A | No. | 482699.81 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 36899.97
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 83670.61 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 12913.58 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 13463.75 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 25367.66 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5) Amps oil filled | Each | 19713.76 | 33KV CT's(200-100/5)A oil filled OD Type
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each |  | 33KV CT's (100-50/5)A oil filled OD Type |  | ITEM DELETED: NOT TO BE USED
7132230330 | 132 kV C.T. 100-50/1-1A | No. | 358156.27 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE
7132230332 | 132 kV C.T. 200-100/1-1A | No. | 331433.7 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1-1A | No. | 290070.6 | CURRENT X-MER 300-150/1/1A - 132KV
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A |  | ITEM DELETED: NOT TO BE USED
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 37970.88 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A |  | ITEM DELETED: NOT TO BE USED
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 36896.64 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 37368.74 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A |  | ITEM DELETED: NOT TO BE USED
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 36485.4 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230414 | 11 kV CTPT Unit 50/5 A | Each | 37635.9 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 82470.05 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 80471.17 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A |  | ITEM DELETED: NOT TO BE USED
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 86805.48 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A |  | ITEM DELETED: NOT TO BE USED
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 80181.91 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 80838.25 | OIL IMM 3 PH CTPT UNITS 33 KV-100&200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 80181.91 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 82412.42 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230471 | 11 kV 3 PH Residual Voltage Transformer | Each | 33323.81 |  |  | NEW BIN CODE ALLOTED
7132230473 | 11 kV PT Station Type | No. |  |  |  | ITEM DELETED: NOT TO BE USED
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 10336.32 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 16586.32 | VOLTAGE TRANSFORMER 33 KV / 110 VOLTS SINGLE
7132230501 | 132 kV P.T. | No. | 247996.79 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 584046.53 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132401672 | Small Steel Almirah 50'' | No. | 5408.9 | STEEL ALMIRAH SMALL SIZE
7132404015 | Safety belts | Nos. | 617.31 | SAFETY BELTS
7132404016 | Safety helmets | Nos. | 139.59 | SAFETY HELMETS
7132404366 | Battery (Low Maintenance SAN controller) | No. | 51840 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 147.22 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 2580.37 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406420 | Pilfer proof SMC/FRPP/PPO LTCT meter box | Each | 3258.27
7132406425 | Universal Meter Box for HT meters. | Each | 2614.17 | Universal Meter Box for HT meters.
7132406721 | CT operated electronic static meters with DLMS. | Each | 2590.64 | LTCT METER WITH DLMS | ISI MARK
7132409830 | Office Chair cane seat & back with full arms rest | No. | 2649.94 | S-TYPE STEEL CHAIR WITH TEAK WOOD HAND
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 534.34 | RUBBER HAND GLOVES
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 5805.2 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 734.29 | RAIN COATS WITH HOODS |  | RATE EXCLUDING G.S.T.
7132427635 | Gum Boots | Nos. | 494.35 | GUM BOOTS |  | RATE EXCLUDING G.S.T.
7132438002 | Silica gel | Kg | 182.73 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 6.73 | POLYCARBONATE SEAL
7132444007 | Grounding Sticks (Galvanised Earthing Rods 25 mm, 3 Mtr. long) | Set. | 1003.21
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 4622.46 | METTING RUBBER 1900X1800X12MM
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 307.92
7132457798 | Transformer Oil In Barrel | KL | 67850 | TRANSFORMER OIL In Tanker/barrel
7132457798 | Transformer Oil In Tanker | KL | 58410 | TRANSFORMER OIL In Tanker/barrel
7132459005 | Poly Carbonate seal double anker type | Each | 5.85 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | 1146.75 | HDPE PIPE 200MM ID; 240MM OD |  |  | 7132401667 | 13429.5238
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 417 | JOINTING ARRANGEMENT OF HDPE PIPE |  |  | 7132409830 | 2649.9429
7132468558 | Battery charger | Each | 10952.19 | 30 Volt 100 AH lead acid battery charger |  |  | 7132476797 | 18542.8571
7132475019 | Files of sizes | Set. | 347.89 |  |  |  | 7132476795 | 21914.2857
7132475019 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 124.76 |  |  | RATE EXCLUDING G.S.T. | 7132420412 | 9630.4762
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 14.29 | PVC INSULATION TAPES 19 MM WIDE AND IN R |  | RATE EXCLUDING G.S.T. | 7132488810 | 53028.5714
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 67.62 |  |  | RATE EXCLUDING G.S.T. | 7132486195 | 32914.2857
7132478004 | Tong tester | Nos. | 1518.07 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI |  |  | 7132486151 | 7979.0476
7132478011 | Hand Torch 5 cell | Nos. | 599.94 |  |  |  | 7131880133 | 74240
7132478012 | Hand Torch 3 cell | Nos. | 393.33 | HAND TORCH 3 CELLED |  |  | 7131880134 | 40228.5714
7132478012 | Cotton Waste | Kg | 61.9 | HAND TORCH 3 CELLED |  | RATE EXCLUDING G.S.T.
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 5191.41 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 56.19 |  |  | RATE EXCLUDING G.S.T.
7132490053 | Bitumen compound | Kg | 101.14
7132498006 | River sand | Cmt | 903 | RIVER SAND
7130310027 | 11 kV Covered Conductor 50 Sqmm XLPE insulation | Mtr. | 489.36 | 11KV COVERED CONDUCTOR XLPE 50SQMM
7130310029 | 11 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 589.88 | 11KV COVERED CONDUCTOR XLPE 70SQMM
7130310043 | 11 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 753.26 | 11KV COVERED CONDUCTOR XLPE 99SQMM
7130310047 | 33 kV Covered Conductor 157 Sqmm XLPE insulation | Mtr. | 1111.21 | 33KV COVERED CONDUCTOR XLPE 157SQMM
7130310048 | 33 kV Covered Conductor 241 Sqmm XLPE insulation | Mtr. | 1565.71 | 33KV COVERED CONDUCTOR XLPE 241SQMM
7130310045 | 33 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 694.74 | 33KV COVERED CONDUCTOR XLPE 70SQMM
7130310046 | 33 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 790.12 | 33KV COVERED CONDUCTOR XLPE 99SQMM
7130310025 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 13494.42 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310026 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 21384.67 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310034 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 137519.06 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310035 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 210046.77 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7131310168 | Spot Billing Machine | Each | 11569.13
11 kV Oil Immersed 3 Phase CT-PT Unit of capacity --
7132230410 | 200/5 Amp | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7132230403 | 100/5 Amp | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131960919 | 33 kV 2 feeder control panel (Static Relays) | Each | 38863.78
7130870040 | G.I.Strip 25x3 mm | Kg | 85.92 |  |  | NEW BIN CODE ALLOTED
7132444005 | Numerical Poly Carbonate seals | No | 8.99
7130820013 | 33 kV Polymer Disc Insulator (45 kN) | No | 236.53 |  |  | BIN CODE Changed. Old Bin 7130820011
7131930110 | D.O.Fuse Polymer unit 11 kV | Each | 1561.44
7131930111 | D.O.Fuse Polymer unit 33 kV | Each | 2234.66
7130800001 | PCC Pole 200 kG; 9.0 Mtr. Long | Each | 3046.2
7130800002 | PCC Pole 365 kG; 11 Mtr. Long | Each | 7605.2
7130820001 | 11 kV Polymer Post Insulator | Nos. | 231.83
7130820002 | 33 kV Polymer Post Insulator | Nos. | 803.65
7130820010 | Silicon rubber composite insulator / 11 kV 45 kN Polymeric Insulator | Nos. | 128.45
7131930107 | Polymer A.B.Switch with complete fitting 11 kV | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131930108 | Polymer A.B.Switch with complete fitting 33 kV | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 200 Kg 8.0 Meter long PCC Pole | No | 2552.95
7130311023 | 2.5 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 22.32 | 2.5 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311024 | 4.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 26.78 | 4.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311025 | 6.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 39.05 | 6.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311026 | 6.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 46.86 | 6.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311027 | 8.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 56.91 | 8.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311028 | 10 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 68.07 | 10 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311029 | 16 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 89.27 | 16 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311030 | 25 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 113.82 | 25 sqmm 4C 3ɸ Armour PVC insulated service Cable
7132210017 | 16 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 44158.56 | XMER 16KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210018 | 25 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 49457.85 | XMER 25KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210019 | 63 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 89213.04 | XMER 63KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210020 | 100 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 117398.25 | XMER 100KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210021 | 200 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 220752.68 | XMER 200KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132220081 | 315 kVA, Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 546827.89 |  | ISI MARK
7132220082 | 500 kVA, Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 826555.57 |  | ISI MARK
7130640008 | RCC Block (with 6 mm MS Bar) * | Each | 158 |  |  | RATE EXCLUDING G.S.T.
7131210011 | LED 9 Watt Lamp | Each | 70 | LED 9 W lamp with holder
7131210023 | LED Lamps with complete fitting-24 W | Nos. |  | 24 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210024 | LED Lamps with complete fitting-48 W | Nos. |  | 48 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210025 | LED Lamps with complete fitting-60 W | Nos. |  | 60 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131941763 | 3 Way RMU, 2OD + 1VL, One Incomer + One Breaker + One Outgoing, 350 MVA, 650 Amps. | Unit | 760396.12 | 11 kV RMU 3 WAY,2 OD+1 VL, 350 MVA, 650 A.
7131941764 | 4 Way RMU, 2OD + 2VL, (One Incomer + Two Breakers + One Outgoing, 350 MVA, 650 Amps. | Unit | 1080119.04 | 11 kV RMU 4 WAY,2 OD+2 VL, 350 MVA, 650 A.
7131941765 | 5 Way RMU, 2OD + 3VL, (One Incomer + Three Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 1394147.12 | 11 kV RMU 5 WAY,2 OD+3 VL, 350 MVA, 650 A.
7131941766 | 6 Way RMU, 2OD + 4VL,(One Incomer + Four Breakers + One Outgoing, 350 MVA, 650 Amps. | Unit | 1708175.2 | 11 kV RMU 6 WAY,2 OD+4 VL, 350 MVA, 650 A.
7131941767 | 1OD for RMU | Unit | 273605.75 | 1OD for RMU
7131941768 | 1VL for 350 MVA, 650 Amps RMU | Unit | 319722.92 | 1VL for 350 MVA, 650 Amps RMU
7132230009 | Indoor Type 33 kV Metering Cubical CTPT Unit 10/5 A | Each | 212181.48 | INDOOR TYPE 33 KV 10/5A CT:PT CUBICAL UNIT
7132230011 | Indoor Type 33 kV Metering Cubical CTPT Unit 25/5 A | Each | 212181.48 | INDOOR TYPE 33 KV 25/5A CT:PT CUBICAL UNIT
7132230012 | Indoor Type 33 kV Metering Cubical CTPT Unit 200/5 A | Each | 229882.12 | INDOOR TYPE 33 KV 200/5A CT:PT CUBICAL UNIT
7132230008 | Indoor Type 11 kV Metering Cubical CTPT Unit 10/5 A | Each | 69481.96 | INDOOR TYPE 11 KV 10/5A CT:PT CUBICAL UNIT
7132230010 | Indoor Type 11 kV Metering Cubical CTPT Unit 25/5 A | Each | 69481.96 | INDOOR TYPE 11 KV 25/5A CT:PT CUBICAL UNIT
7131980004 | (0+1) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH ONE 630 A LOAD BREAK SWITCH. | No. | 231096.84
7131980005 | (0+3) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH THREE 630 A LOAD BREAK SWITCHES. | No. | 427328.6
7131980006 | (0+4) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR 630 A LOAD BREAK SWITCHES. | No. | 518467.28
7131980007 | (0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER IN BETWEEN AFTER ISOLATOR. | No. | 826173.17
7131980008 | (0+2)+BC+(0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH SIX NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER WITH LBS IN BETWEEN AFTER ISOLATOR. | No. | 1306570.86
7131980001 | 12 kV, Outdoor type Vacuum Capacitor switches | No. | 67737.07 |  |  | NEW BIN CODE ALLOTED
7131920028 | AC Distribution board for AC/DC Supply | No. | 10907.7 |  |  | NEW BIN CODE ALLOTED
7132486843 | Chem Rod Earthing electrode (Chemical Earthing) | No. | 8945.71 |  |  | RATE EXCLUDING G.S.T.
7130840003 | Surge Arrestor | No. | 825.74 |  |  | NEW BIN CODE ALLOTED
7131950396 | Ground connection for Messenger Wire | No. | 125.46 |  |  | NEW BIN CODE ALLOTED
7132406800 | 33/11 kV S/S (Name Plate) Board | Job | 9412.76 |  |  | NEW BIN CODE ALLOTED
7130890973 | Stainless steel strap with buckle for installation of Service Distribution Box. | Set | 58.95 |  |  | NEW BIN CODE ALLOTED
7131210840 | 11 kV Fault Passage Indicator for Overhead line | No. | 14104.76 |  |  | NEW BIN CODE ALLOTED; RATE EXCLUDING G.S.T.
Note on A609: Author: NEW BIN CODE ALLOTED
Note on B163: 89326879: Earlier name - 600 mm
Note on B164: 89326879: Earlier name - 900 mm
Note on B316: 89326879: Earlier name- 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for 132 kV)
Note on B321: 89326879: Earlier name - 3 Ø 4 Wire 0.5S Non DLMS
Note on B322: 89326879: Earler name was - CT operated electronic static meters with AMR (Composite Unit)
Note on B325: 89326879: Earlier name- 3 Ø 3 Wire 0.2S Non DLMS
Note on B326: 89326879: Earlie name- 3 Ø 4 Wire 0.2S Non DLMS
Note on B338: 89326879: Earlier name - Transil oil Dielectric Breakdown testkit
Note on B461: 89326879: Earlier capacity was -- 220 kV C.T. 800-400/1
Note on B463: 89326879: Earlier capacity was - 132 kV C.T. 600-300/1
Note on B464: 89326879: Earlier capacity was - 132 kV C.T. 150-75/1
Note on B465: 89326879: Earlier capacity was -- 220 kV C.T. 150-75/1
Note on B466: 89326879: Earlier capacity was -- 220 kV C.T. 300-150/1
Note on B467: 89326879: Earlier capacity was -- 220 kV C.T. 600-300/1
Note on B475: 89326879: Earlier capacity was - 132 kV C.T. 100-50/1
Note on B476: 89326879: Earlier name was --132 kV C.T. 200-100/1
Note on B477: 89326879: Earlier capacity was -- 132 kV C.T. 300-150/1
Note on B517: 89326879: Earlier named as--Grounding Sticks (Earthing Rods)
Note on C8: 89326879: Earlier unit was - Per 1000

## D-1
COST SCHEDULE D-1
LT LINE 3 PHASE 5 WIRE ON PCC SUPPORTS USING RABBIT / WEASEL / SQUIRREL CONDUCTORS WITH MAXIMUM SPAN OF 60 METERS
2018-19
S. No. | PARTICULARS | New Bin Code | Unit | Rate | Using 50 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 3 Wires of 50 Sqmm ACSR & 2 Wires of 20 Sqmm |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 3 Wires of 30 Sqmm ACSR & 2 Wires of 20 Sqmm ACSR |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
1 | 140 Kg, 8.0 Mtr. long PCC support | 7130800012 | No | 2255.2 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4
2 | LT Five Pin Cross arm | 7130810461 | No | 862.11 | 22 | 18966.42 | 22 | 18966.42 | 22 | 18966.42 | 22 | 18966.42 | 22 | 18966.42
3 | LT Shackle insulator (90x75 mm) including cut point / angle location | 7130820106 | No | 12.82 | 88 | 1128.16 | 88 | 1128.16 | 88 | 1128.16 | 88 | 1128.16 | 88 | 1128.16
4 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 40.64 | 30 | 1219.2 | 30 | 1219.2 | 30 | 1219.2 | 30 | 1219.2 | 30 | 1219.2
5 | Earth knob (Aluminium bobbin) | 7130820201 | No | 35.61 | 17 | 605.37 | 17 | 605.37 | 17 | 605.37 | 17 | 605.37 | 17 | 605.37
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.9486 | 4120 | 139868.1496 | 3090 | 104901.1122 | -- |  | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.6046 | -- |  | -- |  | 4120 | 84891.0756 | 3090 | 63668.3067 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.0663 | 1030 | 14488.289 | 2060 | 28976.578 | 1030 | 14488.289 | 2060 | 28976.578 | 5150 | 72441.445
7 | (i) Stay set 16 mm | 7130860032 | No | 441.23 | 9 | 3971.07 | 9 | 3971.07 | 9 | 3971.07 | 9 | 3971.07 | 9 | 3971.07
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 54 | 3803.7406 | 54 | 3803.7406 | 54 | 3803.7406 | 54 | 3803.7406 | 54 | 3803.7406
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 9 | 1403.91 | 9 | 1403.91 | 9 | 1403.91 | 9 | 1403.91 | 9 | 1403.91
| (iv) Stay Insulator | 7130820117 | No | 10.78 | 9 | 97.02 | 9 | 97.02 | 9 | 97.02 | 9 | 97.02 | 9 | 97.02
8 | Split insulator for guarding | 7130820018 | Pair | 4.05 | 44 | 178.2 | 44 | 178.2 | 44 | 178.2 | 44 | 178.2 | 44 | 178.2
9 | Binding wire and tape | 7130830006 | Kg | 155.45 | 3.5 | 544.075 | 3.5 | 544.075 | 3.5 | 544.075 | 3.5 | 544.075 | 3.5 | 544.075
10 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 26 |  | 26 |  | 26 |  | 26 |  | 26
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 35 | 5530 | 35 | 5530 | 35 | 5530 | 35 | 5530 | 35 | 5530 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
11 | Nuts and Bolts |  | Kg |  | 35 |  | 35 |  | 35 |  | 35 |  | 35
| 12x100 mm | 7130620573 | Kg | 69.38 | 10 | 693.8 | 10 | 693.8 | 10 | 693.8 | 10 | 693.8 | 10 | 693.8
| 16x40 mm | 7130620609 | Kg | 69.38 | 5 | 346.9 | 5 | 346.9 | 5 | 346.9 | 5 | 346.9 | 5 | 346.9
| 16x140 mm | 7130620625 | Kg | 67.06 | 20 | 1341.2 | 20 | 1341.2 | 20 | 1341.2 | 20 | 1341.2 | 20 | 1341.2
12 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 5 | 574.25 | 5 | 574.25 | 5 | 574.25 | 5 | 574.25 | 5 | 574.25
13 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 2 | 293.54 | 2 | 293.54 | 2 | 293.54 | 2 | 293.54 | 2 | 293.54
14 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 2 | 655.88 | 2 | 655.88 | 2 | 655.88 | 2 | 655.88 | 2 | 655.88
15 | G.I. Wire 8 SWG for guarding | 7130870043 | Kg | 63 | 6 | 377.9998 | 6 | 377.9998 | 6 | 377.9998 | 6 | 377.9998 | 6 | 377.9998
16 | SUB TOTAL-1 |  |  |  |  | 234425.5739 |  | 213946.8255 |  | 179448.4999 |  | 172714.02 |  | 152510.5803
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 21098.3017 |  | 19255.2143 |  | 16150.365 |  | 15544.2618 |  | 13725.9522
18 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 199.5971 | 17 | 3393.15 | 17 | 3393.15 | 17 | 3393.15 | 17 | 3393.15 | 17 | 3393.15
19 | Labour charges as per Sch No. DL-1 |  |  |  |  | 54431.97 |  | 54431.97 |  | 54431.97 |  | 54431.97 |  | 54431.97
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 10728.2493 |  | 10728.2493 |  | 10728.2493 |  | 10728.2493 |  | 10728.2493
21 | SUB TOTAL-2 |  |  |  |  | 324077.2448 |  | 301755.409 |  | 264152.2341 |  | 256811.651 |  | 234789.9018
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 29303.1967 |  | 26743.3532 |  | 22431.0625 |  | 21589.2525 |  | 19063.8225
23 | Total cost per Km for non-guaranteed works |  |  |  |  | 353380.4415 |  | 328498.7622 |  | 286583.2966 |  | 278400.9035 |  | 253853.7243
24 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 353380 |  | 328499 |  | 286583 |  | 278401 |  | 253854
Note :- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on D21: 89326879: Earlier unit was - No.
Note on D23: 89326879: Earlier unit was - No.

## D-2
COST SCHEDULE D-2
1 Km LT LINES 3 Phase 4 Wire USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON 140 Kg; 8.0 Mtr. LONG PCC SUPPORTS WITH MAXIMUM SPAN OF 60 METERS
2018-19
S. NO. | PARTICULARS | New Bin Code | Unit | Rate | Using 50 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | PCC Pole 140 Kg, 8.0 Mtr long | 7130800012 | No | 2255.2 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4
2 | LT Four Pin cross arm | 7130810441 | No | 742.99 | 22 | 16345.78 | 22 | 16345.78 | 22 | 16345.78
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 12.82 | 66 | 846.12 | 66 | 846.12 | 66 | 846.12
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 35.61 | 17 | 605.37 | 17 | 605.37 | 17 | 605.37
5 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 40.64 | 25 | 1016 | 25 | 1016 | 25 | 1016
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.9486 | 3090 | 104901.1122 | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.6046 | -- |  | 3090 | 63668.3067 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.0663 | 1030 | 14488.289 | 1030 | 14488.289 | 4120 | 57953.156
7 | (i) Stay set 16 mm | 7130860032 | No | 441.23 | 9 | 3971.07 | 9 | 3971.07 | 9 | 3971.07
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 54 | 3803.7406 | 54 | 3803.7406 | 54 | 3803.7406
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 9 | 1403.91 | 9 | 1403.91 | 9 | 1403.91
| (iv) Stay Insulator | 7130820117 | No | 10.78 | 9 | 97.02 | 9 | 97.02 | 9 | 97.02
8 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. /pole and for stay set @ 02 Nos. per stay set. |  |  |  | 26 |  | 26 |  | 26
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 35 | 5530 | 35 | 5530 | 35 | 5530 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 5 | 574.25 | 5 | 574.25 | 5 | 574.25
10 | Split insulator for guarding | 7130820018 | Pair | 4.05 | 44 | 178.2 | 44 | 178.2 | 44 | 178.2
11 | M.S. Nuts and Bolts |  | Kg |  | 35 |  | 35 |  | 35
| 12x100 mm | 7130620573 | Kg | 69.38 | 10 | 693.8 | 10 | 693.8 | 10 | 693.8
| 16x40 mm | 7130620609 | Kg | 69.38 | 5 | 346.9 | 5 | 346.9 | 5 | 346.9
| 16x140 mm | 7130620625 | Kg | 67.06 | 20 | 1341.2 | 20 | 1341.2 | 20 | 1341.2
12 | Binding wire and tape | 7130830006 | Kg | 155.45 | 3.5 | 544.075 | 3.5 | 544.075 | 3.5 | 544.075
13 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 2 | 655.88 | 2 | 655.88 | 2 | 655.88
14 | Red Oxide paint | 7130211158 | Ltr | 146.77 | 2 | 293.54 | 2 | 293.54 | 2 | 293.54
15 | GI wire 8 SWG for guarding | 7130870043 | Kg | 63 | 6 | 377.9998 | 6 | 377.9998 | 6 | 377.9998
16 | SUB TOTAL-1 |  |  |  |  | 196352.6565 |  | 155119.851 |  | 134916.4113
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 17671.7391 |  | 13960.7866 |  | 12142.477
18 | Back filling of pole pit with boulder @ 0.25 Cmt |  | No | 199.5971 | 17 | 3393.15 | 17 | 3393.15 | 17 | 3393.15
19 | Labour charges as per Sch. No. DL-1 |  |  |  |  | 51202.23 |  | 51202.23 |  | 51202.23
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 10728.2493 |  | 10728.2493 |  | 10728.2493
21 | SUB TOTAL-2 |  |  |  |  | 279348.0248 |  | 234404.2668 |  | 212382.5176
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 24544.0821 |  | 19389.9814 |  | 16864.5514
23 | Total cost per Km for non-guaranteed works |  |  |  |  | 303892.1069 |  | 253794.2482 |  | 229247.069
24 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 303892 |  | 253794 |  | 229247
Note:- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on D21: 89326879: Earlier unit was - No.

## D-3
COST SCHEDULE D-3
1 Km LT LINE 1 PHASE 3 WIRE USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON 140 Kg; 8.0 Mtr. LONG PCC SUPPORTS WITH MAXIMUM SPAN OF 60 METERS
2018-19
S. No. | PARTICULARS |  | Unit | Rate | Using one wire of 50 Sqmm, one wire of 30 Sqmm ACSR and one wire of 20 Sqmm ACSR Conductor |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | PCC Pole 140 Kg, 8.0 Mtr long | 7130800012 | No | 2255.2 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4
2 | LT Three Pin cross arm | 7130810413 | No | 623.86 | 22 | 13724.92 | 22 | 13724.92 | 22 | 13724.92
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 12.82 | 44 | 564.08 | 44 | 564.08 | 44 | 564.08
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 35.61 | 22 | 783.42 | 22 | 783.42 | 22 | 783.42
5 | Hardware for 90x75 mm Shackle insu. | 7130820216 | No | 40.64 | 25 | 1016 | 25 | 1016 | 25 | 1016
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.9486 | 1030 | 34967.0374 | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.6046 | 1030 | 21222.7689 | 2060 | 42445.5378 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.0663 | 1030 | 14488.289 | 1030 | 14488.289 | 3090 | 43464.867
7 | (i) Stay set 16 mm | 7130860032 | No | 441.23 | 9 | 3971.07 | 9 | 3971.07 | 9 | 3971.07
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 54 | 3803.7406 | 54 | 3803.7406 | 54 | 3803.7406
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 9 | 1403.91 | 9 | 1403.91 | 9 | 1403.91
| (iv) Stay Insulator | 7130820117 | No | 10.78 | 9 | 97.02 | 9 | 97.02 | 9 | 97.02
8 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 26 |  | 26 |  | 26
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 35 | 5530 | 35 | 5530 | 35 | 5530 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 5 | 574.25 | 5 | 574.25 | 5 | 574.25
10 | Split insulator for guarding | 7130820018 | Pair | 4.05 | 44 | 178.2 | 44 | 178.2 | 44 | 178.2
11 | M.S. Nuts and Bolts |  | Kg |  | 16 |  | 16 |  | 16
| 12x100 mm | 7130620573 | Kg | 69.38 | 3.5 | 242.83 | 3.5 | 242.83 | 3.5 | 242.83
| 16x40 mm | 7130620609 | Kg | 69.38 | 1.5 | 104.07 | 1.5 | 104.07 | 1.5 | 104.07
| 16x140 mm | 7130620625 | Kg | 67.06 | 11 | 737.66 | 11 | 737.66 | 11 | 737.66
12 | Binding wire and tape | 7130830006 | Kg | 155.45 | 3.5 | 544.075 | 3.5 | 544.075 | 3.5 | 544.075
13 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 1.5 | 491.91 | 1.5 | 491.91 | 1.5 | 491.91
14 | Red Oxide paint | 7130211158 | Ltr | 146.77 | 1.5 | 220.155 | 1.5 | 220.155 | 1.5 | 220.155
15 | GI wire 4 mm for guarding | 7130870043 | Kg | 63 | 6 | 377.9998 | 6 | 377.9998 | 6 | 377.9998
16 | SUB TOTAL-1 |  |  |  |  | 143381.8056 |  | 129637.5371 |  | 116168.5773
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 12904.3625 |  | 11667.3783 |  | 10455.172
18 | Back filling of pole pit with boulder @ 0.25 Cmt |  | No | 199.5971 | 17 | 3393.15 | 17 | 3393.15 | 17 | 3393.15
19 | Labour charges as per Sch No. DL-1 |  |  |  |  | 47449.03 |  | 47449.03 |  | 47449.03
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 11354.0675 |  | 11354.0675 |  | 11354.0675
21 | SUB TOTAL-2 |  |  |  |  | 218482.4156 |  | 203501.163 |  | 188819.9968
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 17922.7257 |  | 16204.6921 |  | 14521.0722
23 | Total cost per Km for non-guaranteed works |  |  |  |  | 236405.1413 |  | 219705.8551 |  | 203341.0689
24 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 236405 |  | 219706 |  | 203341
Note: | All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B25: 89326879: Earlier name was - Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad
Note on D23: 89326879: Earlier unit was - No.

## D-4
COST SCHEDULE D-4
2018-19
1 KM OF 3 PHASE 5 WIRE LT LINE ON R.S. JOIST WITH ACSR CONDUCTOR FOR URBAN AREAS
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 3 Ph, 5 Wire line on RSJ 125x70 mm 9.3 Mtr long with max. span 45 Mtrs for size of conductor upto 3x50 Sqmm + 2x30 Sqmm ACSR |  | 3 Ph, 5 Wire line on RSJ 175x85 mm 9.3 Mtr long with max. span 65 Mtrs for size of conductor upto 3x80 Sqmm + 2x30 Sq mm ACSR
[5 empty] | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | (i) R.S. Joist (125x70 mm) 9.3 Mtr long @13.198 Kg = 122.74 kg/pole x 22 No = 2700.28 Kgs | 7130600635 | Kg | 39.5051 | 2700.28 | 106674.9394 | -- | --
| (ii) R.S. Joist (175x85 mm) 9.3 Mtr long @ 19.495 Kg per mtr x 9.3 mtr = 181.3 Kg/pole x 15 No = 2719.55 Kgs | 7130600675 | Kg | 44.9155 | -- | -- | 2719.55 | 122150.0024
2 | LT Five Pin Cross arm | 7130810461 | No | 862.11 | 27 | 23276.97 | 20 | 17242.2
3 | LT Shackle Insulator (90x75 mm) including cut point/angle location | 7130820106 | No | 12.82 | 108 | 1384.56 | 80 | 1025.6
4 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 40.64 | 35 | 1422.4 | 35 | 1422.4
5 | Earth knob (Aluminium bobbin) | 7130820201 | No | 35.61 | 27 | 961.47 | 20 | 712.2
6 | ACSR conductor including 3% sag
| (i) 80 Sqmm Al. Eq (Raccoon) | 7130830060 | Mtr | 50.1858 | -- |  | 3090 | 155074.0911
| (ii) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.9486 | 3090 | 104901.1122 | --
| (iii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.6046 | 2060 | 42445.5378 | 2060 | 42445.5378
7 | (i) Stay set 16 mm | 7130860032 | No | 441.23 | 12 | 5294.76 | 12 | 5294.76
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 72 | 5071.6541 | 72 | 5071.6541
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 12 | 1871.88 | 12 | 1871.88
8 | Split insulator for guarding | 7130820018 | Pair | 4.05 | 60 | 243 | 40 | 162
9 | Binding wire and tape | 7130830006 | Kg | 155.45 | 3.5 | 544.075 | 3 | 466.35
10 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad & support @ 0.3 Cmt (1:3:6) | 7130200202 | Cmt | 2510.8 | 10.1 | 25359.08 | 7.65 | 19207.62 | only material cost (excluding labour & G.S.T.)
11 | M.S. Nuts and Bolts |  | Kg |  | 44 |  | 30
| 12x100 mm | 7130620573 | Kg | 69.38 | 17 | 1179.46 | 12 | 832.56
| 16x40 mm | 7130620609 | Kg | 69.38 | 8 | 555.04 | 5 | 346.9
| 16x65 mm | 7130620614 | Kg | 68.22 | 19 | 1296.18 | 13 | 886.86
12 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 114.85 | 7 | 803.95 | 5 | 574.25
13 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 5 | 733.85 | 5 | 733.85
14 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 5 | 1639.7 | 5 | 1639.7
15 | G.I. Wire 4 mm for guarding | 7130870043 | Kg | 63 | 7.5 | 472.4997 | 5 | 314.9998
16 | SUB TOTAL-1 |  |  |  |  | 326132.1182 |  | 377475.4152
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 29351.8906 |  | 33972.7874
18 | Labour charges for concreting |  | Cmt | 578.8434 | 10.1 | 5846.3183 | 7.65 | 4428.152
19 | Labour charges as per Sch. No. DL-2 |  |  |  |  | 70491.86 |  | 60077.12
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 10341.6452 |  | 10341.6452
21 | SUB TOTAL-2 |  |  |  |  | 442163.8324 |  | 486295.1198
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 40766.5148 |  | 47184.4269
23 | Total cost per Km for non-guaranteed works |  |  |  |  | 482930.3472 |  | 533479.5467
24 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 482930 |  | 533480
Note:- All the rates are with considering price variation clause.
Note on D20: 89326879: Earlier unit was - No.

## D-5
COST SCHEDULE D-5
1 Km. LT LINE 1 PHASE 3 WIRE USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON R.S.JOIST SUPPORTS WITH MAXIMUM SPAN OF 45 METERS FOR URBAN AREAS
2018-19
S. No. | PARTICULARS | New Bin Code | Unit | Rate | Using one wire of 50 Sqmm, one wire of 30 Sqmm ACSR and one wire of 20 Sqmm ACSR Conductor |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 125x70 mm 9.3 Mtr long RSJ supports @ 13.198 Kg/mtr = 122.74 Kg/pole x 22 Nos = 2700.28 Kgs. | 7130600635 | Kg | 39.5051 | 2700.28 | 106674.9394 | 2700.28 | 106674.9394 | 2700.28 | 106674.9394
2 | LT Three Pin cross arm | 7130810413 | No | 623.86 | 22 | 13724.92 | 22 | 13724.92 | 22 | 13724.92
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 12.82 | 54 | 692.28 | 54 | 692.28 | 54 | 692.28
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 35.61 | 22 | 783.42 | 22 | 783.42 | 22 | 783.42
5 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 40.64 | 22 | 894.08 | 22 | 894.08 | 22 | 894.08
6 | ACSR Conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.9486 | 1030 | 34967.0374 | -- | -- | -- | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.6046 | 1030 | 21222.7689 | 2060 | 42445.5378 | -- | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.0663 | 1030 | 14488.289 | 1030 | 14488.289 | 3090 | 43464.867
7 | (i) Stay set 16 mm | 7130860032 | No | 441.23 | 9 | 3971.07 | 9 | 3971.07 | 9 | 3971.07
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 54 | 3803.7406 | 54 | 3803.7406 | 54 | 3803.7406
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 9 | 1403.91 | 9 | 1403.91 | 9 | 1403.91
8 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad & concreting of support @ 0.3 Cmt.per pole (1:3:6) | 7130200202 | Cmt | 2510.8 | 9.5 | 23852.6 | 9.5 | 23852.6 | 9.5 | 23852.6 | only material cost (excluding labour & G.S.T.)
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 7 | 803.95 | 7 | 803.95 | 7 | 803.95
10 | Split insulator for guarding | 7130820018 | Pair | 4.05 | 60 | 243 | 60 | 243 | 60 | 243
11 | M.S.Nuts and Bolts |  | Kg |  | 20 |  | 20 |  | 20
| 12x100 mm | 7130620573 | Kg | 69.38 | 7 | 485.66 | 7 | 485.66 | 7 | 485.66
| 16x40 mm | 7130620609 | Kg | 69.38 | 3 | 208.14 | 3 | 208.14 | 3 | 208.14
| 16x65 mm | 7130620614 | Kg | 68.22 | 10 | 682.2 | 10 | 682.2 | 10 | 682.2
12 | Binding wire and tape | 7130830006 | Kg | 155.45 | 3 | 466.35 | 3 | 466.35 | 3 | 466.35
13 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 5 | 1639.7 | 5 | 1639.7 | 5 | 1639.7
14 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 5 | 733.85 | 5 | 733.85 | 5 | 733.85
15 | G.I. Wire 8 SWG for guarding | 7130870043 | Kg | 63 | 5 | 314.9998 | 5 | 314.9998 | 5 | 314.9998
16 | SUB TOTAL-1 |  |  |  |  | 232056.9051 |  | 218312.6366 |  | 204843.6768
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 20885.1215 |  | 19648.1373 |  | 18435.9309
18 | Labour charges for concreting |  | Cmt | 578.8434 | 9.5 | 5499.0123 | 9.5 | 5499.0123 | 9.5 | 5499.0123
19 | Labour charges as per Sch. No. DL-1 |  |  |  |  | 47449.03 |  | 47449.03 |  | 47449.03
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 10341.6452 |  | 10341.6452 |  | 10341.6452
21 | SUB TOTAL-2 |  |  |  |  | 316231.7141 |  | 301250.4614 |  | 286569.2952
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 29007.1131 |  | 27289.0796 |  | 25605.4596
23 | Total cost per Km for non-guaranteed works |  |  |  |  | 345238.8272 |  | 328539.541 |  | 312174.7548
24 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 345239 |  | 328540 |  | 312175
Note on D22: 89326879: Earlier unit was - No.

## D-6 (1)
COST SCHEDULE -- D-6 (1)
1 KM OF 3 PHASE 5 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS. AND R.S. JOIST / H-BEAM POLE SUPPORT USING AB XLPE CABLE WITH MAXIMUM SPAN 50 METER URBAN AREA
2018-19
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support |  | RS Joist (175X85) mm 9.3 Mtr Long i.e. 19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No =3626.07 Kgs |  | H-BEAM 152x152 mm 37.1 Kg/Mtr 9.0 Mtr long i.e. 408.1 Kg/pole x10 Nos= 4081 Kgs
[5 empty] | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm. |  | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm. |  | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm.
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 6 | 7 | 6 | 7
1(a) | RS Joist (175X85) mm 9.3 Mtr Long i.e.19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No = 3626.07 Kgs | 7130600675 | Kg | 44.9155 |  |  | 3626.07 | 162866.8196
(b) | H-BEAM 152x152 mm 37.1 Kg /Mtr 9.0 Mtr long i.e. 333.9 Kg/pole x 20 Nos = 6678 Kgs | 7130601958 | Kg | 46.4039 |  |  |  |  | 6678 | 309885.1106
(c) | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 2255.2 | 20 | 45104
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 428.94 | 15 | 6434.1 | 15 | 6434.1 | 15 | 6434.1
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 84.3 | 20 | 1686 | 20 | 1686 | 20 | 1686
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 109.82 | 45 | 4941.9 | 45 | 4941.9 | 45 | 4941.9
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 153.07 | 15 | 2296.05 | 15 | 2296.05 | 15 | 2296.05 |  | Max. possibility of 5 Nos tapping in per km line
4 | Universal distribution connector | 7130390006 | Each | 119.8 | 28 | 3354.4 | 28 | 3354.4 | 28 | 3354.4
5 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 590.97 | 14 | 8273.58 | 14 | 8273.58 | 14 | 8273.58
6 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3x25 + 1x16 + 1x25 sqmm. (6% sag) | 7130310032 | Mtr | 76.7117 | 1100 | 84382.903 | 1100 | 84382.903 | 1100 | 84382.903
7 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 441.23 | 12 | 5294.76 | 12 | 5294.76 | 12 | 5294.76
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 72 | 5071.6541 | 72 | 5071.6541 | 72 | 5071.6541
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 12 | 1871.88 | 12 | 1871.88 | 12 | 1871.88
8 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole and @ 0.05 Cmt per pole for base padding of R.S.Joist / H-Beam pole i.e. 9.4 Cmt for RSJ & 13.4 Cmt for H-Beam pole (1:3:6) | 7130200202 | Cmt | 2510.8 |  |  | 9.4 | 23601.52 | 13.4 | 33644.72 | only material cost (excluding labour & G.S.T.)
9 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 |  |  |  |  | NEW BIN CODE ALLOTED ; RATE EXCLUDING G.S.T.
10 | M.S. Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30
| 12x100 mm | 7130620573 | Kg | 69.38 | 2 | 138.76 | 2 | 138.76 | 2 | 138.76
| 16x40 mm | 7130620609 | Kg | 69.38 | 14 | 971.32 | 14 | 971.32 | 14 | 971.32
| 16x65 mm | 7130620614 | Kg | 68.22 | 14 | 955.08 | 14 | 955.08 | 14 | 955.08
11 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 114.85 | 20 | 2297 | 20 | 2297 | 20 | 2297
12 | Distribution box 3 phase 5 connectors | 7131950012 | No | 1193.13 | 15 | 17896.95 | 15 | 17896.95 | 15 | 17896.95
13 | Stainless steel strap with buckle for installation of Service Distribution Box. | 7130890973 | Set | 58.95 | 15 | 884.25 | 15 | 884.25 | 15 | 884.25
14 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 0 | 0 | 10 | 1467.7 | 10 | 1467.7
15 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 0 | 0 | 10 | 3279.4 | 10 | 3279.4
16 | Service Ring | 7130810102 | No | 344.82 | 20 | 6896.4 | 20 | 6896.4 | 20 | 6896.4
17 | PVC insulated single core 16 sq.mm. cable @ 6 mtr. per 3 phase box | 7130311008 | Mtr | 18.1746 | 90 | 1635.7176 | 90 | 1635.7176 | 90 | 1635.7176
18 | Straight through joints | 7130390007 | No | 169.29 | 4 | 677.16 | 4 | 677.16 | 4 | 677.16
19 | End cap for 50/70 Sq.mm | 7130390019 | No | 28.93 | 14 | 405.02 | 14 | 405.02 | 14 | 405.02
20 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.38 | 530 | 2851.4 | 530 | 2851.4 | 530 | 2851.4
21 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 76.075 | 40 | 3043.0012 | 40 | 3043.0012 | 40 | 3043.0012
22 | SUB TOTAL-1 |  |  |  |  | 214315.2859 |  | 353474.7255 |  | 510536.2165
23 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 19288.3757 |  | 31812.7253 |  | 45948.2595
24 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 199.5971 | 20 | 3991.9411
25 | Labour charges for concreting |  | Cmt | 578.8434 |  |  | 9.4 | 5441.128 | 13.4 | 7756.5016
26 | Labour charges as per Sch. No.- DL-7 |  |  |  |  | 57957.6985 |  | 66735.6734 |  | 69992.76
27 | Transportation charges |  |  |  |  | 12621.4649 |  | 13788.8569 |  | 13788.8569
28 | SUB TOTAL-2 |  |  |  |  | 308174.7662 |  | 471253.109 |  | 648022.5945
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 26789.4107 |  | 44184.3407 |  | 63817.0271
30 | Total cost per Km for non-guaranteed works |  |  |  |  | 334964.1769 |  | 515437.4497 |  | 711839.6216
31 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 334964 |  | 515437 |  | 711840
Note:- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on C32: Author: NEW BIN CODE ALLOTED
Note on D22: 89326879: Earlier unit was - No.

## D-6 (2)
COST SCHEDULE -- D-6 (2)
1 KM OF 3 PHASE 5 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS. AND R.S. JOIST/H-BEAM POLE SUPPORT USING AB XLPE CABLE WITH MAXIMUM SPAN 50 METER URBAN AREA
2018-19
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | RS Joist (175X85) mm 9.3 Mtr Long i.e. 19.495 kg/mtr x 9.3 mtr = 181.30 kg x 20 No = 3626.07 Kgs Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | H-BEAM 152x152 mm 37.1 Kg/Mtr 9.0 Mtr long i.e. 408.1 Kg/pole x10 Nos = 4081 Kgs Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | Reason
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 6 | 7 | 6 | 7
1(a) | RS Joist (175X85) mm 9.3 Mtr Long i.e.19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No = 3626.07 Kgs | 7130600675 | Kg | 44.9155 |  |  | 3626.07 | 162866.8196
(b) | H-BEAM 152x152 mm 37.1 Kg /Mtr 9.0 Mtr long i.e. 333.9 Kg/pole x 20 Nos = 6678 Kgs | 7130601958 | Kg | 46.4039 |  |  |  |  | 6678 | 309885.1106
(c) | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 2255.2 | 20 | 45104
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 428.94 | 15 | 6434.1 | 15 | 6434.1 | 15 | 6434.1
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 84.3 | 20 | 1686 | 20 | 1686 | 20 | 1686
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 109.82 | 45 | 4941.9 | 45 | 4941.9 | 45 | 4941.9
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 153.07 | 15 | 2296.05 | 15 | 2296.05 | 15 | 2296.05
4 | Universal distribution connector | 7130390006 | Each | 119.8 | 28 | 3354.4 | 28 | 3354.4 | 28 | 3354.4
5 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 590.97 | 14 | 8273.58 | 14 | 8273.58 | 14 | 8273.58
6 | LT 3 phase 5 Wire Aerial Bunched Cable of Size
(a) | 3x70 + 1x16 + 1x50 sqmm. (6% sag) | 7130300025 | Mtr | 155.8331 | 1100 | 171416.388 | 1100 | 171416.388 | 1100 | 171416.388
7 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 441.23 | 12 | 5294.76 | 12 | 5294.76 | 12 | 5294.76
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 72 | 5071.6541 | 72 | 5071.6541 | 72 | 5071.6541
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 12 | 1871.88 | 12 | 1871.88 | 12 | 1871.88
8 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole and @ 0.05 Cmt per pole for base padding of R.S.Joist / H-Beam pole i.e. 9.4 Cmt for RSJ & 13.4 Cmt for H-Beam pole (1:3:6) | 7130200202 | Cmt | 2510.8 |  |  | 9.4 | 23601.52 | 13.4 | 33644.72 | only material cost (excluding labour & G.S.T.)
9 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 |  |  |  |  | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
10 | M.S. Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30
| 12x100 mm | 7130620573 | Kg | 69.38 | 2 | 138.76 | 2 | 138.76 | 2 | 138.76
| 16x40 mm | 7130620609 | Kg | 69.38 | 14 | 971.32 | 14 | 971.32 | 14 | 971.32
| 16x65 mm | 7130620614 | Kg | 68.22 | 14 | 955.08 | 14 | 955.08 | 14 | 955.08
11 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 20 | 2297 | 20 | 2297 | 20 | 2297
12 | Distribution box 3 phase 5 connectors | 7131950012 | No | 1193.13 | 15 | 17896.95 | 15 | 17896.95 | 15 | 17896.95
13 | Stainless steel strap with buckle for installation of Service Distribution Box. | 7130890973 | Set | 58.95 | 15 | 884.25 | 15 | 884.25 | 15 | 884.25
14 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 0 | 0 | 10 | 1467.7 | 10 | 1467.7
15 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 0 | 0 | 10 | 3279.4 | 10 | 3279.4
16 | Service Ring | 7130810102 | No | 344.82 | 20 | 6896.4 | 20 | 6896.4 | 20 | 6896.4
17 | PVC insulated single core 16 sq.mm. cable @ 6 mtr. per 3 phase box | 7130311008 | Mtr | 18.1746 | 90 | 1635.7176 | 90 | 1635.7176 | 90 | 1635.7176
18 | Straight through joints | 7130390007 | No | 169.29 | 4 | 677.16 | 4 | 677.16 | 4 | 677.16
19 | End cap for 50/70 Sq.mm | 7130390019 | No | 28.93 | 14 | 405.02 | 42 | 1215.06 | 42 | 1215.06
20 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.38 | 530 | 2851.4 | 530 | 2851.4 | 530 | 2851.4
21 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 76.075 | 40 | 3043.0012 | 40 | 3043.0012 | 40 | 3043.0012
22 | SUB TOTAL-1 |  |  |  |  | 301348.7709 |  | 441318.2505 |  | 598379.7415
23 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 27121.3894 |  | 39718.6425 |  | 53854.1767
24 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 199.5971 | 20 | 3991.9411
25 | Labour charges for concreting |  | Cmt | 578.8434 |  |  | 9.4 | 5441.128 | 13.4 | 7756.5016
26 | Labour charges as per Sch. No.- DL-7 |  |  |  |  | 57957.6985 |  | 66735.6734 |  | 69992.76
27 | Transportation charges |  |  |  |  | 12621.4649 |  | 13788.8569 |  | 13788.8569
28 | SUB TOTAL-2 |  |  |  |  | 403041.2648 |  | 567002.5513 |  | 743772.0367
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 37668.5964 |  | 55164.7813 |  | 74797.4677
30 | Total cost per Km for non-guaranteed works |  |  |  |  | 440709.8612 |  | 622167.3326 |  | 818569.5044
31 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 440710 |  | 622167 |  | 818570
Note:- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on C33: Author: NEW BIN CODE ALLOTED
Note on D23: 89326879: Earlier unit was - No.
Note on D33: 89326879: Earlier unit was - No.

## D-6 (3)
COST SCHEDULE -- D-6 (3)
1 KM OF 1 PHASE 3 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS.
2018-19
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support Using 1100 V grade AB Cable 1x25 + 1x16 + 1x25 sqmm.
[5 empty] | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 2255.2 | 20 | 45104
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 428.94 | 15 | 6434.1
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 84.3 | 20 | 1686
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 109.82 | 40 | 4392.8
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 153.07 | 10 | 1530.7
4 | Distribution box 1 phase 9 connectors | 7131950010 | Each | 990.47 | 20 | 19809.4
5 | Universal distribution connector | 7130390006 | No | 119.8 | 33 | 3953.4
6 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 590.97 | 14 | 8273.58
7 | LT 1 phase 3 Wire AB XLPE Cable 1x25 + 1x16 + 1x25 sqmm. (6% sag) | 7130310063 | Mtr | 41.1842 | 1100 | 45302.598
8 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 441.23 | 12 | 5294.76
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 72 | 5071.6541
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 12 | 1871.88
9 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
10 | M.S. Nuts and Bolts |  | Kg |  | 30
| 12x100 mm | 7130620573 | Kg | 69.38 | 2 | 138.76
| 16x40 mm | 7130620609 | Kg | 69.38 | 14 | 971.32
| 16x65 mm | 7130620614 | Kg | 68.22 | 14 | 955.08
11 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 20 | 2297
12 | Stainless steel strap with buckle for installation of Service Distribution Box. | 7130890973 | Set | 58.95 | 20 | 1179
13 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 3 | 440.31
14 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 3 | 983.82
15 | Service Ring | 7130810102 | No | 344.82 | 20 | 6896.4
16 | PVC insulated single core 16 sq.mm. cable @ 3 mtr. per 1 phase box | 7130311008 | Mtr | 18.1746 | 60 | 1090.4784
17 | Straight through joints | 7130390007 | No | 169.29 | 4 | 677.16
18 | End cap for 50/70 Sq.mm | 7130390019 | No | 28.93 | 14 | 405.02
19 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.38 | 530 | 2851.4
20 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 76.075 | 40 | 3043.0012
21 | SUB TOTAL-1 |  |  |  |  | 177605.6217
22 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 15984.506
23 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 199.5971 | 20 | 3991.9411
24 | Labour charges as per schedule DL-8 |  |  |  |  | 51605
25 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 12621.4649
26 | SUB TOTAL-2 |  |  |  |  | 261808.5337
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 22200.7027
28 | Total cost per Km for non-guaranteed works |  |  |  |  | 284009.2364
29 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 284009
Note:- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on C28: Author: NEW BIN CODE ALLOTED
Note on D20: 89326879: Earlier unit was - No.

## D-6 (4)
COST SCHEDULE -- D-6 (4)
1 Km. OF 3 PHASE 4 WIRE LT LINE WITH AERIAL BUNCH CABLE FOR PUMP CONNECTION UPTO 5 HP & 5 CONNECTION PER KM. WITH MAXIMUM SPAN 50 MTRS.
2018-19
Sl. No. | Particulars | New Bin Code | Unit | Rate (Rs.) | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3x16 + 1x25 sqmm.
[5 empty] | Qty. | Amt (Rs.)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg., 8.0 Mtrs. long PCC Poles | 7130800012 | No. | 2255.2 | 20 | 45104
2 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No. | 114.85 | 6 | 689.1
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No. | 84.3 | 30 | 2529
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 109.82 | 15 | 1647.3
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 153.07 | 24 | 3673.68
4 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3x16 + 1x25 sqmm. (6% sag) | 7130310070 | Mtr | 50.6846 | 1100 | 55753.016
5(i) | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet | 7130890007 | Each | 15443.4 | 1 | 15443.4
(ii) | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | 7131950012 | Each | 1193.13 | 5 | 5965.65
6 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 441.23 | 12 | 5294.76
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 70.4396 | 72 | 5071.6541
| (iii) Stay Clamp | 7130810026 | Pair | 155.99 | 12 | 1871.88
7 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
8 | Concreting of piller box @ 0.5 Cmt per box (1:3:6) | 7130200202 | Cmt | 2510.8 | 0.5 | 1255.4 | only material cost (excluding labour & G.S.T.)
9 | M.S. Nuts and Bolts
| 12x100 mm | 7130620573 | Kg | 69.38 | 2 | 138.76
| 16x40 mm | 7130620609 | Kg | 69.38 | 14 | 971.32
| 16x65 mm | 7130620614 | Kg | 68.22 | 14 | 955.08
10 | Universal distribution connector | 7130390006 | Each | 119.8 | 41 | 4911.8
11 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 428.94 | 22 | 9436.68
12 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 590.97 | 22 | 13001.34
13 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 1 | 146.77
14 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 1 | 327.94
15 | Pole Clamp | 7130810077 | No | 433.92 | 44 | 19092.48
16 | Eye Hook | 7130893004 | No | 176.78 | 44 | 7778.32
17 | Service Ring | 7130810102 | No | 344.82 | 30 | 10344.6
18 | Straight through joints | 7130390007 | No | 169.29 | 6 | 1015.74
19 | End cap for 50/70 Sq.mm | 7130390019 | No | 28.93 | 20 | 578.6
20 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.38 | 530 | 2851.4
21 | SUB TOTAL-1 |  |  |  |  | 222801.6701
22 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 20052.1503
23 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 199.5971 | 20 | 3991.9411
24 | Labour charges for concreting |  | Cmt | 578.8434 | 0.5 | 289.4217
25 | Labour charges as per Sch. No.- DL-9 |  |  |  |  | 58900
26 | Transportation charges |  |  |  |  | 12621.4649
27 | SUB TOTAL-2 |  |  |  |  | 318656.6481
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 27850.2088
29 | Total cost per Km for non-guaranteed works |  |  |  |  | 346506.8569
30 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 346507
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on D18: 89326879: Earlier unit was - No.

## D-6 (B)
COST SCHEDULE -- D-6 (B)
COST SCHEDULE FOR ADDITIONAL POLES (MID SPAN) FOR LT LINE WITH AB CABLE
2018-19
S. No. | PARTICULARS | New Bin Code | Unit | Qnty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RSJ (125x70 mm) 9.3 Mtr long @ 13.198 kg | 7130600635 | Kg | 122.74 | 39.5051 | 4848.8609
2 | Concreting of Pole @ 0.05 Cmt for base pad and support @ 0.3 Cmt per pole (1:3:6) | 7130200202 | Cmt | 0.35 | 2510.8 | 878.78 | only material cost (excluding labour & G.S.T.)
3 (i) | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 1 | 428.94 | 428.94
(ii) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 4 | 84.3 | 337.2
(iii) | Universal distribution connector (1 No. per pole) | 7130390006 | No | 1 | 119.8 | 119.8
4 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | 7131950012 | No | 1 | 1193.13 | 1193.13
5 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 1 | 114.85 | 114.85
6 | SUB TOTAL-1 |  |  |  |  | 7921.5609
7 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 712.9405
8 | Labour charges for concreting |  | Cmt | 0.35 | 578.8434 | 202.5952
9 | Labour charges [as per Sch. No.- DL-6(B)] |  |  |  |  | 1902.86
10 | Transportation charges |  |  |  |  | 631.0549
11 | SUB TOTAL-2 |  |  |  |  | 11371.0115
12 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 990.1951
13 | Total Cost per |  |  |  |  | 12361.2066
14 | Total cost (R/Off) |  |  |  |  | 12361

## D-7
COST SCHEDULE D-7
HVDS SYSTEM OF 200 kVA PARENT DTR TAKING 4 Km. LT. TO BE CONVERTED.
2018-19
S. No. | PARTICULARS | Bin Code | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient)
(i) | 25 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210018 | No | 49457.85 | 5 | 247289.25
(ii) | 16 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210017 | No | 44158.56 | 4 | 176634.24
2 | 140 Kg 8 Mtr. Long PCC Pole (for mid span) | 7130800012 | No | 2255.2 | 10 | 22552
3 | (i) Stay Set 16 mm | 7130860032 | No | 441.23 | 40 | 17649.2
| (ii) Stay Wire 7/10 SWG (5.5 Kg/stay) | 7130860077 | Kg | 70.4396 | 220 | 15496.7208
| (iii) Stay Clamp for 140 kg PCC | 7130810026 | Pair | 155.99 | 40 | 6239.6
4 | Transformer mounting cross arm DC channel 100x50x6 mm. 2.7 mtr long 8' Centre | 7130850201 | Set | 4590.18 | 11 | 50491.98
5 | D.O. mounting Channel | 7130810509 | Set | 1676.77 | 11 | 18444.47
6 | DC Channel 100x50x6 mm | 7130850201 | Set | 4590.18 | 11 | 50491.98
7 | 11 kV Single pole cut point fitting | 7130810681 | Set | 3257.64 | 10 | 32576.4
8 | 11 kV Strain Hardware set | 7130820241 | No | 119.62 | 60 | 7177.2
9 | 11 kV Polymer Disc Insulator | 7130820010 | No | 128.45 | 60 | 7707
10 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 504.66 | 33 | 16653.78
11 | 11 kV D.O. Fuse Unit | 7131930412 | No | 1177.88 | 33 | 38870.04
12 | Protection cum metering box with 40 amp. MCCB & 4 No. 3 phase meter. |  | No | 16000 | 7 | 112000
13 | Protection cum metering box with 25 amp. MCCB & 3 No. 3 phase meter. |  | No | 13000 | 4 | 52000
14 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 28.1566 | 220 | 6194.4498
15 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 55.8925 | 10400 | 581282
16 | G.I. Pipe 40 mm (9 Mtr. per sub-station) | 7130641396 | Mtr | 215.22 | 99 | 21306.78
17 | G.I. Wire 8 SWG | 7130870043 | Kg | 63 | 660 | 41579.9736
18 | 11 kV 'V' Cross arm | 7130810495 | No | 1057.95 | 65 | 68766.75
19 | 11 kV Top Clamp | 7130810679 | No | 296.79 | 65 | 19291.35
20 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 142.14 | 195 | 27717.3
21 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 114.85 | 65 | 7465.25
22 | M.S. Nuts and Bolts |  | Kg |  | 320
| 16x40 mm | 7130620609 | Kg | 69.38 | 50 | 3469
| 16x65 mm | 7130620614 | Kg | 68.22 | 100 | 6822
| 16x90 mm | 7130620619 | Kg | 68.22 | 20 | 1364.4
| 16x140 mm | 7130620625 | Kg | 67.06 | 50 | 3353
| 16x160 mm | 7130620627 | Kg | 67.06 | 50 | 3353
| 16X200 mm | 7130620631 | Kg | 67.06 | 50 | 3353
23 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 50
| RCC Block (with 6 mm MS Bar) ** | 7130640008 | Each | 158 | 90 | 14220 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
24 | I- Bolt 16 mm | 7130860017 | No | 105.19 | 77 | 8099.63
25 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 20.6046 | 1200 | 24725.556
26 | SUB TOTAL-1 |  |  |  |  | 1714637.3002
27 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 154317.357
28 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 199.5971 | 10 | 1995.9706
29 | Labour charges [as per Sch. No.- DL-10] |  |  |  |  | 205541.19
30 | Transportation charges |  |  |  |  | 10728.2493
31 | SUB TOTAL-2 |  |  |  |  | 2087220.067
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 214329.6625
33 | Total cost per Km for non-guaranteed works |  |  |  |  | 2301549.7296
34 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 2301550
Note: All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
* | ISI Marked Energy Efficiency level-2 transformer
** | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on D15: 89326879: Earlier unit was - No.
Note on D19: 89326879: Earlier unit was - No.

## D-8
COST SCHEDULE D-8
HVDS SYSTEM OF 100 kVA PARENT DTR TAKING 3 KM. LT TO BE CONVERTED
2018-19
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient)
(i) | 25 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210018 | No. | 49457.85 | 2 | 98915.7
(ii) | 16 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210017 | No. | 44158.56 | 3 | 132475.68
2 | 140 Kg 8 Mtr. Long PCC pole (for mid span) | 7130800012 | No. | 2255.2 | 8 | 18041.6
3 | (i) Stay Set 16 mm | 7130860032 | No. | 441.23 | 30 | 13236.9
| (ii) Stay Wire 7/10 (5.5 kg/stay) | 7130860077 | Kg | 70.4396 | 165 | 11622.5406
| (iii) Stay Clamp for 140 kg PCC | 7130810026 | Pair | 155.99 | 30 | 4679.7
4 | Transformer mounting cross arm DC channel 100x50x6 mm. 2.7 mtr long 8' centre | 7130850201 | Set | 4590.18 | 7 | 32131.26
5 | DC Cross arm 100x50x6 mm 8 ' centre 2.7 mtr long | 7130850201 | Set | 4590.18 | 7 | 32131.26
6 | DO mounting Channel | 7130810509 | Set | 1676.77 | 11 | 18444.47
7 | 11 kV Single pole cut point channel | 7130810681 | Set | 3257.64 | 10 | 32576.4
8 | 11 kV Strain Hardware set | 7130820241 | No | 119.62 | 48 | 5741.76
9 | 11 kV Polymer Disc Insulator | 7130820010 | No | 128.45 | 48 | 6165.6
10 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 504.66 | 21 | 10597.86
11 | 11 kV D.O. Set | 7131930412 | No | 1177.88 | 21 | 24735.48
12 | Protection cum metering box with 40 amp. MCCB & 4 No. 3 phase meter for 25 kVA X-mer |  | No | 16000 | 3 | 48000
13 | Protection cum metering box with 25 amp. MCCB & 3 No. 3 phase meter for 16 kVA X-mer |  | No | 13000 | 4 | 52000
14 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 28.1566 | 140 | 3941.9226
15 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 55.8925 | 1820 | 101724.35
16 | G.I. Pipe 40 mm (5 Mtr. per substation) | 7130641396 | Mtr | 215.22 | 63 | 13558.86
17 | G.I. Wire 8 SWG | 7130870043 | Kg | 63 | 180 | 11339.9928
18 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1057.95 | 45 | 47607.75
19 | 11 kV Top clamp | 7130810679 | No | 296.79 | 45 | 13355.55
20 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 142.14 | 135 | 19188.9
21 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 45 | 5168.25
22 | M.S. Nuts and Bolts |  | Kg |  | 250
| 16x40 mm | 7130620609 | Kg | 69.38 | 40 | 2775.2
| 16x65 mm | 7130620614 | Kg | 68.22 | 80 | 5457.6
| 16x90 mm | 7130620619 | Kg | 68.22 | 10 | 682.2
| 16x140 mm | 7130620625 | Kg | 67.06 | 40 | 2682.4
| 16x160 mm | 7130620627 | Kg | 67.06 | 40 | 2682.4
| 16X200 mm | 7130620631 | Kg | 67.06 | 40 | 2682.4
23 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 38
| RCC Block (with 6 mm MS Bar) ** | 7130640008 | Each | 158 | 68 | 10744 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
24 | I - Bolt 16 mm | 7130860017 | No | 105.19 | 21 | 2208.99
25 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 20.6046 | 900 | 18544.167
26 | SUB TOTAL-1 |  |  |  |  | 805841.143
27 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 72525.7029
28 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 199.5971 | 8 | 1596.7764
29 | Labour charges [as per Sch. No.- DL-11] |  |  |  |  | 150841.09
30 | Transportation charges |  |  |  |  | 8582.5953
31 | SUB TOTAL-2 |  |  |  |  | 1039387.3077
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 100730.1429
33 | Total cost per Km for non-guaranteed works |  |  |  |  | 1140117.4505
34 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 1140117
Note: All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
* | ISI Marked Energy Efficiency level-2 transformer
** | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on D15: 89326879: Earlier unit was - No.
Note on D19: 89326879: Earlier unit was - No.

## D-9
COST SCHEDULE D-9
HVDS SYSTEM OF 63 kVA PARENT DTR TAKING 2 KM. LT TO BE CONVERTED
2018-19
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient)
(i) | 25 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210018 | No | 49457.85 | 1 | 49457.85
(ii) | 16 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210017 | No | 44158.56 | 2 | 88317.12
2 | 140 Kg 8 Mtr. Long PCC Pole (for mid span) | 7130800012 | No | 2255.2 | 6 | 13531.2
3 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 441.23 | 25 | 11030.75
| (ii) Stay Wire 7/10 SWG (5.5 kg/stay) | 7130860077 | Kg | 70.4396 | 137.5 | 9685.4505
| (iii) Stay Clamp for 140 kg PCC Pole | 7130810026 | Pair | 155.99 | 25 | 3899.75
4 | Transformer mounting arrangement DC cross arm 100x50x6 mm. 2.7 mtr long 8' Centre | 7130850201 | Set | 4590.18 | 5 | 22950.9
5 | DC cross arm 100x50x6 mm 8 ' Centre 2.7 mtr long | 7130850201 | Set | 4590.18 | 5 | 22950.9
6 | DO Mounting Channel | 7130810509 | Set | 1676.77 | 5 | 8383.85
7 | 11 kV Single Pole cut point channel | 7130810681 | Set | 3257.64 | 10 | 32576.4
8 | 11 kV Strain Hardware set | 7130820241 | Set | 119.62 | 36 | 4306.32
9 | 11 kV Polymer Disc Insulator | 7130820010 | No | 128.45 | 36 | 4624.2
10 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 504.66 | 15 | 7569.9
11 | 11 kV D.O. Set | 7131930412 | No | 1177.88 | 15 | 17668.2
12 | Protection cum metering box with 40 Amp. MCCB & 4 No. 3 phase meter for 25 kVA X-mer |  | No | 16000 | 2 | 32000
13 | Protection cum metering box with 25 Amp. MCCB & 3 No. 3 phase meter for 16 kVA X-mer |  | No | 13000 | 3 | 39000
14 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 28.1566 | 100 | 2815.659
15 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 55.8925 | 1300 | 72660.25
16 | G.I. Pipe 40 mm (5 Mtr. per Sub-station) | 7130641396 | Mtr | 215.22 | 45 | 9684.9
17 | G.I. Wire 8 SWG | 7130870043 | Kg | 63 | 130 | 8189.9948
18 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1057.95 | 45 | 47607.75
19 | 11 kV Top clamp | 7130810679 | No | 296.79 | 45 | 13355.55
20 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 142.14 | 135 | 19188.9
21 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 114.85 | 45 | 5168.25
22 | M.S. Nuts and Bolts |  | Kg |  | 190
| 16x40 mm | 7130620609 | Kg | 69.38 | 30 | 2081.4
| 16x65 mm | 7130620614 | Kg | 68.22 | 60 | 4093.2
| 16x90 mm | 7130620619 | Kg | 68.22 | 10 | 682.2
| 16x140 mm | 7130620625 | Kg | 67.06 | 30 | 2011.8
| 16x160 mm | 7130620627 | Kg | 67.06 | 30 | 2011.8
| 16X200 mm | 7130620631 | Kg | 67.06 | 30 | 2011.8
23 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 31
| RCC Block (with 6 mm MS Bar) ** | 7130640008 | Each | 158 | 56 | 8848 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
24 | I - Bolt 16 mm | 7130860017 | No | 105.19 | 10 | 1051.9
25 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 20.6046 | 600 | 12362.778
26 | SUB TOTAL-1 |  |  |  |  | 581778.9223
27 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 52360.103
28 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 199.5971 | 6 | 1197.5823
29 | Labour charges [as per Sch. No.- DL-12] |  |  |  |  | 113945.61
30 | Transportation charges |  |  |  |  | 6436.9516
31 | SUB TOTAL-2 |  |  |  |  | 755719.1692
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 72722.3653
33 | Total cost per Km for non-guaranteed works |  |  |  |  | 828441.5345
34 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 828442
Note:- | All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
* | ISI Marked Energy Efficiency level-2 transformer
** | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on D15: 89326879: Earlier unit was - No.
Note on D19: 89326879: Earlier unit was - No.

## D-10
COST SCHEDULE D-10
CONVERSION OF 1 KM LT LINE INTO 11 kV LINE
2018-19
S. No. | PARTICULARS | New Bin Code | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Poles (for where ever required ) | 7130800012 | No | 1 | 2255.2 | 2255.2
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 17 | 1057.95 | 17985.15
3 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 17 | 296.79 | 5045.43
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 17 | 114.85 | 1952.45
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 51 | 142.14 | 7249.14
6 | Jointing sleeves suitable for Weasel/ Rabbit conductor | 7130830854 | No | 6 | 29.14 | 174.84
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 146.77 | 440.31
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 327.94 | 983.82
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 17 | 76.075 | 1293.2755
10 | Danger Board | 7130880041 | No | 17 | 89.74 | 1525.58
11 | Binding wires & tape | 7130830006 | Kg | 5 | 155.45 | 777.25
12 | Nuts and bolts
| 16x90 mm | 7130620619 | Kg | 2 | 68.22 | 136.44
| 16x160 mm | 7130620627 | Kg | 17 | 67.06 | 1140.02
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2508.6 | 2508.6
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 63 | 2204.9986
| (iii) Stay clamp (Pair) H.T. | 7130810026 | No | 2 | 291.13 | 582.26
| (iv) Stay wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 70.4396 | 774.836
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 441.23 | 882.46
| (vi) I - Bolt big size. | 7130620013 | No | 4 | 124.12 | 496.48
14 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  | 3
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 5 | 158 | 790 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
15 | SUB TOTAL-1 |  |  |  |  | 49198.5402
16 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 4427.8686
17 | Back filling of poles with boulders @ of 0.3 Cmt per pole |  | No | 1 | 199.5971 | 199.5971
18 | Labour charges as per Schedule No. DL-3 (E-1) |  |  |  |  | 33362.06
19 | Transport charges upto 50 Kms. Average lead from area store to const. camping site transport |  |  |  |  | 4184.018
20 | SUB TOTAL-2 |  |  |  |  | 91372.0838
21 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 6149.8175
22 | Cost per Km. for Non guaranteed works |  |  |  |  | 97521.9014
23 | Cost per Km. for Non guaranteed works (Rounded off) |  |  |  |  | 97522
Note:- | (i) Three wire LT line will be utilized for converting into 11 kV line.
(ii) For replacement of deteriorated conductor of LT line suitable provision should be made while preparing the estimates
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)

## D-11
COST SCHEDULE D-11
2018-19
LT LINE CONVERSION USING RABBIT CONDUCTOR MAXIMUM SPAN OF 45 MTRS.
S. No. | PARTICULARS | New Bin code | Unit | Rate | 1 Phase 2 Wire to 1 Phase 3 Wire Conversion |  | 1 Phase 2 Wire to 3 Phase 4 Wire Conversion |  | 1 Phase 3 Wire to 3 Phase 4 Wire Conversion |  | 1 Phase 3 Wire to 3 Phase 5 Wire Conversion
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | LT Three Pin cross arm | 7130810413 | No | 623.86 | 24 | 14972.64
2 | LT Four Pin cross arm | 7130810441 | No | 742.99 |  |  | 24 | 17831.76 | 24 | 17831.76
3 | LT Five Pin cross arm | 7130810461 | No | 862.11 | [6 empty] | 24 | 20690.64
4 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 12.82 | 24 | 307.68 | 48 | 615.36 | 24 | 307.68 | 48 | 615.36
5 | Hardware for Shackle Insulator | 7130820216 | No | 40.64 | 8 | 325.12 | 16 | 650.24 | 8 | 325.12 | 16 | 650.24
6 | ACSR RABBIT Conductor including 3% Sag | 7130830057 | Mtr | 33.9486 | 1030 | 34967.0374 | 2060 | 69934.0748 | 1030 | 34967.0374 | 2060 | 69934.0748
7 | Split insulator for guarding | 7130820018 | Pair | 4.05 | 40 | 162 | 40 | 162 | 40 | 162 | 40 | 162
8 | M.S. Nuts & bolts
| 12x100 mm | 7130620573 | Kg | 69.38 | 4 | 277.52 | 8 | 555.04 | 4 | 277.52 | 8 | 555.04
| 16x40 mm | 7130620609 | Kg | 69.38 | 4 | 277.52 | 6 | 416.28 | 4 | 277.52 | 6 | 416.28
| 16x140 mm | 7130620625 | Kg | 67.06 | 10 | 670.6 | 10 | 670.6 | 10 | 670.6 | 10 | 670.6
| 16x65 mm | 7130620614 | Kg | 68.22 | 6 | 409.32 | 6 | 409.32 | 6 | 409.32 | 6 | 409.32
9 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 1 | 146.77 | 1 | 146.77 | 1 | 146.77 | 1 | 146.77
10 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 1 | 327.94 | 1 | 327.94 | 1 | 327.94 | 1 | 327.94
11 | G.I. Wire 4 mm for guarding | 7130870043 | Kg | 63 | 6 | 377.9998 | 7.5 | 472.4997 | 7.5 | 472.4997 | 7.5 | 472.4997
12 | Clamp for R.S. Joist or PCC 140 Kg./8 mtr long | 7130810216 | Pair | 309.8 | 20 | 6196 | 20 | 6196 | 20 | 6196 | 20 | 6196
13 | SUB TOTAL-1 |  |  |  |  | 59418.1472 |  | 98387.8845 |  | 62371.7671 |  | 101246.7645
14 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 5347.6332 |  | 8854.9096 |  | 5613.459 |  | 9112.2088
15 | Labour Charges as per DL-4. |  |  |  |  | 13553.88 |  | 19675.36 |  | 13553.88 |  | 19675.36
16 | Transportation Charges |  |  |  |  | 3347.2165 |  | 3974.8176 |  | 3347.2165 |  | 3974.8176
17 | SUB TOTAL-2 |  |  |  |  | 81666.8769 |  | 130892.9717 |  | 84886.3226 |  | 134009.1509
18 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 7427.2684 |  | 12298.4856 |  | 7796.4709 |  | 12655.8456
19 | Grand Total |  |  |  |  | 89094.1453 |  | 143191.4573 |  | 92682.7935 |  | 146664.9965
20 | Total (rounding off) |  |  |  |  | 89094 |  | 143191 |  | 92683 |  | 146665
Note on D23: 89326879: Earlier unit was - No.

## D-12
COST SCHEDULE D-12 ( E-2)
2018-19
CONVERSION OF 1 KM 1 PHASE 3 WIRE LT LINE INTO 11 kV LINE
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Pole (for where ever required ) | 7130800012 | No | 1 | 2255.2 | 2255.2
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 22 | 1057.95 | 23274.9
3 | 11 kV Top clamp Angle type with cleat. | 7130810679 | No | 22 | 296.79 | 6529.38
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 22 | 114.85 | 2526.7
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 66 | 142.14 | 9381.24
6 | Jointing sleeves suitable for weasel / rabbit conductor | 7130830854 | No | 6 | 29.14 | 174.84
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 146.77 | 440.31
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 327.94 | 983.82
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 22 | 76.075 | 1673.6507
10 | Danger Board | 7130880041 | No | 22 | 89.74 | 1974.28
11 | Binding wire & tape | 7130830006 | Kg | 5 | 155.45 | 777.25
12 | Nuts and Bolts
| 16x90 mm | 7130620619 | Kg | 2 | 68.22 | 136.44
| 16x160 mm | 7130620627 | Kg | 17 | 67.06 | 1140.02
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 12 | 2508.6 | 30103.2
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 441 | 63 | 27782.9824
| (iii) Stay Clamp (Pair) H.T. | 7130810026 | No | 2 | 291.13 | 582.26
| (iv) Stay Wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 70.4396 | 774.836
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 441.23 | 882.46
| (vi) I- Bolt big size. | 7130620013 | No. | 4 | 124.12 | 496.48
14 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  | 3
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 5 | 158 | 790 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
15 | PVC Insulated cable 16 sqmm 1 core unarmoured | 7130311008 | Mtr. | 2104 | 18.1746 | 38239.4426
16 | ACSR Conductor 20 sqmm. Al. Eq. for neutral | 7130830053 | Mtr | 1030 | 14.0663 | 14488.289
17 | SUB TOTAL-1 |  |  |  |  | 165407.9806
18 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 14886.7183
19 | Back filling of pole with boulders @ 0.3 Cmt. per pole. |  | No. | 1 | 199.5971 | 199.5971
20 | Labour charges as per Schedule No. DL-5 ( E-2) |  |  |  |  | 48898.2
21 | Transport charges upto 50 Kms. Average lead from Area Store to construction camping site transport |  |  |  |  | 4184.018
22 | SUB TOTAL-2 |  |  |  |  | 233576.514
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 20675.9976
24 | Cost per Km. for Non guaranteed works |  |  |  |  | 254252.5115
25 | Cost per Km. for Non guaranteed works (Rounded off) |  |  |  |  | 254253
Note:- | (1) In 1 Phase 3 Wire L.T. three wire conductor will be reutilised.
(2) In Case of replacement of Old conductor, new conductor may be incorporated in the estimate and depreciated value will be accounted for in the estimate.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)

## D-13
COST SCHEDULE D-13 (E-3)
CONVERSION OF 1 kM 3 PHASE 5 WIRE LT LINE INTO 11 kV LINE
2018-19
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Pole (for where ever required) | 7130800012 | No | 1 | 2255.2 | 2255.2
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 22 | 1057.95 | 23274.9
3 | 11 kV Top Clamp Angle type with cleat. | 7130810679 | No | 22 | 296.79 | 6529.38
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 22 | 114.85 | 2526.7
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 66 | 142.14 | 9381.24
6 | Jointing sleeves suitable for weasel / rabbit conductor | 7130830854 | No | 6 | 29.14 | 174.84
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 146.77 | 440.31
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 327.94 | 983.82
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 22 | 76.075 | 1673.6507
10 | Danger Board | 7130880041 | No | 22 | 89.74 | 1974.28
11 | Binding wire & tape | 7130830006 | Kg | 5 | 155.45 | 777.25
12 | Nuts and Bolts
| 16x90 mm | 7130620619 | kg | 2 | 68.22 | 136.44
| 16x160 mm | 7130620627 | kg | 17 | 67.06 | 1140.02
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 23 | 2508.6 | 57697.8
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 441 | 63 | 27782.9824
| (iii) Stay Clamp (Pair) H.T. | 7130810026 | No | 2 | 291.13 | 582.26
| (iv) Stay Wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 70.4396 | 774.836
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 441.23 | 882.46
| (vi) I-Bolt big size. | 7130620013 | No. | 4 | 124.12 | 496.48
14 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  | 3
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 5 | 158 | 790 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
15 | PVC insulated cable 16 sqmm 1 core unarmoured | 7130311008 | Mtr. | 2104 | 18.1746 | 38239.4426
16 | ACSR Conductor 20 sqmm. Al. Eq. for neutral | 7130830053 | Mtr | 1030 | 14.0663 | 14488.289
17 | SUB TOTAL-1 |  |  |  |  | 193002.5806
18 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 17370.2323
19 | Back filling of pole with boulders @ 0.3 Cmt. per pole. |  | No. | 1 | 199.5971 | 199.5971
20 | Labour charges as per Schedule No. DL-6 (E-3) |  |  |  |  | 51062.76
21 | Transport charges upto 50 Kms. Average lead from Area Store to construction camping site transport |  |  |  |  | 4184.018
22 | SUB TOTAL-2 |  |  |  |  | 265819.188
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 24125.3226
24 | Cost per Km. for Non guaranteed works |  |  |  |  | 289944.5105
25 | Cost per Km. for Non guaranteed works (Rounded off) |  |  |  |  | 289945
Note:- | (1) In 3 Phase 5 Wire LT system, 5th conductor i.e. neutral conductor and 4th conductor will be returned to Area Stores and depreciated value of neutral conductor will be accounted for at the time of estimate framing. L.T. Phase conductor will be reutilised.
(2) In case of replacement of Old conductor, new conductor may be incorporated in the estimate and depreciated value will be accounted for in the estimate.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)

## D-14
COST SCHEDULE -- D-14
DISTRIBUTION BOX ON EXISTING LT LINES FOR SERVICE CONNECTIONS
2018-19
S. No. | DESCRIPTION | Bin Code No | UNIT | Rate per Distribution Box | Incidental Charges (9%) | Labour Charges per Distribution Box | Cost per Distribution Box | Cost per Distribution Box Round Off
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Single phase Distribution box for 9 connections | 7131950010 | Nos. | 990.47 | 89.1423 | 135.319 | 1214.9313 | 1215
2 | Three phase Distribution box for 5 connections | 7131950012 | Nos. | 1193.13 | 107.3817 | 135.319 | 1435.8307 | 1436
| Incidental Charges @ 9% : - |  |  | 9%

## E-1
COST SCHEDULE -- E-1
METERING OF 11/0.4 kV DISTRIBUTION TRANSFORMER (TO BE SUPPLEMENTED WITH COST SCHEDULE C-7 (A1, A2, B1, B2, C1, C2)
2018-19
S. No. | PARTICULARS | Bin Code No | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1(a) | Poly phase static energy meter 10-60 Amp. with meter box | 7131300046 | No | 1 | 1621.45 | --
1(b) | CT operated electronic static meter 100/5 Amp. | 7131310997 | No | 1 | 1639.61 | 1639.61 | 1 | 1639.61 | 1639.61 | 1 | 1639.61 | 1639.61 | 1 | 1639.61 | 1639.61
2 | LT CT :-
| (i) 100/5 Amp. | 7132230016 | No | 4 | 345.07 | 1380.28 | 4 | 345.07 | 1380.28 | -- | -- | -- | -- | -- | --
| (ii) 200/5 Amp. | 7132230019 | No | -- | -- | -- | -- | -- | -- | 4 | 345.07 | 1380.28 | -- | -- | --
| (iii) 300/5 Amp. | 7132230021 | No | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | 276.27 | 1105.08
3 | Meter Box (G.I. Plain sheet) for 3 Phase LT CT operated meter. | 7132406420 | No | 1 | 2580.37 | 2580.37 | 1 | 2580.37 | 2580.37 | 1 | 2580.37 | 2580.37 | 1 | 2580.37 | 2580.37
4 | Copper control cable 4 core 2.5 sq.mm Unarmoured | 7130310654 | Mtr | 12 | 62.7585 | 753.1025 | 12 | 62.7585 | 753.1025 | 12 | 62.7585 | 753.1025 | 12 | 62.7585 | 753.1025
5 | SUB TOTAL-1 |  |  |  |  | 6353.3625 |  |  | 6353.3625 |  |  | 6353.3625 |  |  | 6078.1625
6 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 571.8026 |  | 0.09 | 571.8026 |  | 0.09 | 571.8026 |  | 0.09 | 547.0346
7 | Labour & Transportation charges |  |  |  |  | 2531.3309 |  |  | 2531.3309 |  |  | 2531.3309 |  |  | 2531.3309
8 | SUB TOTAL-2 |  |  |  |  | 9456.496 |  |  | 9456.496 |  |  | 9456.496 |  |  | 9156.528
9 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 794.1703 |  | 0.125 | 794.1703 |  | 0.125 | 794.1703 |  | 0.125 | 759.7703
10 | Cost of Metering for non-guaranteed works |  |  |  |  | 10250.6663 |  |  | 10250.6663 |  |  | 10250.6663 |  |  | 9916.2983
11 | Cost of Metering for non-guaranteed works (Rounded off). |  |  |  |  | 10251 |  |  | 10251 |  |  | 10251 |  |  | 9916
Note:- All the rates are with considering price variation clause.
38

## E-2
COST SCHEDULE -- E-2
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| SINGLE PHASE CONNECTION |  |  |  |  | 2018-19
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT Single Phase Static Meter 5-30 Amps. Pilfer Proof with transparent polycarbonate meter box | 7131300500 | No | 1 | 695.5 | 695.5 | 695.5 | 695.5
2 | Armoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130311025 | Mtr | 30 | 39.05 | 1171.5
3 | Unarmoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130310039 | Mtr | 30 |  |  | 29.08 | 872.4
4 | LT Shackle Insulator 65x50 mm | 7130820101 | No | 2 | 11.31 | 22.62 | 11.31 | 22.62
5 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No | 2 | 35.7 | 71.4 | 35.7 | 71.4
6 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | 7132406022 | No | 1 | 147.22 | 147.22 | 147.22 | 147.22
7 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.29 | 14.29 | 14.29 | 14.29
8 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 40 | 40 | 40 | 40
9 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
10 | SUB TOTAL-1 |  |  |  |  | 2192.53 |  | 1893.43
11 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 197.3277 | 0.09 | 170.4087
12 | Labour Charges |  | Per Installation |  |  | 252.3697 |  | 252.3697
13 | Cost for meter replacement of a Single Phase Consumer |  |  |  |  | 2642.2274 |  | 2316.2084
14 | Cost for meter replacement of a Single Phase Consumer (Round off) |  |  |  |  | 2642 |  | 2316

## E-3
COST SCHEDULE -- E-3
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| THREE PHASE CONNECTION |  |  |  |  | 2018-19
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT 3 phase electronic energy meter 10-60 Amps. with poly carbonate meter box | 7131300046 | No. | 1 | 1621.45 | 1621.45 | 1621.45 | 1621.45
2 | Armoured Service Cable - Three Phase, 4 core-10 sq mm | 7130311028 | Mtr | 30 | 68.07 | 2042.1
3 | Unarmoured Service Cable - Three Phase, 4 core-10 sq mm | 7130310040 | Mtr | 30 |  |  | 60.26 | 1807.8
4 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 11.31 | 22.62 | 11.31 | 22.62
5 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 35.7 | 71.4 | 35.7 | 71.4
6 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | 7132455002 | Nos | 1 | 307.92 | 307.92 | 307.92 | 307.92
7 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.29 | 14.29 | 14.29 | 14.29
8 | Misc Items , e.g., Screw, cut-outs |  | Lot | 1 | 40 | 40 | 40 | 40
9 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
10 | SUB TOTAL-1 |  |  |  |  | 4149.78 |  | 3915.48
11 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 373.4802 | 0.09 | 352.3932
12 | Labour Charges |  | Per Installation |  |  | 403.7915 |  | 403.7915
13 | Cost for meter replacement of a Three Phase Consumer |  |  |  |  | 4927.0517 |  | 4671.6647
14 | Cost for meter replacement of a Three Phase Consumer (Round Off) |  |  |  |  | 4927 |  | 4672
| No of Consumers for Meter Replacement |  |  | 100
| Total Cost |  |  |  |  | 492705.17 |  | 467166.47
| Total Cost Round Off |  |  |  |  | 492705 |  | 467166

## E-4
COST SCHEDULE -- E-4
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| THREE PHASE CONNECTION CT- OPERATED METERS |  |  |  |  | 2018-19
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Rate | Amount
1 | CT Operated Electronic Static Meters 100/5 Amp. with data storage | 7131310997 | No. | 1 | 1639.61 | 1639.61
2 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.29 | 14.29
3 | Misc Items , e.g., Screw, cut-outs |  | Lot | 1 | 40 | 40
4 | M-Seal |  | Lot | 1 | 30 | 30
5 | SUB TOTAL-1 |  |  |  |  | 1723.9
6 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 155.151
7 | Labour Charges |  | Per Installation |  |  | 403.7915
8 | Cost for meter replacement of Three Phase Consumer CT Operated Meters |  |  |  |  | 2282.8425
9 | Cost for meter replacement of 3- Phase Consumer CT Operated Meters (Round Off) |  |  |  |  | 2283

## E-5
COST SCHEDULE -- E-5
METER SHIFTING OF SINGLE PHASE CONSUMER TO OUTSIDE OF PREMISES WITH NEW SERVICE CABLE
| SINGLE PHASE CONNECTION | [5 empty] | 2018-19
S. No. | PARTICULARS | Bin Code No. | Unit | Qty. | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Armoured Service Cable - Single Phase, 2 core- 6 sq. mm. | 7130311025 | Mtr | 30 | 39.05 | 1171.5
2 | Unarmoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130310039 | Mtr | 30 |  |  | 29.08 | 872.4
3 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 11.31 | 22.62 | 11.31 | 22.62
4 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 35.7 | 71.4 | 35.7 | 71.4
5 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | 7132406022 | Nos | 1 | 147.22 | 147.22 | 147.22 | 147.22
6 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.29 | 14.29 | 14.29 | 14.29
7 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 40 | 40 | 40 | 40
8 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
9 | SUB TOTAL-1 |  |  |  |  | 1497.03 |  | 1197.93
10 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 134.7327 | 0.09 | 107.8137
11 | Labour Charges |  | Per Installation |  |  | 252.3697 |  | 252.3697
12 | Cost for meter shifting of a Single Phase Consumer |  |  |  |  | 1884.1324 |  | 1558.1134
13 | Cost for meter shifting of a Single Phase Consumer (Round Off) |  |  |  |  | 1884 |  | 1558

## E-6
COST SCHEDULE -- E-6
METER SHIFTING OF THREE PHASE CONSUMER TO OUTSIDE OF PREMISES WITH NEW SERVICE CABLE
| THREE PHASE CONNECTION | [5 empty] | 2018-19
S. No. | PARTICULARS | Bin Code No. | Unit | Qty. | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Armoured Service Cable - Three Phase, 4 core-10 sq mm | 7130311028 | Mtr | 30 | 68.07 | 2042.1
2 | Unarmoured Service Cable - Three Phase, 4 core-10 sq mm | 7130310040 | Mtr | 30 |  |  | 60.26 | 1807.8
3 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 11.31 | 22.62 | 11.31 | 22.62
4 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 35.7 | 71.4 | 35.7 | 71.4
5 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | 7132455002 | Nos | 1 | 307.92 | 307.92 | 307.92 | 307.92
6 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.29 | 14.29 | 14.29 | 14.29
7 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 40 | 40 | 40 | 40
8 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
9 | SUB TOTAL-1 |  |  |  |  | 2528.33 |  | 2294.03
10 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 227.5497 | 0.09 | 206.4627
11 | Labour Charges |  | Per Installation |  |  | 403.7915 |  | 403.7915
12 | Cost for meter shifting of a Three Phase Consumer |  |  |  |  | 3159.6712 |  | 2904.2842
13 | Cost for meter shifting of a Three Phase Consumer (Round Off) |  |  |  |  | 3160 |  | 2904