## Sheet1
COMPARATIVE STATEMENT OF RATES FROM YEAR 2014-15 to 2015-16
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2014-15 | 2015-16 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
PART-I, 33 kV LINES AND D.P. STRUCTURES
(A) |  | 33 kV line on PCC Pole / H-Beam poles with Raccoon conductor.
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-1(i) | Per Km | 306120 | 318910 | 4.1781
| ii | On H-Beam 152 x 152 mm 37.1 Kg/ Mtr 13 Mtr long | A-1(ii) | Per Km | 536088 | 557162 | 3.9311
| iii | On 365 Kg 11 Mtrs long PCC poles | A-1(iii) | Per Km | 0 | 370283
(B) |  | 33 kV Four Pole structure on PCC / H-Beam Pole | A-2 (A)
| i | PCC Pole | A-2 (A) (i) | Each | 272411 | 288048 | 5.7402
| ii | H-Beam Pole | A-2 (A) (ii) | Each | 363478 | 373903 | 2.8681
(C) |  | 33 kV DP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-2 (B)(i) | Each | 57296 | 61904 | 8.0424
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-2 (B)(ii) | Each | 101150 | 104589 | 3.3999
| iii | On 365 Kg 11 Mtrs long PCC poles | A-2 (B)(iii) | Each | 0 | 67396
(D) |  | 33 kV line on PCC Pole / H-Beam Pole with Dog conductor.
| i | On 280 Kg, 9.1 Mtrs long PCC poles | A-3(i) | Per Km | 357246 | 375986 | 5.2457
| ii | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3(ii) | Per Km | 600081 | 611998 | 1.9859
| iii | On 365 Kg 11 Mtrs long PCC poles | A-3(iii) | Each | 0 | 425051
(E) |  | Augmentation of 1 km. of 33 kV line from Raccoon to Dog conductor. | A-3 (A) | Per Km | 235703 | 251645 | 6.7636
(F) |  | Additional (Mid Span) Pole for 33 kV Line | A-3 (B)
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3 (B)(i) | Per No. | 35717 | 35554 | -0.45637
(G) |  | 33 kV line on H-Beam supports suspension type with Panther Conductor (Maximum span of 50 Mtrs) | A-4
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-4 (i) | Per Km | 1638014 | 1721183 | 5.0774
(H) |  | 33 kV DP Structure on H-Beam supports with Panther Conductor | A-5
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-5 (i) | Each | 164187 | 120212 | -26.7835
(I) |  | 33 kV Under ground cable crossing under Railway track for 60 mtr length, under 2.5 mtr deep for ground level single feeder line. | A-6 | 60 Mtr
| i | With 3 core U/G XLPE 240 sqmm Cable | A-6(i) | 60 Mtr | 1992699 | 2103398 | 5.5552
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-6(ii) | 60 Mtr | 2081314 | 2195764 | 5.4989
(J) |  | 33 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level single feeder line | A-6 (A) | 50 Mtr | 597999 | 622517 | 4.1
(K) |  | Last span cabling of 33 kV H.T. Connection
|  | Using H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-7
| i | With 3x185 sq.mm AB XLPE Cable | A-7(i) | 50 Mtr | 189600 | 193119 | 1.856
| ii | With 3x240 sq.mm AB XLPE Cable | A-7(ii) | 50 Mtr | 212258 | 215997 | 1.7615
(L) |  | 33 kV MEDP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-8 (i) | Each | 82183 | 87526 | 6.5013
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-8 (ii) | Each | 120230 | 124266 | 3.3569
(M) |  | Last span cabling of 33 kV line using Covered Conductor of size
| i | 70 sq.mm (207 Amp) | A-9 (i) | 50 Mtr | 0 | 135248
| ii | 99 sq.mm (258 Amp) | A-9 (ii) | 50 Mtr | 0 | 140303
Part-II, 33/11 kV SUB-STATIONS
(A) |  | New Sub-stations:
| i | 1.6 MVA, 33/11 kV S/s expandable to 2 x 1.6 MVA with control room | B-1(i) | Each | 6634021 | 6838505 | 3.0824
| ii | 3.15 MVA, 33/11 kV S/s expandable to 2 x 3.15 MVA with control room | B-1(ii) | Each | 8549974 | 8634577 | 0.98951
| iii | 5 MVA, 33/11 kV S/s expandable to 2 x 5 MVA with control room | B-1(iii) | Each | 10084118 | 10161052 | 0.76292
(B) |  | 33/11 kV Power Transformer
| i | 1.6 MVA | B-2(i) | Each | 962479 | 965128 | 0.27523
| ii | 3.15 MVA | B-2(ii) | Each | 2501861 | 2367879 | -5.3553
| iii | 5.0 MVA | B-2(iii) | Each | 3502418 | 3359986 | -4.0667
(C) |  | Installation of additional transformer for parallel operation with one additional bay on 11 kV side
| i | 1.6 MVA | B-3(i) | Each | 3014649 | 3063366 | 1.616
| ii | 3.15 MVA | B-3(ii) | Each | 4874559 | 4801482 | -1.4992
| iii | 5.0 MVA | B-3(iii) | Each | 5874934 | 5793420 | -1.3875
(D) |  | 11 kV Out door yard extension for additional bay with circuit breaker. | B-4 | Each | 511754 | 515090 | 0.65188
(E) |  | 33 kV Out door yard extension for additional bay without circuit breaker. | B-5 | Each | 220380 | 233004 | 5.7283
(F) |  | Installation of 33 kV VCB | B-6 | Each | 407147 | 420114 | 3.1848
(G) |  | Installation of single phase A.B. Switch on existing feeder outlet DP from 33/11 kV S/s | B-7 | Each | 23249 | 23913 | 2.856
(H) |  | Augmentation of Power Transformer
| i | 1.6 to 3.15 MVA | B-8(i) | Each | 3013852 | 2891595 | -4.0565
| ii | 3.15 to 5.0 MVA without 33 kV VCB | B-8(ii) | Each | 3619193 | 3481958 | -3.7919
| iii | 3.15 to 5.0 MVA with 33 kV VCB | B-8(iii) | Each | 4066488 | 3937967 | -3.1605
(I) |  | Installation of 1.6 MVA 33/11 kV Sub-Station ON LINE | B-9 | Each | 1309512 | 1325735 | 1.2389
PART-III, 11 kV LINES AND D.P.STRUCTURES
(A) |  | 11 kV line on 140 Kg 8.0 Mtr long PCC poles with
| i | Rabbit conductor | C-1(I) | Per Km | 233121 | 244025 | 4.6774
| ii | Weasel conductor | C-1(II) | Per Km | 190865 | 196206 | 2.7983
(B) |  | 11 kV DP structure on 140 Kg, 8.0 Mtr long PCC poles | C-2 | Each | 36138 | 37102 | 2.6676
PART-IV, 11 kV LINES AND D.P.STRUCTURES ON RAIL & H-BEAM
(A) |  | 11 kV line on H-Beam / PCC Pole with Rabbit conductor
| i | On H-Beam 11 meter long | C-3(i) | Per Km | 472265 | 484324 | 2.5534
| ii | On 365 Kg 11 Mtrs long PCC poles | C-3(ii) | Per Km | 0 | 309203
(B) | ii | Additional (Mid span) Poles for 11 kV Line on H-Beam | C-3 (A) | Per No. | 27576 | 27672 | 0.34813
(C) | iii | 11 kV Line on A.B.Cable | C-3 (B) | Per Km
| a | Using H-Beam 152x152 mm, 37.1Kg/mtr 11 Mtrs long supports.
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[i] | Per Km | 1323200 | 1344420 | 1.6037
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[ii] | Per Km | 1455152 | 1481953 | 1.8418
| b | Using 200 Kg; 9.0 Mtr long PCC Pole
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[iii] | Per Km | 703413 | 737869 | 4.8984
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[iv] | Per Km | 835365 | 875402 | 4.7928
(D) | iv | Augmentation of 11 kV Line from Weasel to Raccoon Conductor | C-3 (C) | Per Km | 176245 | 188319 | 6.8507
(E) | v | Augmentation of 11 kV Line from Weasel to Rabbit Conductor | C-3 (D) | Per Km | 124629 | 133008 | 6.7232
(F) | vi | 11 kV Overhead XLPE Cable Line on H-Beam Pole with average span 30 Mtrs. | C-3 (E) | Per Km | 2493728 | 2557916 | 2.574
(G) |  | 11 kV DP structure on
| i | H-Beam 11 meter long | C-4(i) | Each | 79373 | 79655 | 0.35528
| ii | On 365 Kg 11 Mtrs long PCC poles | C-4(ii) | Each | 0 | 50262
(H) |  | 11 kV line on RS Joist (175X85 mm) 11.0 Meters long with
| i | Rabbit conductor | C-5(I) | Per Km | 340870 | 353296 | 3.6454
| ii | Weasel conductor | C-5(II) | Per Km | 298616 | 307878 | 3.1016
(I) |  | 11 kV DP structure on RS Joist 175X85 mm 11.0 Mtr. long | C-6 | Each | 57303 | 57914 | 1.0663
(J) |  | 11 kV line on PCC pole
| a | On 365 Kg 11 Mtrs long PCC poles
| i | Using Raccoon conductor | C-8(I) | Per Km | 0 | 358947
| ii | Using Dog conductor | C-8(II) | Per Km | 0 | 410297
(K) |  | 11 kV line on H-Beam (152x152 mm) 13 meter long with
| i | Raccoon conductor | C-9(I) | Per Km | 566311 | 579209 | 2.2775
| ii | Dog conductor | C-9(II) | Per Km | 613398 | 630559 | 2.7977
(L) |  | Additional (Mid Span) Poles for new 11 kV Line with Raccoon Conductor | C-9(A) | Per No. | 31298 | 31311 | 0.041536
(M) |  | 11 kV under ground cable crossing under railway track for 60 mtr length, under 2.5 mtr deep for ground level | C-12 | 50 Mtr | 1762298 | 1862805 | 5.7032
(N) |  | 11 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level | C-12 (A) | 50 Mtr | 320902 | 333720 | 3.9944
(O) |  | Laying of 1 Km 11 kV Line using
| i | 3 Core 95 Sqmm underground cable | C-15(I) | Per Km | 894647 | 930785 | 4.0394
| ii | 3 Core 240 Sqmm underground cable | C-15(II) | Per Km | 1370399 | 1424669 | 3.9602
| iii | 3 Core 400 Sqmm underground cable | C-15(III) | Per Km | 1938792 | 2014725 | 3.9165
(P) |  | D.T. Capacitors on existing DTR's (Retained & shifted) | C-16
| i | LT Capacitor for 25 kVA DT | C-16 (i) | Per No. | 1942 | 1975 | 1.6993
| ii | LT Capacitor for 63 kVA DT | C-16 (ii) | Per No. | 3683 | 3747 | 1.7377
| iii | LT Capacitor for 100 kVA DT | C-16 (iii) | Per No. | 4385 | 4462 | 1.756
| iv | LT Capacitor for 200 kVA DT | C-16 (iv) | Per No. | 4385 | 4462 | 1.756
| v | LT Capacitor for 315 kVA DT | C-16 (v) | Per No. | 4385 | 4462 | 1.756
(Q) |  | 11 kV MEDP Structure on H-Beam Pole
| i | 37.1 Kg /Mtrs 11 Mtrs long H-Beam supports | C-17 (i) | Each | 87687 | 87177 | -0.58161
(R) |  | New Automated 11 kV Capacitor Bank at 33/11 kV Sub-stations
| i | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. | C-18 (i) | Each | 1036047 | 1043835 | 0.7517
| ii | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . | C-18 (ii) | Each | 857969 | 865574 | 0.8864
PART-V, 11/0.4 kV Transformer S/s.
A (A-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(I) | Each | 120244 | 127455 | 5.997
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(II) | Each | 173233 | 182347 | 5.2611
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(III) | Each | 267661 | 269627 | 0.73451
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(IV) | Each | 407112 | 411174 | 0.99776
(B-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(I) | Each | 156903 | 163164 | 3.9904
| ii | 63 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(II) | Each | 209893 | 218056 | 3.8891
| iii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11mtr long | C-7(B-1)(III) | Each | 267132 | 269237 | 0.788
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(IV) | Each | 407149 | 411403 | 1.0448
(B-1) A |  | Relocation of 11/0.4 kV Out-door type Transformer Sub-station using H-Beam Pole and 3.5 Core PVC Cable [Based on Cost Schedule C-7 (B-1) except X-mer Cost]
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (I) | Each | 101422 | 104012 | 2.5537
| ii | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (II) | Each | 119646 | 121859 | 1.8496
| iii | 100 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (III) | Each | 137261 | 139468 | 1.6079
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr,11 mtr long | C-7(B-1) A (IV) | Each | 168055 | 170788 | 1.6263
(B-1) B |  | Renovation of Existing Distribution Transformer
| i | 25 kVA Transformer | C-7(B-1) B (I) | Each | 23315 | 23299 | -0.068625
| ii | 63 kVA Transformer | C-7(B-1) B (II) | Each | 38803 | 39399 | 1.536
| iii | 100 kVA Transformer | C-7(B-1) B (III) | Each | 48130 | 48779 | 1.3484
| iv | 200 kVA Transformer | C-7(B-1) B (IV) | Each | 77944 | 79053 | 1.4228
| v | 315 kVA Transformer | C-7(B-1) B (V) | Each | 89934 | 91550 | 1.7969
(A-2) |  | 11/0.4 kV Out-door type Transformer sub-station using 1 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(I) | Each | 119614 | 126281 | 5.5738
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(II) | Each | 170668 | 180503 | 5.7627
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(III) | Each | 262842 | 265009 | 0.82445
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(IV) | Each | 395784 | 399951 | 1.0528
(B-2) | v | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(I) | Each | 156272 | 161988 | 3.6577
| vi | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(II) | Each | 207327 | 216210 | 4.2845
| vii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(III) | Each | 262813 | 265105 | 0.8721
| viii | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(IV) | Each | 396322 | 400666 | 1.0961
(B) |  | Augmentation of 11/.4 kV S/s capacity (Assuming 25 years of life & 10 years in service)
| i | 25 kVA to 63 kVA | C-10 (I) | Each | 129272 | 139612 | 7.9986
| ii | 63 kVA to 100 kVA | C-10 (II) | Each | 224538 | 228275 | 1.6643
| iii | 100 kVA to 200 kVA | C-10 (III) | Each | 366277 | 372427 | 1.6791
(C) | i | 11/.4 kV Out door Sub-station (16 kVA Transformer) | C-11 | Each | 115010 | 121647 | 5.7708
(D) | ii | 11/.4 kV Outdoor Sub-station (10 kVA Transformer) | C-11 (A) | Each | 98892 | 102238 | 3.3835
(E) |  | Single pole mounted low capacity Single phase / Three phase 11/.4 kV Distribution Transformer Sub-station
| i | 5 kVA Single phase | C-13(I) | Each | 73209 | 75901 | 3.6771
| ii | 10 kVA Single phase | C-13(II) | Each | 84741 | 87719 | 3.5142
| iii | 16 kVA Three phase | C-13(III) | Each | 93171 | 99528 | 6.8229
(F) |  | Plinth mounted 11/.4 kV Outdoor Sub-station
| i | 63 kVA Transformer | C-14(I) | Each | 230146 | 239699 | 4.1508
| ii | 100 kVA Transformer | C-14(II) | Each | 285767 | 289428 | 1.2811
| iii | 200 kVA Transformer | C-14(III) | Each | 455715 | 460931 | 1.1446
PART-VI, L.T. LINES
(A) |  | 3 phase, 5 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 4 Rabbit + 1 Squirrel | D-1(I) | Per Km | 277022 | 293526 | 5.9576
| ii | 3 Rabbit + 2 Squirrel | D-1(II) | Per Km | 255520 | 270463 | 5.8481
| iii | 4 Weasel + 1 Squirrel | D-1(III) | Per Km | 221615 | 233964 | 5.5723
| iv | 3 Weasel + 2 Squirrel | D-1(IV) | Per Km | 213965 | 225792 | 5.5275
| v | 5 Squirrel | D-1(V) | Per Km | 191014 | 201276 | 5.3724
(B) |  | 3 phase, 4 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 3 Rabbit + 1 Squirrel | D-2(I) | Per Km | 236820 | 250364 | 5.7191
| ii | 3 Weasel + 1 Squirrel | D-2(II) | Per Km | 195265 | 205693 | 5.3404
| iii | 4 Squirrel | D-2(III) | Per Km | 172315 | 181176 | 5.1423
(C) |  | 1 phase, 3 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-3(I) | Per Km | 182251 | 191684 | 5.1758
| ii | 2 Weasel + 1 Squirrel | D-3(II) | Per Km | 168399 | 176794 | 4.9852
| iii | 3 Squirrel | D-3(III) | Per Km | 153099 | 160450 | 4.8015
(D) |  | 3 Phase, 5 Wire LT line on 125 x 70 mm, 9.3 Mtrs long R.S. Joist with 3 Rabbit & 2 Weasel conductors (Span upto 45 Meters) | D-4(I) | Per Km | 424197 | 438855 | 3.4555
(E) |  | 3 Phase, 5 Wire LT line on 175 x 85 mm, 9.3 Mtrs long R.S. Joist with 3 Raccoon & 2 Weasel conductors (Span upto 65 Meters) | D-4(II) | Per Km | 452360 | 469194 | 3.7214
(F) |  | 1 Phase, 3 Wire LT line on 9.3 Mtrs long 125x70 mm R.S. Joist with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-5(I) | Per Km | 316294 | 323308 | 2.2176
| ii | 2 Weasel + 1 Squirrel | D-5(II) | Per Km | 302442 | 308418 | 1.9759
| iii | 3 Squirrel | D-5(III) | Per Km | 287142 | 292073 | 1.7173
(G) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (i) | Per Km | 379647 | 394195 | 3.832
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (ii) | Per Km | 317955 | 329894 | 3.7549
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (iii) | Per Km | 567556 | 579416 | 2.0897
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (iv) | Per Km | 505864 | 515115 | 1.8288
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (v) | Per Km | 739365 | 748601 | 1.2492
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (vi) | Per Km | 677673 | 684300 | 0.97791
(H ) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (i) | Per Km | 490829 | 510080 | 3.9221
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| ii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (ii) | Per Km | 678738 | 695301 | 2.4403
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| iii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (iii) | Per Km | 850547 | 864486 | 1.6388
(I) |  | 1 phase 3 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x25+1x16+1x25 sq.mm. | D-6 [3] | Per Km | 282640 | 293047 | 3.6821
(J) |  | 3 phase 4 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 3x16+1x25 sq.mm. | D-6 [4] | Per Km | 295828 | 283964 | -4.0104
(K) |  | 3 phase 5 Wire L.T. Line on R.S.Joist (175x85) mm, 9.3 Mtr. Long (By replacement of existing bare LT conductor) for Urban area using AB XLPE Cable of size
| i | 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6(A) (i) | Per Km | 267059 | 278305 | 4.2111
(L) |  | Additional pole of R.S. Joist (125x70) mm (Mid span) for L.T.Line with A.B.Cable. | D-6(B) | Per No. | 11864 | 11930 | 0.5563
(M) |  | HVDS system of 200 kVA parent DTR taking 4 KM LT to be converted | D-7 | 4 Km | 2382649 | 2668928 | 12.0152
(N) |  | HVDS system of 100 kVA parent DTR taking 3 KM LT to be converted | D-8 | 3Km | 1125676 | 1220433 | 8.4178
(O) |  | HVDS system of 63 kVA parent DTR taking 2 KM LT to be converted | D-9 | 2Km | 839747 | 910638 | 8.4419
(P) |  | Conversion of 1 Km LT line into 11 kV line | D-10 | Per Km | 72503 | 80078 | 10.4478
(Q) |  | LT line conversion using Rabbit conductor maximum span of 45 mtrs
| i | 1 phase 2 wire to 1 phase 3 wire conversion | D-11(I) |  | 70575 | 75485 | 6.9571
| ii | 1 phase 2 wire to 3 phase 4 wire conversion | D-11(II) |  | 114126 | 122106 | 6.9923
| iii | 1 phase 3 wire to 3 phase 4 wire conversion | D-11(III) |  | 73487 | 78662 | 7.0421
| iv | 1 phase 3 wire to 3 phase 5 wire conversion | D-11(IV) |  | 116951 | 125193 | 7.0474
(R) |  | Conversion of 1 Km 1 Phase 3 wire LT line into 11 kV line | D-12 | Per Km | 192809 | 207713 | 7.7299
(S) |  | Conversion of 1 Km 3 Phase 5 wire LT line into 11 kV line | D-13 | Per Km | 221544 | 239014 | 7.8856
(T) |  | Distribution Box on existing LT Lines for Service Connections.
| i | Single phase Distn. Box for 20 Connections | D-14 (i) | Per No. | 1299 | 1350 | 3.9261
| ii | Three phase Distn. Box for 06 Connections | D-14 (ii) | Per No. | 1517 | 1577 | 3.9552
(U) |  | 1 phase 2 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x16+1x25 sq.mm. | D-15 | Per Km | 248148 | 257348 | 3.7075
PART-VII, METERING
(A) |  | Metering of 11/0.4 kV Distribution X'mer
| i | 25 kVA Transformer | E-1(I) | Each | 10033 | 9927 | -1.0565
| ii | 63 kVA Transformer | E-1(II) | Each | 10033 | 9927 | -1.0565
| iii | 100 kVA Transformer | E-1(III) | Each | 10033 | 9927 | -1.0565
| iv | 200 kVA Transformer | E-1(IV) | Each | 9754 | 9635 | -1.22
Meter modernisation- Replacing the existing meters with electronic meters which are highly capable of improving billing efficiency.
(B) | i | Cost of meter replacement of single phase consumer along with shifting of meter outside the premises. | E-2 | Each | -
| i | With Armoured service cable | E-2(i) | Each | 2684 | 2731 | 1.7511
| ii | With Unarmoured service cable | E-2(ii) | Each | 2390 | 2436 | 1.9247
(C) | ii | Cost of meter replacement of three phase consumer along with shifting of meter outside the premises. | E-3 | Each | -
| i | With Armoured service cable | E-3(i) | Each | 5262 | 5315 | 1.0072
| ii | With Unarmoured service cable | E-3(ii) | Each | 5033 | 5086 | 1.053
(D) | iii | Cost of meter replacement of three phase consumer CT Operated meter along with shifting of meter outside the premises. | E-4 | Each | 3066 | 3084 | 0.58708
(E) | iv | Meter shifting of Single phase consumer to outside of premises with New Service Cable. | E-5 | Each | -
| i | With Armoured service cable | E-5(i) | Each | 1605 | 1668 | 3.9252
| ii | With Unarmoured service cable | E-5(ii) | Each | 1311 | 1373 | 4.7292
(F) | v | Meter shifting of Three phase consumer to outside of premises with New Service Cable. | E-6 | Each | -
| i | With Armoured service cable | E-6(i) | Each | 2726 | 2779 | 1.9442
| ii | With Unarmoured service cable | E-6(ii) | Each | 2497 | 2550 | 2.1225
|  |  |  | Total | 110045709 | 113946293 | 3.5445

## SOR RATE
RATE OF STOCK MATERIALS IN 2015-16
Material Code | Description | unit | Unit rate for 2015-16 | SAP DESCRIPTION
7130200201 | 1:1.5:3 Ratio | Cmt | 4212
7130200202 | 1:3:6 Ratio | Cmt | 3019
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 157 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 268 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Per 1000 | 10423
7130210809 | Aluminium Paint | Ltr. | 290 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 223
7130211158 | Red Oxide Paint | Ltr. | 130 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 225744 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5
7130310007 | 70 Sqmm. | Km. | 73880 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V
7130310008 | 120 Sqmm. | Km. | 92081 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100
7130310020 | 3x400 Sq.mm. | km | 2104858 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 39632 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V
7130310022 | 50 Sqmm. | Km. | 56726 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 59321 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 75464 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 93866 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM
7130310038 | 2.5 Sqmm. | Per Mtr. | 6 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 27 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 55 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 101834 | 11KV PVC INSULATED 150SQMM SINGLE CORE X
7130310042 | 16.0 Sqmm. | km | 66832 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 94953 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310048 | 25 Sq.mm. | km | 139291
7130310049 | 120 Sq.mm. | km | 401162
7130310050 | 400 Sqmm. | km | 1142914
7130310051 | 3x95 Sq.mm. | km | 841556 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1033058
7130310053 | 3x185 Sq.mm. | km | 1180744 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 1501438 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 17336
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 24765
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 287007 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 406042
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 607146
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 572690
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 3784 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 3982 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 50560 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310064 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X35+1X16+1x25 | km | DELETED | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 118163 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 129093 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310067 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x16+1x50 | km | DELETED | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310068 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x16+1x70 | km | DELETED
7130310069 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x35+1x70 | km | DELETED | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 47069 | LT AB CABLEB 3X16+1X25 SQMM
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 60003 | LT AB CABLEB 3X25+1X25 SQMM
7130310075 | 3x240 Sq.mm. | km | 1926090 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 514014.41
7130310077 | 95 Sq.mm | km | 520056 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 775508 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 939613 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 1447702 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310652 | 2 Core (UNARMOURED) | Km. | 39708 | CONTROL CABLE COP 2CORE 2.5SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. | 78312 | CONTROL CABLE COP 2CORE 2.5SQMM PVC/PVC
7130310654 | 4 Core (UNARMOURED) | Km. | 67671 | CONTROL CABLE COP 4CORE 2.5SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. | 112811 | CONTROL CABLE COP 4CORE 2.5SQMM PVC/PVC
7130310658 | 8 Core (UNARMOURED) | Km. | 125719 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310660 | 10 Core (UNARMOURED) | Km. | 154500 | CONTROL CABLE COP 10CORE 2.5SQMM PVC/PVC
7130310660 | 10 Core (ARMOURED) | Km. | 172208 | CONTROL CABLE COP 10CORE 2.5SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 173129 | CONTROL CABLE COP 12CORE 2.5SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 15990 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 38685 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 52581 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 101586 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 198613 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 247683 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km | 213718 | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC
7130311057 | 150 Sqmm. | km | 412459 | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV
7130311061 | 300 Sqmm. | km | 784944 | Power Cable ARM ALU 3.5CORE 300/150SQMM
7130311084 | 16.0 Sqmm. | km | 99916 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 9906
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 12383 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 14859 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 17336 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 18574
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 22289
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 780 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 842
7130320045 | Cable tie for AB Cable | Each | 25
7130320046 | 11 kV ABC-T Jointing kit 35-70 sqmm | Set | DELETED | 11KV ABC T-JOINTING KIT 35-70 SQMM
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | Set | DELETED | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 2396 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 2524
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 5 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 35084 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 804
7130352031 | 16 Sq.mm, 4 Core | Set | 804 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 863
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1213
7130352034 | 150 Sq.mm, 3.5 Core | Set | 1808
7130352035 | 300 Sq.mm, 3.5 Core | Set | 2923
7130352036 | 400 Sq.mm, 3.5 Core | Set | 3735
7130352037 | End terminating jointing kit for 240 sqmm XLPE cable | Set | 21050 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x70 Sq.mm | Set | 7880
7130352039 | 3x95 Sq.mm | Set | 8701 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 10187 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 10751 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 11000 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 2406 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 2561 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 2630 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box | No. | 3096 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 2 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 2 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 4
7130354277 | 32 Sq mm | Nos. | 5
7130354278 | 50 Sq mm | Nos. | 8 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 13 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 16 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 22 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 25 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 40
7130354284 | 225 Sq mm | Nos. | 46
7130354285 | 240 Sq mm | Nos. | 66
7130354286 | 300 Sq mm | Nos. | 77 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 100
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 627 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 80 | INSULATING PIERCING CONNECTOR AB CABLE(S
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 104 | INSULATING PIERCING CONNECTOR FOR AB CAB
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 145 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 149 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 172 | STRAIGHT THROUGH JOINT
7130390008 | Piercing connector for services 16-50 Sq. mm Tap off 2.5-16 Sq. mm | Each | DELETED
7130390017 | Suspension Clamp Assembly with Hook bracket & Pole Clamp | Each | DELETED
7130390018 | Tension/Dead end Clamp Assembly with Hook bracket & Pole Clamp | Each | DELETED
7130390019 | End cap for 50/70 Sq.mm | Nos. | 28 | END CLAMP CAP FOR 50/70 SQMM
7130600023 | 50 x 50 x 6 mm | MT | 40214 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 40214 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 40214 | M S ANGLE 75X75X6 MM
7130600075 | Angle line Suspension Assembly (Suitable for all size cable) | Each | DELETED | Jointing kit 11KV ABC Cabl 3x25+1x35sqmm
7130600166 | 75x40 mm | MT | 40214 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 40214 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 40214 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 40214 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT | 44989 | R.S.JOIST 125 x 70 mm
7130600675 | 175 x 85 mm | MT | 44989 | R S JOIST 175X85 MM
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 47741 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 47741 | RAIL 60 KG PER METER
7130601958 | 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 44989 | H BEAMS 152X152MM; 37,1 KG/MTR.
7130601965 | 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 44989 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR
7130610206 | Barbed wire | MT | 66528 | G.I. WIRES: - Barbed wire.
7130620013 | I-Bolt (big size) | No | 118 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 64
7130620133 | 16x40 mm | Kg | 89 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 89 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 64 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 65 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 65 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 64 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 63 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 63 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 62 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 62 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 62 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 62 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 62 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt | No | 395 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 127 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 mm cable of dia 105 mm | RM | 929 | G.I. PIPE 200MM FOR 400MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 805 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 3220 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | 600 mm | Each | 3857
7130640036 | 900 mm | Each | 7661 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG)
7130640037 | M.S.Pipe 200 mm dia with collars | RM (light) | 918 | M.S. PIPE 200MM DIA WITH COLLARS
7130641396 | Gl Pipe 40 mm | Per Mtr | 190 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | No | 820 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 4169 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing (TATA Make) 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. T&D/DRG/MISC/2 Revision -2 | Sq.mtr | 1131
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 119
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 599 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 435 | SUSPENSION CLAMP
7130797533 | Suspension Clamp (Suitable for all size cable) | Each | DELETED | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 1654 | PCC POLE 140 KG; 8,0 MTR LONG
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each | 6408
7130800033 | 280 Kg; 9.1 Mtr long | Each | 3129 | PCC POLE 280 KG; 9,1 MTR LONG
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each | 10737 | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT
7130800672 | 350 Kg; 7.0 Mtr long | Each | 2851 | PCC POLE 350 KG; 7,0 MTR LONG
7130810005 | Through Bolt | No | 83 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr 100 x 50 mm. | Set | 6808 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810026 | Stay clamp for 140 kG PCC Pole | Pair | 142 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 265 | Stay clamp LT/Pair
7130810060 | LT U CLAMP | No. | 71 | LT U CLAMP
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 68 | Strain Plate
7130810077 | Pole Clamp | No. | 394 | POLE CLAMP
7130810102 | Service Ring | No. | 349 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 265 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 282 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 282 | HT STAY CLAMP R S JOIST A TYPE
7130810251 | Stay Clamp Rail "B" type | Pair | 282 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 282 | 33 KV TOP CLAMP SEMIFINISHED
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 618 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 736 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 854 | LT FIVE PIN CROSS ARM
7130810495 | 11 kV Cross Arm Cleat type | No. | 1048 | 11 KV V CROSS ARM
7130810509 | Lightning Arrestor Structure | No. | 7845 | D.O. / LA Mounting channel 75x40 mm.
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 3322 | D.O. / LA Mounting channel 75x40 mm.
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2485 | 1.1 MTR DPDC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 3940 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 2862 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 4022 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 4547 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 2332 | 33 KV V CROSS ARM
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 5377 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 90 | STRAIN PLATE
7130810624 | Strain Plate | Set | 94 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 388 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 294 | 11KV top clamp
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 3227 | 11KV cut point channel paint
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 8457 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 294 | Stay clamp for 'H' Beam
7130820008 | 11 kV Pin insulator with Pin | Each | 157 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 388 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 140 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 354 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 3 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 412 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 1907 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 31
7130820030 | Disc insulator | Each | 231 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 40 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 230 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 9 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 10 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 9 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 60 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 199 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 32 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 30 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 34 | HARDWARE FOR 75X90MM LTSHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 123 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 255 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2183 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 139 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km | 11084 | CONDUCTOR AAA SQURREL
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km | 17295 | CONDUCTOR AAA WEASEL
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km | 27240 | CONDUCTOR AAA RABBIT
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 33968 | CONDUCTOR AAA RACOON
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 32 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 126 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 534
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 13002 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq)
7130830054 | Bimetallic clamp for VCB | Each | 312
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 20281 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq)
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 312
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 33544 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q)
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 158
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 50002 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 64842 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq)
7130830070 | 0.2 Sq inch ( 130 Sqmm Al.Eq.)(Panther) | Km | 167935 | CONDUCTOR ACSR PANTHER 130 sq mm
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 50246 | CONDUCTOR AAA DOG
7130830585 | T-Clamp for Dog Conductor. | Each | 239 | T-CLAMPS FOR ACSR CONDUCTOR Dog Condutor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 191 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830586 | T-Clamp for Panther Conductor. | Each | 279 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 232 | Bimetallic clamps for transformer &kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 26 | SLEEVE JOINTING ALUMINIUM FOR 0.03SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 195 | SLEEVE REPAIR ALUMINIUM FOR .2SQ INCH AC
7130840021 | 33 kV Polymer Lightning Arrestor | Each | 3483 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 425 | LIGHTNING ARRESTORS11 KV gapless type.
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 4547 | Transformer mounting 100 x 50 mm channel
7130850201 | Transformer Mounting with Belting for Addl. X-Arm | No. | 4393 | Transformer mounting 100 x 50 mm channel
7130860017 | I-Bolt - 16 mm | No. | 100 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 387 | STAY SET WITHOUT STAY WIRE16mm Paint11KV
7130860033 | Stay Set 20 mm (Painted) | Each | 705 | STAY SET WITHOUT STAY WIRE 20mm (Painted
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 61002 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 61600 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 681
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 100 | EARTHING COIL 8SWG GI WIRE 50MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 371 | Earthing rod 25mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 55133 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 55094 | G.I. WIRES: - 4,0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 55094 | G.I. WIRES: - 5,0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 1930
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 1003 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877679 | Section Suspension Assembly (Suitable for all size cable) | Each | DELETED | Jointing Kit 11 kV ABC Section Suspensio
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 2270 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2018 | Jointing Kit&HW LT ABC CableStraight Sus
7130880006 | Cable marker for U/G cable | No. | 113 | CABLE MARKER FOR U/G CABLE
7130880006 | Pad Connector (for Panther conductor) | No. | 124 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 74 | 7130880041Danger boards 33KV & 11 KV.
7130890003 | M.S. sheet meter piller box | Each | DELETED | M.S. SHEET METER PILLER BOX
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 4543 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 5733
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 13002 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 13621 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 51 | LT LINE SPACERS
7130890009 | GSM Modem | Nos. | 4017 | GSM MODEM
7130893004 | Eye Hook | No. | 161 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 3315 | 33 KV guarding channel 100x50 mm.
7131210001 | Panel lndication lamps | Nos. | 106
7131210846 | Metal Halide light lamp | No. | DELETED | LAMP METAL HALIDE 250W
7131210852 | CFL 7 Watts | Each | 97
7131210881 | 250 Watt Metal Halide | Each | 1260 | METAL HALIDE LAMP 250 WATT
7131220182 | Tube Light Rod (T5 type) | Each | 52 | LAMPS: -Tube Light (40 Watts.)
7131230003 | 250 Watt Sodium Vapour | Each | 470 | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER
7131230116 | 250 Watt Mercury Vapour | Each | 370 | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each | 1967 | S/ V HIGH PRESSURE LAMP 400W 230/250V
7131280006 | CFL 15 Watts | Each | 103
7131280007 | CFL 20 Watts | Each | 135 | CFL 20 WATTS LAMP
7131280008 | CFL 23 Watts | Each | 174
7131280009 | 125 Watt Mercury Vapour | Each | 161
7131280010 | Halogen Filament (1000 Watts) | Each | 99
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each | 6502
7131280012 | Street Light fitting with tube light | Each | 650 | STREET LIGHT FITTING WITH TUBE LIGHT
7131280013 | Street Light fitting with CFL | Each | 2718 | STREET LIGHT FITTING WITH CFL
7131280014 | HPSV lamp 150 watt | Each | 325 | HPSV LAMP 150 WATT
7131280015 | HPSV Choke 250 watt | Each | 1355 | HPSV LAMP 250 WATT
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each | 3100 | 150 WATT METAL HALIDE HPSV FITTING
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each | 3874 | 250 WATT METAL HALIDE HPSV FITTING
7131280882 | CFL 11 Watts | Each | 97
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 2326 | ENERGY METER ENECTRONIC 10-60 AMPS
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for 132 kV) | Each | 1039058 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 178
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 648 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 975 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A
7131300881 | CMRI | Each | 50063 | Common Meter Reading Instrument CMRI
7131310013 | 3 Ø 4 Wire 0.5S Non DLMS | Each | 4030 | HT TRIVECTOR METER 5 AMPS
7131310015 | CT operated electronic static meters with AMR (Composite Unit). | Each | 11297 | ELECTORNIC LTCT METER 3X4 100/5 A
7131310033 | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | Each | 3970 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR
7131310034 | 3 Ø 4 Wire 0.5S with DLMS Protocol category B | Each | 4030 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR
7131310035 | 3 Ø 3 Wire 0.2S Non DLMS | Each | 16362 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC (
7131310036 | 3 Ø 4 Wire 0.2S Non DLMS | Each | 16362 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC (
7131310037 | Test terminal Box (TTB) | Each | 870 | TTB
7131310994 | Three Phase, 20-100 Amps. with Meter Box with data storage. | Each | 2618 | LT ELEC.STATIC METER3X4X20-100A WITHLUGS
7131310997 | CT operated electronic static meters 100/5 Amp. With data storage. | Each | 2487 | 3 PHASE 4 WIRE LTCT OPERATED METER
7131320009 | Digital Multimeter Electronic Type | Nos. | 2700 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) | Nos. | 3940
7131324780 | Megger 500 V | Nos. | 3240
7131324806 | Megger up to 2.5 kV | Nos. | 4883 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 6842
7131334001 | Set of 3 O.C. relays instantaneous high set feature | Nos. | 7851 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH | Old Bin Code 7131329276
7131334002 | Set of 2 O.C.+ 1 earth fault relay without instantaneous high set feature | Nos. | 7278 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO | Old Bin Code 7131329277
7131399007 | Master trip relays | Nos. | 1585 |  | Old Bin Code 7131329278
7131338004 | Transil oil Dielectric Breakdown testkit | Nos. | 64638
7131338025 | Neon tester | Nos. | 51 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 216
7131387502 | Thermometer (Wall Mounted) | Nos. | 427 | THERMOMETER (WALL MOUNTED)
7131390009 | Piercing connector suitable for 16 Sq.mm-95 Sq.mm AB Cable-Service connections | Nos. | DELETED
7131390010 | Piercing connector for Main 16-50 Sq. mm Tap off 16-50 Sq. mm. | Each | DELETED
7131390012 | Piercing connector suitable for 25 Sq.mm-95 Sq.mm AB Cable-main to main connections | Nos. | DELETED
7131390013 | Piercing connector suitable for 50 Sq.mm-150 Sq.mm AB Cable-main to main connections | Nos. | DELETED
7131390014 | Earthing Coil for messenger wire | Nos. | 169
7131390015 | Anchor sleeve for messenger wire | Nos. | 31
7131390016 | Universal hook & Bolts & nuts | Nos. | 420
7131820031 | LT Single Phase MCB 5 Amps. | Each | 101
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 101 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 430
7131820034 | LT Three Phase MCB 32 Amps. | Each | 430
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 2865
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 3104
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 3104
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2268
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 5193 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900005 | Locally fabricated - 3 Phase fuse units (Robust fuse for circuit base). | Each | 2114 | LT ROBUST POLE FUSE UNIT
7131900005 |  |  | 2603 | LT ROBUST POLE FUSE UNIT
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 7 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 283 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 435 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 13 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 14 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 279 | H.R.C. FUSE UNITS: -100 Amps.
7131900876 | H.R.C. Fuse 100 Amps. | Each | 109 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 701 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 775 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 684 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 683 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 681 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 674 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 671 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 671 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 672 | FUSE WIRE TINNED COPPER 10 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 44 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 87 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 25 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 269 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 534 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 964 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920112 | 11 kV Kiosk VCB | Each | 248028 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 681 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 1634 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 3161 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 4438 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 6021 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 9095 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  | 51.2435
7131920767 | Distribution Board with MCB | No. | DELETED | DIST.BOARD & DP MCB 4NO 6A&2NO 16A
7131930109 | 33 kV ; 600 Amps with earth switch. | Each | 40392 | 33 KV 600AMPS WITH EARTH SWITCH ISOLATO
7131930221 | 11 kV Porcelain A.B. Switch | Each | 7750 | AB Switch with complete fitting 11 KV
7131930221 | Single phase AB switch complete. | Set | 12911 | AB Switch with complete fitting 11 KV
7131930321 | 33 kV Porcelain A.B. Switch | Each | 18624 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1199 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 2918 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 20680 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 35789 | 33 KV Isolator 800A without earth switch
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 2387 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 22680 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 22680
7131941762 | 11 kV VCB without control panel & CT's. | Each | 110737 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 226584 | 33KV VCB FOR 30 VOLT DC
7131950009 | Distribution box 1 ph. 4 connectors | Each | DELETED | DISTRIBUTION BOX 1 PH 4 CONNECTOR
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1147 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950011 | Distribution box 3 phase 2 connectors | Each | DELETED | DISTRIBUTION BOX 3 PH 2 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1355 | DISTRIBUTION BOX 3 PH 4 CONNECTOR
7131950013 | Spring loaded distribution box for service connection with stainless steel buckle. | Each | DELETED | SPRING LOADED DIST. BOX FOR SERVICE CONN
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 57208
7131950016 | 11 kV Sectionalizer. | Each | 345600
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 13758 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 17198 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 34396 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 45861 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 26078 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 28850 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 26331 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 26995 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960520 | 2 Feeder Control (Static Relays) | Each | 39700 | 11KV MULTICIRCUIT(2F) CONTROL PANNELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 39815 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 39815 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm;3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 184
7132004003 | Hack saw frames + B185 | Nos. | 119
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 10
7132013331 | Discharge Rod | Nos. | 515 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 2700
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 989
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 306
7132061858 | Combination Plier | Nos. | 204 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 66 | SCREW DRIVER 250MM
7132072007 | Screw driver 200 mm | Nos. | 62 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 57 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. | 743 | SCREW DRIVER INSULATED 255MM
7132074032 | Ring Spanners (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 1430 | RING SPANNER
7132074033 | Tube Spanners | Set. | 591
7132074034 | Double end spanner (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 676 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 439
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F& tommy Bar) | Set. | 1303 | BOX SPANNER
7132088614 | Pipe Wrench 24 inches size | Nos. | 1086
7132088615 | Pipe Wrench 18 inches size | Nos. | 596
7132200014 | 1089 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 | Each | 135369 | 11 KV CAPACITOR 600KVAR
7132200812 | 5 kVAR | Each | 1628 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 3254 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 3910 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200815 | 20 kVAR | Each | 6490 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 179001 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each | 44836 | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each | 54268 | TRANSFORMER 25KVA 11/0.4KV FOUR STAR
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each | 88254 | TRANSFORMER 63KVA 11/0.43KV FOUR STAR
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each | Not Procured | TRANSFORMER 63KVA 11/0.43KV FOUR STAR
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each | 119054 | TRANSFORMER 100KVA 11/0.43KV FOUR STAR
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each | 220748 | TRANSFORMER 200KVA 11/0.4KV FOUR STAR
7132210012 | 315 kVA (CEA Design) | Each | 423239 | XMER 315KVA 11/0.43KV CEA REG. CU WOUND
7132210077 | 5 kVA Single Phase | Each | 25351 | TRANSFORMER 11/.4KV 5 KVA 1 PHASE
7132210078 | 10 kVA Single Phase | Each | 36194 | TRANSFORMER 11/.4KV 10 KVA 1 PHASE
7132210079 | 16 kVA (3 Star) Copper Wound | Each | 52823 | TRANSFORMER 11/.4KV 16 KVA 3 PHASE COPPE
7132210107 | Single Phase transformer with protection (16 kVA) | No | 63182 | Single Ph transfor with protection 16KVA
7132210108 | 25 kVA (3 Star) Aluminium Wound | Each | 47679 | TRANSFORMER 11/.4KV 25 KVA 3 STAR RATING
7132210109 | 25 kVA (Conventional) | Each | 41834 | TRANSFORMER 11/.4 KV 25 KVA
7132210116 | 63 kVA (3 Star) Aluminium Wound | Each | 82795 | TRANSFORMER 11/.4KV 63 KVA 3 STAR RATING
7132210117 | 100 kVA (3 Star) Aluminium Wound | Each | 112713 | TRANSFORMER 11/.4KV 100 KVA 3 STAR RATIN
7132210118 | 200 kVA (Conventional) | Each | 237089 | TRANSFORMER 11/.4KV 200 KVA 3 STAR RATIN
7132210120 | 200 kVA (3 Star) Aluminium Wound | Each | 204019 | TRANSFORMER 11/0.4 KV 200 KVA
7132210125 | 315 kVA (Conventional) | Each | 322632 | TRANSFORMER 11/0.4 KV 315 KVA
7132210127 | 500 kVA (Conventional) | Each | 538012 | TRANSFORMER 11/0.4 KV 500 KVA
7132210215 | 50 kVA (Copper winding) | Each | 146905 | TRANSFORMER 33/.4KV 50KVA
7132210231 | 63 kVA (Conventional) | Each | 69656 | TRANSFORMER 33/0.4 KV 200 KVA
7132210234 | 100 kVA (Conventional) | Each | 87074 | TRANSFORMER 33/0.4 KV 300 KVA
7132220091 | Power Transformer 1600 kVA | Each | 841136 | TRANSFORMER 33/11KV 1.6 MVA POWER
7132220095 | Power Transformer 3150 kVA | Each | 2112952 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 5000 kVA | Each | 3010759 | TRANSFORMER 33/11KV 5 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 241090 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 335 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 222386 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 335 | L.T. C.T.200/5 Amps.
7132230021 | L.T.C.T. 300/5 Amps. | Each | 268 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 268 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1 | No. | 460044 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 18227 | 33KV CT 400-200/5-5A
7132230065 | 132 kV C.T. 600-300/1 | No. | 290795 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV
7132230075 | 132 kV C.T. 150-75/1 | No. | 331734 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1 | No. | 735218 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1 | No. | 484141 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1 | No. | 448513 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 30290
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 67155 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 8903 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 8903 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 18948 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5) Amps oil filled | Each | 16868 | 33KV CT's(200-100/5)A oil filled OD Type
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each | 16544 | 33KV CT's (100-50/5)A oil filled OD Type
7132230330 | 132 kV C.T. 100-50/1 | No. | 328366 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE
7132230332 | 132 kV C.T. 200-100/1 | No. | 304009 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1 | No. | 266309 | CURRENT X-MER 300-150/1/1A - 132KV
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each | 35395 | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 31841 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each | 31131 | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 30287 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 30894 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each | 30894 | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 29949 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230414 | 11 kV CTPT Unit 50/5 A | Each | 30894 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 64768 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 64587 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each | 77029 | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 64768 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each | 64768 | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 66527 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 66527 | OIL IMM 3 PH CTPT UNITS 33 KV-100&200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 64768 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 66145 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 8903 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN | Old Bin Code-7132230472
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 16371 | VOLTAGE TRANSFORMER 33KV/110VOLTS SINGLE | Old Bin Code-7132230482
7132230501 | 132 kV P.T. | No. | 227961 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 540886 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132404015 | Safety belts | Nos. | 549 | SAFETY BELTS
7132404016 | Safety helmets | Nos. | 123 | SAFETY HELMETS
7132404366 | Battery (Low Maintenance SAN controller) | No. | 49161 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 131 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 2437 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406425 | Universal Meter Box for HT meters. | Each | 2528 | Universal Meter Box for HT meters.
7132406721 | CT operated electronic static meters with DLMS. | Each | 2538 | LTCT METER WITH DLMS
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 457 | RUBBER HAND GLOVES
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 5166 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 771 | RAIN COATS WITH HOODS
7132427635 | Gum Boots | Nos. | 519 | GUM BOOTS
7132438002 | Silica gel | Kg | 163 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 4 | POLYCARBONATE SEAL
7132444007 | Grounding Sticks (Earthing Rods) | Set. | 893
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 3710 | METTING RUBBER 1900X1800X12MM | Old Bin Code-7132448851
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 274
7132457798 | Transformer Oil In Barrel | KL | 77842 | TRANSFORMER OIL In Tanker/barrel
7132457798 | Transformer Oil In Tanker | KL | 68897 | TRANSFORMER OIL In Tanker/barrel
7132459005 | Poly Carbonate seal double anker type | Each | 5 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | 1020 | HDPE PIPE 200MM ID; 240MM OD
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 371 | JOINTING ARRANGEMENT OF HDPE PIPE
7132468558 | Battery charger | Each | 9316 | 30 Volt 100 AH lead acid battery charger
7132475019 | Files of sizes | Set. | 310
7132475019 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 131
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 15 | PVC INSULATION TAPES 19 MM WIDE AND IN R
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 71
7132478004 | Tong tester | Nos. | 1351 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI
7132478011 | Hand Torch 5 cell | Nos. | 534
7132478012 | Hand Torch 3 cell | Nos. | 364 | HAND TORCH 3 CELLED
7132478012 | Cotton Waste | Kg | 65 | HAND TORCH 3 CELLED
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 4619 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 59
7132490053 | Bitumen compound | Kg | 90
7132498006 | River sand | Cmt | 650 | RIVER SAND

## A-1
COST SCHEDULE A-1
1 KM OF 33 kV LINE ON PCC POLES / H-BEAMS WITH MAXIMUM SPAN OF 100 METERS USING RACCOON CONDUCTOR
[9 empty] | 2015-16 | NEW COLUMN ADDED
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 3129 | 31290
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 44.989 | 216981.947
3 | 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 10 No = 7800 Kgs | 7130601072 | Kg
4 | 365 Kg; 11 Mtr long PCC Pole |  | No | [6 empty] | 10 | 5022 | 50220 | New introduced
5 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2332 | 23320 | 10 | 2332 | 23320 | 10 | 2332 | 23320
6 | Back Clamp for Cross Arm
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 10 | 265 | 2650 |  |  |  | 10 | 265 | 2650
| (ii) Stay Clamp for "H" Beam | 7130810692 | No |  |  |  | 10 | 294 | 2940
| (iii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iv) Stay Clamp for Rail Pole B Type | 7130810251 | No
7 | 33 kV Top Clamps | 7130810676 | No | 10 | 388 | 3880 | 10 | 388 | 3880 | 10 | 388 | 3880
8 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 100 | 1000 | 10 | 100 | 1000 | 10 | 100 | 1000
9 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 388 | 11640 | 30 | 388 | 11640 | 30 | 388 | 11640 | Earlier - 33 kV Pin Insulator
10 | Raccoon ACSR Conductor (80 Sqmm, Al. Eq) with 3% sag | 7130830060 | Mtr | 3100 | 50.002 | 155006.2 | 3100 | 50.002 | 155006.2 | 3100 | 50.002 | 155006.2
11 | Jointing Sleeves suitable ( for 80 Sqmm, Al.Eq. ACSR cond.) | 7130830050 | No | 6 | 32 | 192 | 6 | 32 | 192 | 6 | 32 | 192
12 | (i) Stay set 20 mm | 7130860033 | No | 3 | 705 | 2115 | 3 | 705 | 2115 | 3 | 705 | 2115
| (ii) Stay Clamp For PCC Pole | 7130810193 | No | 3 | 265 | 795 |  |  |  | 3 | 265 | 795
| (iii) Stay Clamp For "H" Beam | 7130810692 | No |  |  |  | 3 | 294 | 882
| (iv) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (v) Stay Clamp for Rail Pole B Type | 7130810251 | No
| (vi) Stay Wire 7/8 SWG @ 8.5 kg/ stay | 7130860076 | Kg | 25.5 | 61.002 | 1555.551 | 25.5 | 61.002 | 1555.551 | 25.5 | 61.002 | 1555.551
13 | Concreting of supports @ 0.6 Cmt. Per pole for Rail / H-Beam / 365 kG PCC; and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / Rail / H-Beam pole. |  | Cmt | 1.3 |  |  | 8 |  |  | 8
14 | Cement @ 208 Kg/cmt | 7130200401 | Kg | 270.4 | 5.36 | 1449.344 | 1664 | 5.36 | 8919.04 | 1664 | 5.36 | 8919.04
15 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 130 | 182 | 6 | 130 | 780 | 1.4 | 130 | 182
16 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 290 | 435 | 6 | 290 | 1740 | 1.5 | 290 | 435
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 10 | 66.528 | 665.28 | 10 | 66.528 | 665.28 | 10 | 66.528 | 665.28
18 | Danger Board | 7130880041 | No | 10 | 74 | 740 | 10 | 74 | 740 | 10 | 74 | 740
19 | Binding wire and tape | 7130830006 | Kg | 3.5 | 139 | 486.5 | 3.5 | 139 | 486.5 | 3.5 | 139 | 486.5
20 | M.S. Nuts and Bolts |  | Kg | 17 |  |  | 17 |  |  | 17
| 16x65 mm | 7130620614 | Kg |  | 63 |  | 7 | 63 | 441 |  | 63
| 16x90 mm | 7130620619 | Kg | 3 | 63 | 189 |  | 63 |  | 3.5 | 63 | 220.5
| 16x140 mm | 7130620625 | Kg |  | 62 |  | 10 | 62 | 620 |  | 62
| 16x160 mm | 7130620627 | Kg | 14 | 62 | 868 |  | 62 |  | 14.5 | 62 | 899
21 | Guarding 33 kV |  | Rs |  | 8369.31
| (i) G.I. Wire 6 SWG | 7130870045 | Kg | 49 | 55.094 | 2699.606 | 49 | 55.094 | 2699.606 | 49 | 55.094 | 2699.606
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 20 | 55.094 | 1101.88 | 20 | 55.094 | 1101.88 | 20 | 55.094 | 1101.88
| (iii) 33 kV guarding channel | 7130897759 | No | 1 | 3315 | 3315 | 1 | 3315 | 3315 | 1 | 3315 | 3315
| (iv) Stay Clamp Set | 7130810692 | No | 3 | 294 | 882 | 3 | 294 | 882 | 3 | 294 | 882
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 62 | 74.4 | 1.2 | 62 | 74.4 | 1.2 | 62 | 74.4
| (vi) I--Bolt Big Size | 7130620013 | No | 4 | 118 | 472 | 4 | 118 | 472 | 4 | 118 | 472
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 705 | 1410 | 2 | 705 | 1410 | 2 | 705 | 1410
| (viii) Stay wire 7/8 SWG & 8.5 Kg/stay | 7130860076 | Kg | 17 | 61.002 | 1037.034 | 17 | 61.002 | 1037.034 | 17 | 61.002 | 1037.034
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 63 | 94.5 | 1.5 | 63 | 94.5 | 1.5 | 63 | 94.5
22 | SUB TOTAL-1 |  |  |  |  | 249545.295 |  |  | 444990.938 |  |  | 276007.491
23 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 22459.0766 |  | 0.09 | 40049.1844 |  | 0.09 | 24840.6742
24 | Service in lieu of concreting metal & sand only |  | Cmt | 1.3 | 2968.461 | 3858.9993 | 8 | 2968.461 | 23747.6879 | 8 | 2968.461 | 23747.6879
25 | Labour charges as per Schedule No.- AL-1 |  |  |  |  | 31335.2 |  |  | 36663.05 |  |  | 33975.3
26 | Transport charges upto 50 Kms average lead form area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 11711.3553 |  |  | 11711.3553 |  |  | 11711.3553
27 | SUB TOTAL-2 |  |  |  |  | 318909.9261 |  |  | 557162.2156 |  |  | 370282.5083
28 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 27449.9825 |  | 0.11 | 48949.0032 |  | 0.11 | 30360.824
29 | Cost per Km for non-guaranteed works |  |  |  |  | 346359.9086 |  |  | 606111.2188 |  |  | 400643.3324
30 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 346360 |  |  | 606111 |  |  | 400643
Note:-
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
ITEMS REMOVED FROM SoR 2015-16
1 | 33 kV G.I. Pins with Nuts | 7130820158

## A-2 (A)
COST SCHEDULE A-2 (A)
| 33 kV FOUR POLE STRUCTURE ON PCC / H-BEAM POLE | [5 empty] | 2015-16
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty | PCC Pole 280 kg 9.1 Mtr. Long | H-Beams 37.1 Kg/Mtr., 13 Mtr. Long
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 280 Kg.,9.1 Mtrs. long PCC Poles | 7130800033 | No | 3129 | 4 | 12516
2 | H-Beams 152 X 152 mm., 37.1 Kg/Mtr 13 Mtr. Long (482.3 Kg x 4 No = 1929.2 Kgs) | 7130601958 | Kg | 44.989 | 1929.2 |  | 86792.7788
3 | 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 4 No = 3120 Kgs | 7130601072 | Kg | 47.741 | 3120
4 | D.C.cross- arm of 100 X 50 X 6 mm. ISMC channel suitable for 5' centre DP | 7130810608 | Set | 5377 | 8 | 43016 | 43016
5 | 33 kV Strain H.W. fitting | 7130820248 | No | 255 | 24 | 6120 | 6120
6 | 33 kV Polymer Disc Insulator | 7130820011 | No | 354 | 72 | 25488 | 25488 | Earlier- 33 kV Disc Insulator
7 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 64.842 | 30 | 1945.26 | 1945.26
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No. | 388 | 8 | 3104 | 3104 | Earlier - 33 kV Pin Insulator
9 | DC cross arm 3.8 Mtr. Channel of 100x50 mm | 7130810006 | Set | 6808 | 8 | 54464 | 54464
10 | (i) Stay set 20 mm | 7130860033 | No | 705 | 8 | 5640 | 5640
| (ii) Stay Clamp For PCC Pole | 7130810193 | No | 265 | 8 | 2120
| (iiii) Stay Clamp For "H" Beam | 7130810692 | No | 294 | 8 |  | 2352
| (v) Stay Clamp for Rail Pole A Type | 7130810201 | No | 282 | 8
| (iv) Stay Wire 7/8 SWG @ 8.5 kg/ stay | 7130860076 | Kg | 61.002 | 68 | 4148.136 | 4148.136
11 | 33 kV AB Switch | 7131930321 | Each | 18624 | 3 | 55872 | 55872
12 | Concreting of supports @ 0.6 Cmt. Per pole for Rail / H-Beam and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / Rail / H-Beam pole. | 2.6 cmt for Rail & H-Beam, 2.2 cmt for PCC Pole & 2.4 cmt for stay | Cmt. (1:3:6)
| Cement @ 208 Kg/cmt for PCC | 7130200401 | Kg | 5.36 | 457.6 | 2452.736
| Cement @ 208 Kg/cmt for H-Beam | 7130200401 | Kg | 5.36 | 540.8 |  | 2898.688
| Cement @ 208 Kg/cmt for Rail | 7130200401 | Kg | 5.36 | 540.8
| Cement @ 208 Kg/cmt for Stay | 7130200401 | Kg | 5.36 | 499.2 | 2675.712 | 2675.712
13 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 100 | 4 | 400 | 400
14 | Red oxide paint | 7130211158 | Ltr | 130 | 6 |  | 780
15 | Aluminium paint | 7130210809 | Ltr | 290 | 6 |  | 1740
16 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 66.528 | 4 | 266.112 | 266.112
17 | Danger Board | 7130880041 | No | 74 | 1 | 74 | 74
18 | Strain Plate (65x8) mm | 7130810624 | No | 90 | 48 | 4320 | 4320
19 | M.S.Nuts and Bolts |  | Kg.
| 16x40 mm | 7130620609 | Kg | 64 | 2 |  | 128
| 16x65 mm | 7130620614 | Kg | 63 | 2 |  | 126
| 16x90 mm | 7130620619 | Kg | 63 | 10 | 126 | 630
| 16x200 mm | 7130620631 | Kg | 62 | 15 | 930 | 930
20 | SUB TOTAL-1 |  |  |  |  | 225677.956 | 303910.6868
21 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 20311.016 | 27351.9618
22 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 4.6/5/5 | 13654.9205 | 14842.3049
23 | Labour charges as per Schedule No.- AL-2(A) |  |  |  |  | 16886.57 | 16280.44
24 | Transportation charges |  |  |  |  | 11517.1272 | 11517.1272
25 | SUB TOTAL-2 |  |  |  |  | 288047.5898 | 373902.5207
26 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 24824.5752 | 33430.1755
27 | Cost per D.P. |  |  |  |  | 312872.1649 | 407332.6963
28 | Cost per D.P. (Rounded Off) |  |  |  |  | 312872 | 407333
ITEMS REMOVED FROM SoR 2015-16
1 | 33 kV G.I. Pins with Nuts | 7130820158

## A-2 (B)
COST SCHEDULE A-2 (B)
2015-16
| 33 kV DP STRUCTURE ON PCC POLES / H-BEAM POLE (TO BE SUPPLEMENTED WITH EVERY 1.0 KM OF LINE OF RACCOON / DOG CONDUCTOR) | [8 empty] | NEW COLUMN ADDED
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg/Mtr 13.0 Mtr long H-Beam |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 3129 | 6258
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 44.989 | 43396.3894
| (iii) 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 2 No = 1560 Kgs | 7130601072 | Kg
| (iv) 365 Kg; 11 Mtr long PCC Pole |  | No | [6 empty] | 2 | 5022 | 10044 | New introduced
2 | DC cross arm of 100x50 mm Channel 5' Center | 7130810608 | No | 1 | 5377 | 5377 | 1 | 5377 | 5377 | 1 | 5377 | 5377
3 | 33 kV Polymer Disc Insulator | 7130820011 | No | 18 | 354 | 6372 | 18 | 354 | 6372 | 18 | 354 | 6372 | Earlier- 33 kV Disc Insulator
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 6 | 255 | 1530 | 6 | 255 | 1530 | 6 | 255 | 1530
5 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 388 | 1164 | 3 | 388 | 1164 | 3 | 388 | 1164 | Earlier - 33 kV Pin Insulator
6 | Horizontal & cross bracing 5' centre with set of 4 back clamps |  | No | 1 | 3472.84 |  | 1 | 3588.84 |  |  | 3472.84
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 4 | 265 | 1060 |  |  |  | 4 | 265 | 1060
| (ii) Stay Clamp for "H" Beam | 7130810692 | No |  |  |  | 4 | 294 | 1176
| (iii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iv) Stay Clamp for Rail Pole B Type | 7130810251 | No
| (v) M.S.Angle 65X65x6 mm | 7130600032 | Kg | 60 | 40.214 | 2412.84 | 60 | 40.214 | 2412.84 | 60 | 40.214 | 2412.84
7 | (i) Stay set 20 mm | 7130860033 | No | 6 | 705 | 4230 | 6 | 705 | 4230 | 6 | 705 | 4230
| (ii) Stay Clamp for PCC Pole | 7130810193 | No | 6 | 265 | 1590 |  |  |  | 6 | 265 | 1590
| (iii) Stay Clamp for "H" Beam | 7130810692 | No |  |  |  | 6 | 294 | 1764
| (iv) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (v) Stay Clamp for Rail Pole B Type | 7130810251 | No
| (vi) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 51 | 61.002 | 3111.102 | 51 | 61.002 | 3111.102 | 51 | 61.002 | 3111.102
8 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 90 | 540 | 6 | 90 | 540 | 6 | 90 | 540
9 | Concreting @ 0.6 Cmt per pole for Rail / H-Beam supports and 0.5 Cmt per pole for PCC @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / Rail / H-Beam |  | Cmt
| Cement @ 208 Kg/Cmt for pole | 7130200401 | Kg | 228.8 | 5.36 | 1226.368 | 270.4 | 5.36 | 1449.344 | 270.4 | 5.36 | 1449.344
| Cement @ 208 Kg/Cmt for stay | 7130200401 | Kg | 374.4 | 5.36 | 2006.784 | 374.4 | 5.36 | 2006.784 | 374.4 | 5.36 | 2006.784
10 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 2 | 100 | 200 | 2 | 100 | 200 | 2 | 100 | 200
11 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 130 | 65 | 2 | 130 | 260 | 0.5 | 130 | 65
12 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 290 | 145 | 2 | 290 | 580 | 0.5 | 290 | 145
13 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 2 | 66.528 | 133.056 | 2 | 66.528 | 133.056 | 2 | 66.528 | 133.056
14 | Danger Board | 7130880041 | No | 1 | 74 | 74 | 1 | 74 | 74 | 1 | 74 | 74
15 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 64 | 32 | 0.5 | 64 | 32 | 0.5 | 64 | 32
| 16x65 mm | 7130620614 | Kg | 0.5 | 63 | 31.5 | 0.5 | 63 | 31.5 | 0.5 | 63 | 31.5
| 16x90 mm | 7130620619 | Kg |  | 63 |  | 2.5 | 63 | 157.5 |  | 63
| 16x140 mm | 7130620625 | Kg | 2 | 62 | 124 |  |  |  | 2 | 62 | 124
| 16x200 mm | 7130620631 | Kg | 4 | 62 | 248 | 3.5 | 62 | 217 | 4 | 62 | 248
16 | SUB TOTAL-1 |  |  |  |  | 37930.65 |  |  | 76214.5154 |  |  | 41939.626
17 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 3413.7585 |  |  | 6859.3064 |  | 0.09 | 3774.5663
18 | Service in lieu of concreting metal & sand only |  | Cmt | 2.9 | 2968.461 | 8608.5368 | 3.1 | 2968.461 | 9202.229 | 3.1 | 2968.461 | 9202.229
19 | Labour charges as per Schedule No.- AL-2 |  |  |  |  | 7344.69 |  |  | 7706.29 |  |  | 7872.71
20 | Transport charges upto 50 Kms average lead from Area Store to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 4606.8555 |  |  | 4606.8555 |  |  | 4606.8555
21 | SUB TOTAL-2 |  |  |  |  | 61904.4909 |  |  | 104589.1964 |  |  | 67395.9869
22 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 4172.3715 |  | 0.11 | 8383.5967 |  | 0.11 | 4613.3589
23 | Cost per DP for non-guaranteed works |  |  |  |  | 66076.8624 |  |  | 112972.793 |  |  | 72009.3458
24 | Cost per DP for non-guaranteed works (Round off) |  |  |  |  | 66077 |  |  | 112973 |  |  | 72009
Note:
1 | This Schedule is to be supplemented with Schedule A-1 & A-3.
2 | All the rates are with considering price variation clause.

## A-3
COST SCHEDULE - A-3
1 KM OF 33 kV LINE ON PCC POLES / H-BEAM SUPPORT WITH MAXIMUM SPAN OF 100 METERS USING DOG CONDUCTOR
[8 empty] | 2015-16 |  | NEW COLUMN ADDED
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152 mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 3129 | 31290
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 44.989 | 216981.947
3 | 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 10 No = 7800 Kgs | 7130601072 | Kg
4 | 365 Kg; 11 Mtr long PCC Pole |  | No | [6 empty] | 10 | 5022 | 50220 | New introduced
5 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2332 | 23320 | 10 | 2332 | 23320 | 10 | 2332 | 23320
6 | Back Clamp for Cross Arm
| (i) Stay Clamp For PCC Pole | 7130810193 | No | 10 | 265 | 2650 |  |  |  | 10 | 265 | 2650
| (ii) Stay Clamp For H-Beam Pole | 7130810692 | No |  |  |  | 10 | 294 | 2940
| (iii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iv) Stay Clamp for Rail Pole B Type | 7130810251 | No
7 | 33 kV Top Clamps | 7130810676 | No | 10 | 388 | 3880 | 10 | 388 | 3880 | 10 | 388 | 3880
8 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 100 | 1000 | 10 | 100 | 1000 | 10 | 100 | 1000
9 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 388 | 11640 | 30 | 388 | 11640 | 30 | 388 | 11640 | Earlier - 33 kV Pin Insulator
10 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 3100 | 64.842 | 201010.2 | 3100 | 64.842 | 201010.2 | 3100 | 64.842 | 201010.2
11 | Jointing Sleeves (suitable for 100 Sqmm, Al. Eq. ACSR cond.) | 7130830051 | No | 6 | 126 | 756 | 6 | 126 | 756 | 6 | 126 | 756
12 | Stay set 20 mm | 7130860033 | No | 3 | 705 | 2115 | 3 | 705 | 2115 | 3 | 705 | 2115
13 | Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 3 | 265 | 795 |  |  |  | 3 | 265 | 795
| (ii) Stay Clamp for "H" Beam | 7130810692 | No |  |  |  | 3 | 294 | 882
| (iii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iv) Stay Clamp for Rail Pole B Type | 7130810251 | No
14 | Stay Wire 7/8 SWG @ 8.5 kg Per stay | 7130860076 | Kg | 25.5 | 61.002 | 1555.551 | 25.5 | 61.002 | 1555.551 | 25.5 | 61.002 | 1555.551
15 | Concreting of Rail / H-Beam supports @ 0.6 cmt. Per pole and @ 0.3 Cmt per stay and @ 0.05 cmt per pole for base padding for PCC / Rail / H- Beam pole. |  | Cmt | 1.4 |  |  | 8 |  |  | 8
| Cement @ 208 Kg/cmt | 7130200401 | Kg | 291 | 5.36 | 1559.76 | 1352 | 5.36 | 7246.72 | 1352 | 5.36 | 7246.72
| Cement @ 208 Kg/Cmt for stay | 7130200401 | Kg | 312 | 5.36 | 1672.32 | 312 | 5.36 | 1672.32 | 312 | 5.36 | 1672.32
16 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 130 | 182 | 6 | 130 | 780 | 1.4 | 130 | 182
17 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 290 | 435 | 6 | 290 | 1740 | 1.5 | 290 | 435
18 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 10 | 66.528 | 665.28 | 10 | 66.528 | 665.28 | 10 | 66.528 | 665.28
19 | Danger Boards | 7130880041 | No | 10 | 74 | 740 | 10 | 74 | 740 | 10 | 74 | 740
20 | Binding wire and tape | 7130830006 | Kg | 3.5 | 139 | 486.5 | 3.5 | 139 | 486.5 | 3.5 | 139 | 486.5
21 | M.S. Nuts and Bolts |  | Kg | 18 |  |  | 18 |  |  | 18
| 16x40 mm | 7130620609 | Kg |  | 64 |  | 0.5 | 64 | 32 |  | 64
| 16x65 mm | 7130620614 | Kg |  | 63 |  | 7.5 | 63 | 472.5 |  | 63
| 16x90 mm | 7130620619 | Kg | 3.5 | 63 | 220.5 |  | 63 |  | 3.5 | 63 | 220.5
| 16x140 mm | 7130620625 | Kg |  | 62 |  | 10 | 62 | 620 |  | 62
| 16x160 mm | 7130620627 | Kg | 14.5 | 62 | 899 |  | 62 |  | 14.5 | 62 | 899
22 | Guarding |  |  |  | 11086.42 |  |  | 11086.42 |  |  | 11086.42
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 55.094 | 2699.606 | 49 | 55.094 | 2699.606 | 49 | 55.094 | 2699.606
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 55.094 | 1101.88 | 20 | 55.094 | 1101.88 | 20 | 55.094 | 1101.88
| (iii) 33 kV Guarding Channel | 7130897759 | No | 1 | 3315 | 3315 | 1 | 3315 | 3315 | 1 | 3315 | 3315
| (iv) Stay Clamp Set | 7130810692 | No | 3 | 294 | 882 | 3 | 294 | 882 | 3 | 294 | 882
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 62 | 74.4 | 1.2 | 62 | 74.4 | 1.2 | 62 | 74.4
| (vi) I-Bolt Big Size | 7130620013 | No | 4 | 118 | 472 | 4 | 118 | 472 | 4 | 118 | 472
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 705 | 1410 | 2 | 705 | 1410 | 2 | 705 | 1410
| (viii) Stay wire 7/8 SWG & 8.5 Kg/ stay | 7130860076 | Kg | 17 | 61.002 | 1037.034 | 17 | 61.002 | 1037.034 | 17 | 61.002 | 1037.034
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 63 | 94.5 | 1.5 | 63 | 94.5 | 1.5 | 63 | 94.5
23 | SUB TOTAL-1 |  |  |  |  | 297958.531 |  |  | 491622.438 |  |  | 322575.491
24 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 26816.2678 |  | 0.09 | 44246.0194 |  | 0.09 | 29031.7942
25 | Service in lieu of concreting metal & sand only |  | Cmt | 1.4 | 2968.461 | 4155.8454 | 8 | 2968.461 | 23747.6879 | 8 | 2968.461 | 23747.6879
26 | Labour charges as per Schedule No.- AL-3 |  |  |  |  | 32540.83 | -- | -- | 37867.15 |  |  | 35180.92
27 | Transport charges upto 50 Kms average lead form area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 14514.9157 |  |  | 14514.9157 |  |  | 14514.9157
28 | SUB TOTAL-2 |  |  |  |  | 375986.3899 |  |  | 611998.211 |  |  | 425050.8087
29 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 32775.4384 |  | 0.11 | 54078.4682 |  | 0.11 | 35483.304
30 | Cost per Km for non-guaranteed works |  |  |  |  | 408761.8283 |  |  | 666076.6791 |  |  | 460534.1127
31 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 408762 |  |  | 666077 |  |  | 460534
Note:
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
ITEMS REMOVED FROM SoR 2015-16
1 | 33 kV G.I. Pins with Nuts for 33 kV Pin Insulator | 7130820158

## A-3 (A)
COST SCHEDULE -- A-3 (A)
2015-16
SCHEDULE FOR AUGMENTATION OF 1 kM OF 33 kV LINE FROM RACCOON TO DOG CONDUCTOR
S.No. | Particulars | New SAP Bin Code | Unit | Qty | Cost per Unit | Cost
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | ACSR Dog Conductor 100 sq.mm | 7130830063 | Km | 3.1 | 64842 | 201010.2
2 | Jointing Sleeves suitable for Dog ACSR Conductor | 7130830051 | No | 6 | 126 | 756
3 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 6 | 388 | 2328 | Earlier - 33 kV Pin Insulator
4 | Guarding
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 55.094 | 2699.606
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 55.094 | 1101.88
| (iii) 33 kV Guarding Channel (Set) | 7130897759 | No | 1 | 3315 | 3315
| (iv) M.S Nut & Bolt 16x140 mm. | 7130620625 | Kg | 1.2 | 62 | 74.4
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 118 | 472
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 705 | 1410
| (vii) Stay Wire 7/8 SWG @ 8.5 Kg. Stay | 7130860076 | Kg | 17 | 61.002 | 1037.034
| (viii) MS Nut & Bolt 16x90 mm | 7130620619 | Kg | 1.5 | 63 | 94.5
5 | Concreting of Stay Set @ 0.3 Cmt per stay |  | Cmt | 0.6
| Cement @ 208 kg/ Cmt | 7130200401 | Kg | 124.8 | 5.36 | 668.928
6 | SUB TOTAL-1 |  | ` |  |  | 214967.548
7 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 19347.0793
8 | Service in lieu of concreting, metal & sand |  | Cmt | 0.6 | 2968.461 | 1781.0766
9 | Labour Charges |  |  |  |  | 15549.22
| Stay erection |  | No | 2 | 140.63 | 281.26
| Stringing of Dog Conductor |  | Ckt Km | 1 | 9040.24 | 9040.24
| Labour Charge for Guarding |  | Span | 1 | 1707.6 | 1707.6
| Dismantling Charges |  | Ckt Km | 1 | 4520.12 | 4520.12
10 | SUB TOTAL-2 |  |  |  |  | 251644.9239
11 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 23646.4303
12 | Returnable cost of old conductor assuming 25 years of life & 20 years in service |  |  | 3.1 | 5229.36 | 16211.016
13 | Cost per Km |  |  |  |  | 259080.3382
14 | Cost (Rounded Off) |  |  |  |  | 259080
ITEMS REMOVED FROM SoR 2015-16
1 | 33 kV G.I. Pins with Nuts | 7130820158

## A-3 (B)
COST SCHEDULE -- A-3 (B)
2015-16
COST SCHEDULE FOR ADDITIONAL (MID SPAN) POLE FOR 33 kV LINE USING 37.1 KG / MTR 13 M. LONG H-BEAM SUPPORT
S. No. | PARTICULARS | New SAP Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) H-Beam
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 482.3 | 44.989 | 21698.1947
2 | 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 1 No = 780 Kgs | 7130601072 | Kg
3 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 1 | 2332 | 2332
4 | Cross Arm Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 1 | 294 | 294
| (ii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iii) Stay Clamp for Rail Pole B Type | 7130810251 | No
5 | 33 kV Top Clamp | 7130810676 | No | 1 | 388 | 388
6 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 1 | 100 | 100
7 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 388 | 1164 | Earlier - 33 kV Pin Insulator
8 | Concreting of Rail / H-Beam support @ 0.6 Cmt. per pole and @ 0.05 Cmt per pole for base padding of Rail / H-Beam pole. |  | Cmt | 0.65
| Cement @ 208 Kg/cmt | 7130200401 | Kg | 135.2 | 5.36 | 724.672
9 | Red Oxide Paint | 7130211158 | Ltr | 1 | 130 | 130
10 | Aluminium Paint | 7130210809 | Ltr | 1 | 290 | 290
11 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 1 | 66.528 | 66.528
12 | Danger Boards | 7130880041 | No | 1 | 74 | 74
13 | Binding wire and tape | 7130830006 | Kg | 0.5 | 139 | 69.5
14 | M.S. Nuts and Bolts |  | Kg | 2.5
| 16x40 mm | 7130620609 | Kg | 0.5 | 64 | 32
| 16x65 mm | 7130620614 | Kg | 1 | 63 | 63
| 16x90 mm | 7130620619 | Kg |  | 63
| 16x140 mm | 7130620625 | Kg | 1 | 62 | 62
| 16x160 mm | 7130620627 | Kg |  | 62
15 | SUB TOTAL-1 |  |  |  |  | 27487.8947
16 | Incidental Charges @ 9 % : - |  |  |  | 0.09 | 2473.9105
17 | Service in lieu of concreting metal & sand only |  | Cmt | 0.65 | 2968.461 | 1929.4996
18 | Labour charges as per Schedule No.- AL-3 (B) (Revised for one Pole) |  |  |  |  | 2211.36
19 | Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 1451.4916
20 | SUB TOTAL-2 |  |  |  |  | 35554.1564
21 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 3023.6684
22 | Cost of erection of 1 No. of H-Beam Pole for 33 kV Line |  |  |  |  | 38577.8248
23 | Cost (Rounded Off) |  |  |  |  | 38578
ITEMS REMOVED FROM SoR 2015-16
1 | 33 kV G.I. Pins with Nuts for 33 kV Pin Insulator | 7130820158

## A-4
COST SCHEDULE A-4
1 KM OF 33 kV LINE ON 37.1 KG / MTR 13 M. LONG H-BEAM SUSPENSION TYPE WITH PANTHER CONDUCTOR (WITH MAXIMUM SPAN OF 50 METERS)
2015-16
S. No. | PARTICULARS | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M long (482.30 Kg) x 20 No = 9646 Kgs | 7130601958 | Kg | 9646 | 44.989 | 433963.894
2 | 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 20 No = 15600 Kgs | 7130601072 | Kg
3 | DC Cross arm (100x50 mm) Channel 2.4 Mtr. (1.5 X 20 = 30) | 7130810512 | No. | 30 | 3940 | 118200
4 | 33 kV Suspension Hardware suitable for Panther Conductor (3x20=60) | 7130820312 | Set | 60 | 2183 | 130980
5 | 33 kV Polymer Disc Insulator (9X20=180) | 7130820011 | No. | 180 | 354 | 63720 | Earlier- 33 kV Disc Insulator
6 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No, | 20 | 100 | 2000
7 | ACSR Panther Conductor with 5% sag | 7130830070 | Mtr. | 3150 | 167.935 | 528995.25
8 | Jointing Sleeves suitable for Panther conductor | 7130830971 | No. | 6 | 195 | 1170
9 | Stay Set 20 mm Complete | 7130860033 | Set. | 12 | 705 | 8460
10 | Stay Clamp for "H" Beam | 7130810692 | No. | 100 | 294 | 29400
11 | Stay Clamp for Rail Pole A Type | 7130810201 | No
12 | Stay Clamp for Rail Pole B Type | 7130810251 | No
13 | Stay Wire 7/8 SWG @ 8.5 Kg/Stay | 7130860076 | Kg. | 170 | 61.002 | 10370.34
14 | Concreting of Rail / H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt. per Pole for base Padding & @ 0.3 Cmt. Per stay |  | Cmt. | 17.2
| Cement @ 208 Kg/cmt | 7130200401 | Kg. | 3577.6 | 5.36 | 19175.936
15 | Red Oxide Paint | 7130211158 | Ltr. | 26 | 130 | 3380
16 | Aluminium Paint | 7130210809 | Ltr. | 26 | 290 | 7540
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg. | 20 | 66.528 | 1330.56
18 | Danger Boards | 7130880041 | No. | 20 | 74 | 1480
19 | Binding Wire & Tape | 7130830006 | Kg. | 8 | 139 | 1112
20 | MS Nut & Bolts |  | Kg. | 123
| 16x40 mm | 7130620609 | Kg. | 2 | 64 | 128
| 16x65 mm | 7130620614 | Kg. | 30 | 63 | 1890
| 16x90 mm | 7130620619 | Kg. | 20 | 63 | 1260
| 16x140 mm | 7130620625 | Kg. |  | 62
| 16x160 mm | 7130620627 | Kg. | 1 | 62 | 62
| 16x200 mm | 7130620631 | Kg. |  | 62
| 16x250 mm | 7130620637 | Kg. | 70 | 62 | 4340
21 | MS Angle 65x65x6 for Tie | 7130600032 | Kg. | 435 | 40.214 | 17493.09
22 | Strain Plate (65x8 mm) | 7130810624 | No. | 120 | 90 | 10800
23 | Guarding 33 kV for single span
| (i) G.I. Wire 6 SWG | 7130870045 | Kg. | 40 | 55.094 | 2203.76
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg. | 20 | 55.094 | 1101.88
| (iii) 33 kV Guarding Channel | 7130897759 | No. | 2 | 3315 | 6630
| (iv) M.S Nut & Bolt 16x250 mm. | 7130620637 | Kg. | 5 | 62 | 310
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 118 | 472
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 705 | 1410
| (vii) Stay Wire 7/8 SWG & 8.5 Kg. Stay | 7130860076 | Kg. | 17 | 61.002 | 1037.034
| (viii) Stay Clamp for "H" Beam | 7130810692 | No. | 2 | 294 | 588
| (ix) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (x) Stay Clamp for Rail Pole B Type | 7130810251 | No
| (xi) MS Nut & Bolt 16x90 mm | 7130620619 | Kg. | 1 | 63 | 63
24 | SUB TOTAL-1 |  |  |  |  | 1411066.744
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 126996.007
26 | Service in lieu of concreting metal & Sand only |  | Cmt | 17.2 | 2968.461 | 51057.5289
27 | Labour Charges per Km as per Schedule - AL-4 |  | Km | 1 |  | 104617.63
28 | Transport Charges up to 50 km average lead from area Stores to Construction Camp Including Side Transport |  | LS | LS |  | 27444.6296
29 | SUB TOTAL-2 |  |  |  |  | 1721182.5394
30 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 155217.3418
31 | Cost per Km for Non- guaranteed Works |  |  |  |  | 1876399.8813
32 | Cost per Km for Non- guaranteed Works (Rounded off ) |  |  |  |  | 1876400

## A-5
COST SCHEDULE A-5
33 kV D.P. STRUCTURE ON 13 M. LONG H-BEAM POLE FOR PANTHER CONDUCTOR (TO BE SUPPLEMENTED WITH EVERY 0.3 kM OF SUSPENSION LINE)
2015-16
S. No. | Particulars | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg. | 964.6 | 44.989 | 43396.3894
2 | 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 2 No = 1560 Kgs | 7130601072 | Kg
3 | DC Cross arm (100x50 mm) Channel 5' Center | 7130810608 | No. | 1 | 5377 | 5377
4 | 33 kV Tension Hardware suitable for Panther Conductor | 7130870318 | No. | 6 | 1003 | 6018
5 | 33 kV Suspension Hardware suitable for Panther Conductor | 7130820312 | No. | 3 | 2183 | 6549
6 | 33 kV Polymer Disc Insulator | 7130820011 | No. | 27 | 354 | 9558 | Earlier- 33 kV Disc Insulator
7 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 2 | 100 | 200
8 | Horizontal & Cross bracing |  | No. | 1
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 294 | 1176
| (ii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iii) M.S. Angle 65X65x6 mm | 7130600032 | Kg | 60 | 40.214 | 2412.84
9 | Stay Set 20 mm complete | 7130860033 | Set. | 6 | 705 | 4230
10 | Stay Clamp for "H" Beam | 7130810692 | No. | 9 | 294 | 2646
11 | Stay Clamp for Rail Pole A Type | 7130810201 | No
12 | Stay Clamp for Rail Pole B Type | 7130810251 | No
13 | Stay Wire 7/8 SWG @ 8.5 Kg./pole | 7130860076 | Kg. | 51 | 61.002 | 3111.102
14 | Concreting of Rail / H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt per Pole for base Padding & @ 0.3 Cmt. Per stay |  | Cmt. | 3.1
| Cement @ 208 Kg/cmt | 7130200401 | Kg. | 644.8 | 5.36 | 3456.128
15 | Red Oxide Paint | 7130211158 | Ltr. | 2 | 130 | 260
16 | Aluminium Paint | 7130210809 | Ltr. | 2 | 290 | 580
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 2 | 66.528 | 133.056
18 | Danger Board | 7130880041 | No | 2 | 74 | 148
19 | Strain Plate (65x8 mm) | 7130810624 | No. | 4 | 90 | 360
20 | MS Nut & Bolts |  | Kg. | 15
| 16x40 mm | 7130620609 | Kg. | 1 | 64 | 64
| 16x65 mm | 7130620614 | Kg. | 3 | 63 | 189
| 16x90 mm | 7130620619 | Kg. | 1 | 63 | 63
| 16x140 mm | 7130620625 | Kg. | 2 | 62 | 124
| 16x160 mm | 7130620627 | Kg. | 2 | 62 | 124
| 16x200 mm | 7130620631 | Kg. | 2 | 62 | 124
| 16x250 mm | 7130620637 | Kg. | 4 | 62 | 248
21 | SUB TOTAL-1 |  |  |  |  | 90547.5154
22 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 8149.2764
23 | Service in lieu of concreting metal & Sand only |  | Cmt | 3.1 | 2968.461 | 9202.229
24 | Labour Charges as per Schedule AL-2 |  |  |  |  | 7706.29
25 | Transport Charges up to 50 km. average lead from area Stores to Construction Camp including Side Transport (Transport Schedule T-1) |  |  |  |  | 4606.8555
26 | SUB TOTAL-2 |  |  |  |  | 120212.1664
27 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 9960.2267
28 | Cost per DP for Non- guaranteed Works |  |  |  |  | 130172.393
29 | Cost per DP for Non- guaranteed Works (Rounded off ) |  |  |  |  | 130172

## A-6
COST SCHEDULE A-6
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER RAILWAY TRACK FOR 60 MTR. LENGTH, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
2015-16
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD | 7132461004 | Mtr | 1020 | 120 | 122400 | 122400
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 371 | 38 | 14098 | 14098
3 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 1926.09 | 160 | 308174.4
4 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2104.858 | 160 |  | 336777.28
5 | End terminating jointing kit for 240 sqmm XLPE cable | 7130352037 | Set | 21050 | 4 | 84200
6 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 35084 | 4 |  | 140336
7 | GI pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 929 | 12 | 11148 | 11148
8 | GI bend 200 mm | 7130640028 | No | 805 | 4 | 3220 | 3220
9 | Caping of HDPE Pipe on both end of pipe with Concreting and Bricks work | 7130640029 | Cmt | 3220 | 4 | 12880 | 12880
10 | M.S.Flat (50x6) mm | 7130600173 | kg | 40.214 | 100 | 4021.4 | 4021.4
11 | Cable marker for U/G cable | 7130880006 | No | 113 | 4 | 452 | 452
12 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end. * | 7130642039 | No | 820 | 10 | 8200 | 8200
13 | Sundries |  | LS | LS | LS | 2200 | 2200
14 | SUB TOTAL-1 |  |  |  |  | 570993.8 | 655732.68
15 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 51389.442 | 59015.9412
16 | Service in lieu of Earthing Coal & Sand etc ** |  | No | 1828.5215 | 10 | 18285.2151 | 18285.2151
17 | Labour Charges as per Schedule AL-5 |  |  |  |  | 1393425.33 | 1393425.33
18 | Transportation Charges |  |  |  |  | 69304.6202 | 69304.6202
19 | SUB TOTAL-2 |  |  |  |  | 2103398.4072 | 2195763.7864
20 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 62809.318 | 72130.5948
21 | Way leave charges payable to Railway including supervision | 15% |  |  |  | 315509.7611 | 329364.568
22 | Cost per 50 Mtr for non guaranteed works |  |  |  |  | 2481717.4863 | 2597258.9492
23 | Cost per 50 Mtr for non guaranteed works (Rounded off ) |  |  |  |  | 2481717 | 2597259
* | 4 Nos earthing is for cable & 6 Nos. earthing is for 2 DP's
** | 3 Nos earthing cost Rs 5485.56, thus per earthing cost Rs 1828.52
*

## A-6 (A)
COST SCHEDULE A-6 (A)
SCHEDULE FOR 33 kV UNDERGROUND CABLE ROAD CROSSING FOR 50 MTR. LENGTH, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE
2015-16
S. No. | PARTICULARS | New Sap Bin Code | Unit | Rate | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RCC pipe Type NP - 3 (2.5 mtr long)
i | 600 mm | 7130640030 | Each | 3857
ii | 900 mm | 7130640036 | Each | 7661 | 50 | 383050
2 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 1926.09 | 50 | 96304.5
3 | End terminating jointing kit for 240 sqmm XLPE cable | 7130352037 | Set | 21050 | 2 | 42100
4 | Cable separator in RCC Pipe with Angle Cross of 50x50x6 mm Angle @ 2 No. in one pipe |  | No | 495 | 40 | 19800
5 | G.I. pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 929 | 12 | 11148
6 | G.I. bend 200 mm | 7130640028 | No | 805 | 2 | 1610
7 | Caping of RCC Pipe on both end of pipe with Concreting and Bricks work |  | Cmt | 3220 | 2 | 6440
8 | Sundries |  | LS | LS | LS | 2200
9 | SUB TOTAL-1 |  |  |  |  | 562652.5
10 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 50638.725
11 | Labour Charges as per Schedule CL-10 (Schedule is for 1 km line same has been revised as per 50 Mtrs.) |  |  |  |  | 9226.06
12 | SUB TOTAL-2 |  |  |  |  | 622517.285
13 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 61891.775
14 | Municipality Charges for reinstatement of Road as per Nagar Nigam |  | LS |  |  | 112000
15 | Cost per 50 Mtr for non guaranteed works |  |  |  |  | 796409.06
16 | Cost per 50 Mtr Undergrounding (Rounded off ) |  |  |  |  | 796409
17 | Transportation Charges as per Schedule |  |  |  |  | 69304.6202
18 | Total Cost including Transportation Charges |  |  |  |  | 865713.6202
19 | Total Cost (Rounded off ) |  |  |  |  | 865714

## A-7
COST SCHEDULE A-7
2015-16
SCHEDULE FOR LAST SPAN CABLING OF 33 kV H.T. CONNECTION
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 3x185 sq.mm AB XLPE Cable | 3x240 sq.mm AB XLPE Cable
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 44.989 | 482.3 | 21698.1947 | 21698.1947
2 | 60 Kg/Mtr 13.0 Mtr long Rails (780 Kg each) x 1 No = 780 Kgs | 7130601072 | Kg | 47.741 | 780
3 | 3x185 sq.mm 33 kV AB XLPE Cable | 7130310053 | Mtr. | 1180.744 | 50 | 59037.2
4 | 3x240 sq.mm 33 kV AB XLPE Cable | 7130310054 | Mtr. | 1501.438 | 50 |  | 75071.9
5 | 33 kV Termination Kit for 3x185 sqmm AB XLPE Cable * | 7130320039 | Set | 14859 | 2 | 29718
6 | 33 kV Termination Kit for 3x240 sqmm AB XLPE Cable * | 7130320040 | Set | 17336 | 2 |  | 34672
7 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 100 | 1 | 100 | 100
8 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | No. | 3227 | 2 | 6454 | 6454
9 | Stay Set 20 mm | 7130860033 | No | 705 | 2 | 1410 | 1410
10 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 61.002 | 17 | 1037.034 | 1037.034
11 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay |  | Cmt |  | 1.25
| Cement @ 208 kg/ Cmt | 7130200401 | Kg | 5.36 | 260 | 1393.6 | 1393.6
12 | Red Oxide Paint | 7130211158 | Ltr | 130 | 1 | 130 | 130
13 | Aluminium Paint | 7130210809 | Ltr | 290 | 1 | 290 | 290
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 66.528 | 1 | 66.528 | 66.528
15 | Danger Board | 7130880041 | No | 74 | 1 | 74 | 74
16 | Stay Clamp for "H" Beam | 7130810692 | No | 294 | 4 | 1176 | 1176
17 | Stay Clamp for Rail Pole A Type | 7130810201 | No | 282 | 4
18 | Stay Clamp for Rail Pole B Type | 7130810251 | No | 282 | 4
19 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 64 | 5 | 320 | 320
20 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 63 | 1 | 63 | 63
21 | Dead end Assembly (Suitable for all size cable) | 7130877681 | No. | 2270 | 2 | 4540 | 4540
22 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 820 | 2 | 1640 | 1640
23 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5 | 25 | 125 | 125
24 | SUB TOTAL-1 |  |  |  |  | 129272.5567 | 150261.2567
25 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 11634.5301 | 13523.5131
26 | Labour Charges |  |  | 32243.8248 | 1 | 32243.8248 | 32243.8248
27 | Transport Charges |  |  | 12600.84 | 1 | 12600.84 | 12600.84
28 | Service in lieu of Concreting |  | Cmt | 2968.461 | 1.25 | 3710.5762 | 3710.5762
29 | Service in lieu of Earthing Coal & Sand etc |  | No | 1828.5215 | 2 | 3657.043 | 3657.043
30 | SUB TOTAL-2 |  |  |  |  | 193119.3709 | 215997.0539
31 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 14219.9812 | 16528.7382
32 | GRAND TOTAL |  |  |  |  | 207339.3521 | 232525.7921
33 | GRAND TOTAL (Round Off) |  |  |  |  | 207339 | 232526
* | Note -- Appropriate size of termination kit and 33 kV AB XLPE Cable may be used for S.No 04 and 05 acccording to the load of HT connection.

## A-8
COST SCHEDULE A-8
33 kV MEDP STRUCTURE ON PCC POLE / H-BEAM POLE (TO BE SUPPLEMENTED FOR H.T. CONNECTION)
2015-16
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg/Mtr 13.0 Mtr long H-Beam
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 3129 | 6258
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr; 13 Mtr long (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 44.989 | 43396.3894
| (iii) 60 Kg/Mtr 13.0 Mtr long Rail Pole (780 Kg each) x 2 No = 1560 Kgs | 7130601072 | Kg
2 | DC cross arm of 100x50 mm Channel (3.8 Mtr. Long) | 7130810608 | Set | 2 | 5377 | 10754 | 2 | 5377 | 10754
3 | 33 kV Polymer Disc Insulator | 7130820011 | No | 18 | 354 | 6372 | 18 | 354 | 6372 | Earlier- 33 kV Disc Insulator
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 6 | 255 | 1530 | 6 | 255 | 1530
5 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 388 | 1164 | 3 | 388 | 1164 | Earlier - 33 kV Pin Insulator
6 | (i) Stay set 20 mm | 7130860033 | No | 6 | 705 | 4230 | 4 | 705 | 2820
| (ii) Stay Clamp for PCC Pole | 7130810193 | No | 6 | 265 | 1590
| (iii) Stay Clamp for "H" Beam | 7130810692 | No |  |  |  | 4 | 294 | 1176
| (iv) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (v) Stay Clamp for Rail Pole B Type | 7130810251 | No
| (vi) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 51 | 61.002 | 3111.102 | 34 | 61.002 | 2074.068
7 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 90 | 540 | 6 | 90 | 540
8 | Concreting of Rail / H-Beam supports @ 0.6 Cmt per pole and @ 0.5 Cmt per pole for PCC; @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / Rail / H-Beam pole. |  | Cmt | 2.9 |  |  | 2.5
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 603.2 | 5.36 | 3233.152 | 520 | 5.36 | 2787.2
9 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 2 | 100 | 200 | 2 | 100 | 200
10 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 130 | 65 | 2 | 130 | 260
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 290 | 145 | 2 | 290 | 580
12 | Barbed wire (@ 2 Kg/Pole) | 7130610206 | Kg | 7 | 66.528 | 465.696 | 7 | 66.528 | 465.696
13 | Danger Board | 7130880041 | No | 1 | 74 | 74 | 1 | 74 | 74
14 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 64 | 32 | 0.5 | 64 | 32
| 16x65 mm | 7130620614 | Kg | 0.5 | 63 | 31.5 | 0.5 | 63 | 31.5
| 16x90 mm | 7130620619 | Kg |  | 63 |  | 2.5 | 63 | 157.5
| 16x140 mm | 7130620625 | Kg | 2 | 62 | 124 |  | 62
| 16x200 mm | 7130620631 | Kg | 4 | 62 | 248 | 3.5 | 62 | 217
15 | GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 2 | 820 | 1640 | 2 | 820 | 1640
16 | G.I.Bend of 40 mm dia. |  | Each | 1 | 90 | 90 | 1 | 90 | 90
17 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3 | 3483 | 10449 | 3 | 3483 | 10449 | Earlier 33 kV Gapless type LA used
18 | 33 kV CTPT unit of appropriate capacity |  | No
19 | Copper control cable 10 Core 2.5 Sqmm. (armoured) | 7130310660 | Mtr | 10 | 172.208 | 1722.08 | 10 | 172.208 | 1722.08
20 | H.T. Static Trivector Meter 3 Ø 4 Wire 0.5 S with DLMS Protocol category A | 7131310033 | No | 1 | 3970 | 3970 | 1 | 3970 | 3970
21 | Universal Meter Box for HT meters. | 7132406425 | Each | 1 | 2528 | 2528 | 1 | 2528 | 2528
22 | Test terminal Box (TTB) | 7131310037 | Each | 1 | 870 | 870 | 1 | 870 | 870
23 | SUB TOTAL-1 |  |  |  |  | 61436.53 |  |  | 95900.4334
24 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 5529.2877 |  | 0.09 | 8631.039
25 | Service in lieu of concreting metal & sand only |  | Cmt | 2.9 | 2968.461 | 8608.5368 | 2.5 | 2968.461 | 7421.1525
26 | Labour charges as per Schedule No.- AL-2 |  |  |  |  | 7344.69 |  |  | 7706.29
27 | Transport charges upto 50 Kms average lead from Area Store to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 4606.8555 |  |  | 4606.8555
28 | SUB TOTAL-2 |  |  |  |  | 87525.9001 |  |  | 124265.7704
29 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 6758.0183 |  | 0.11 | 10549.0477
30 | Cost per DP for non-guaranteed works |  |  |  |  | 94283.9184 |  |  | 134814.8181
31 | Cost per DP for non-guaranteed works (Round off) |  |  |  |  | 94284 |  |  | 134815
Note:- 1. This Schedule is to be supplemented with Schedule A-1 & A-3.
2. All the rates are with considering price variation clause.
ITEMS REMOVED FROM SoR 2015-16
1 | 33 kV G.I. Pins with Nuts for 33 kV Pin Insulator | 7130820158

## A-9
COST SCHEDULE A-9
2015-16
SCHEDULE FOR LAST SPAN CABLING OF 33 kV LINE USING COVERED CONDUCTOR OF 70 & 99 SQ.MM SIZE
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 70 sq.mm Covered Conductor | 99 sq.mm Covered Conductor
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 44.989 | 482.3 | 21698.1947 | 21698.1947
2 | 33 kV Covered conductor 70 sq.mm (207 Amp) (with 3% sag) |  | Mtr. | 675.6 | 50 | 33780
3 | 33 kV Covered conductor 99 sq.mm (258 Amp) (with 3% sag) |  | Mtr. | 768.36 | 50 |  | 38418
4 | 33 kV Polymer Disc Insulator | 7130820011 | Set | 354 | 3 | 1062 | 1062
5 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 100 | 1 | 100 | 100
6 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | No. | 3227 | 2 | 6454 | 6454
7 | Stay Set 20 mm | 7130860033 | No | 705 | 2 | 1410 | 1410
8 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 61.002 | 17 | 1037.034 | 1037.034
9 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay |  | Cmt |  | 1.25
| Cement @ 208 kg/ Cmt | 7130200401 | Kg | 5.36 | 260 | 1393.6 | 1393.6
10 | Red Oxide Paint | 7130211158 | Ltr | 130 | 1 | 130 | 130
11 | Aluminium Paint | 7130210809 | Ltr | 290 | 1 | 290 | 290
12 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 66.528 | 1 | 66.528 | 66.528
13 | Danger Board | 7130880041 | No | 74 | 1 | 74 | 74
14 | Stay Clamp for "H" Beam | 7130810692 | No | 294 | 4 | 1176 | 1176
15 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 64 | 5 | 320 | 320
16 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 63 | 1 | 63 | 63
17 | Dead end Assembly (Suitable for all size cable) | 7130877681 | No. | 2270 | 2 | 4540 | 4540
18 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 820 | 3 | 2460 | 2460
19 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5 | 25 | 125 | 125
20 | SUB TOTAL-1 |  |  |  |  | 76179.3567 | 80817.3567
21 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 6856.1421 | 7273.5621
22 | Labour Charges |  |  | 32243.8248 | 1 | 32243.8248 | 32243.8248
23 | Transport Charges |  |  | 12600.84 | 1 | 12600.84 | 12600.84
24 | Service in lieu of Concreting |  | Cmt | 2968.461 | 1.25 | 3710.5762 | 3710.5762
25 | Service in lieu of Earthing Coal & Sand etc |  | No | 1828.5215 | 2 | 3657.043 | 3657.043
26 | SUB TOTAL-2 |  |  |  |  | 135247.7829 | 140303.2029
27 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 8379.7292 | 8889.9092
28 | GRAND TOTAL |  |  |  |  | 143627.5121 | 149193.1121
29 | GRAND TOTAL (Round Off) |  |  |  |  | 143628 | 149193

## B-1
COST SCHEDULE B -1
SCHEDULE FOR 33/11 kV, 3.15 MVA, 1.6 MVA SUB-STATION WITH TWO BAYS FOR OUTGOING FEEDERS AND 5 MVA SUB-STATION WITH THREE BAYS FOR OUTGOING FEEDERS AT NEW SITE
2015-16
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Proposed 33/11 kV S/s expandable to 2x1.6 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x3.15 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x5 MVA with control room
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 |  | LAND AND CIVIL WORKS
| i | Area fencing with Barbed wire & RCC post |  | RM | 396 | 400 | 158400 | 400 | 158400 | 400 | 158400
| ii | Drilling of bore well (60 Mtr. deep) with Submersible / Jet pump, overhead tank & pipe line for earth pit |  | Each | 172300 | 1 | 172300 | 1 | 172300 | 1 | 172300
| iii | Construction of control room with toilet (size 9.8 mtr x 5.5 mtr control room). |  | No | 856000 | 1 | 856000 | 1 | 856000 | 1 | 856000
| iv | Chain link mesh yard fencing with 65x65x6 mm 3 Mtr. Height M.S.Angle. |  | RM | 3000 | 140 | 420000 | 140 | 420000 | 140 | 420000
| v | Iron Gate [3.26 x 1.8 m (Weight approx. 300 Kg) in RCC Column of size 40x40 cm] |  | Each | 39600 | 2 | 79200 | 2 | 79200 | 2 | 79200
| vi | Yard levelling & Moorum filling 40x30 x 0.30 m area |  | Cmt | 350 | 300 | 105000 | 300 | 105000 | 300 | 105000
| vii | Yard Metalling 30 m x 30 m x 0.2 m |  | Cu. M | 1300 | 180 | 234000 | 180 | 234000 | 180 | 234000
| viii | WBM Road (3.75 Mtr wide) |  | Mtr | 1862 | 120 | 223440 | 120 | 223440 | 120 | 223440
| ix | Hume pipe culvert (450 mm dia) |  | Each | 43200 | 1 | 43200 | 1 | 43200 | 1 | 43200
| x | Brick masonary retaining wall 1 Mtr. High. |  | RM | 1800 | 130 | 234000 | 130 | 234000 | 130 | 234000
|  | Sub total-1 | 7: 2525540; 9: 2525540; 11: 2525540
2 |  | EQUIPMENTS
| i | 33/11 kV transformer 1.60 MVA | 7132220091 | No | 841136 | 1 | 841136 | -- | -- | -- | --
|  | 33/11 kV transformer 3.15 MVA | 7132220095 | No | 2112952 | -- |  | 1 | 2112952 | -- | --
|  | 33/11 kV transformer 5.00 MVA | 7132220097 | No | 3010759 | -- |  | -- |  | 1 | 3010759
| ii | 33 kV VCB (With CT's & panel) | 4: No; 5: 317003; 6: --; 8: 1
|  | (i) 33 kV VCB (Without CT's & Panel) | 7131943380 | No | 226584 | -- |  | 1 | 226584 | 1 | 226584
|  | (ii) 33 kV Control Panel | 7131960524 | No | 39815 | -- |  | 1 | 39815 | 1 | 39815
|  | (iii) 33 kV CT's 200-100/5 Amps | 7132230265 | No | 16868 | -- |  | 3 | 50604 | 3 | 50604
| iii | 11 kV VCB for X'mer protection (With CTs & panel) | 4: No; 5: 177261; 6: 1; 8: 1; 10: 1
|  | (i) 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 110737 | 1 | 110737 | 1 | 110737 | 1 | 110737
|  | (ii) 11 kV Control Panel for Transformer Protection | 7131960522 | Each | 39815 | 1 | 39815 | 1 | 39815 | 1 | 39815
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | No | 8903 | 3 | 26709 | 3 | 26709 | 3 | 26709
| iv | 11 kV VCB for feeder protection with CTs & panel. | 4: No; 5: 327554; 6: 2; 8: 2; 10: 3
|  | (i) 11 kV VCB with Relay & Control Panel | 7131960497 | No | 137068 | 2 | 274136 | 2 | 274136 | 3 | 411204 | 7131941762+7131960008=7131960497
|  | (ii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 8903 | 6 | 53418 | 6 | 53418 | 9 | 80127
| v | 33 kV Isolator (600 A.) Set without earth switch | 7131930752 | No | 35789 | 2 | 71578 | 2 | 71578 | 2 | 71578 | CORRECTED, EARLIER-33 kV Isolator (600 A.) Set
| vi | 11 kV Isolator (600 A.) (including 2 Nos. for capacitor bank) Set | 7131930663 | No | 20680 | 6 | 124080 | 6 | 124080 | 8 | 165440
| vii | 33 kV DO Fuse unit | 7131930415 | Each | 2918 | 3 | 8754 | -- | -- | -- | --
| viii | 11 kV DO Fuse unit | 7131930412 | Each | 1199 | 3 | 3597 | 3 | 3597 | 3 | 3597
| ix | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3483 | 3 | 10449 | 3 | 10449 | 3 | 10449 | Polymer L.A. replaces Porcelain
| x | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 425 | 12 | 5100 | 12 | 5100 | 15 | 6375 | Polymer L.A. replaces Porcelain
| xi | 33 kV AB Switch | 7131930321 | Each | 18624 | 1 | 18624 | 1 | 18624 | 1 | 18624
| xii | 11 kV AB Switch | 7131930221 | Each | 7750 | 3 | 23250 | 3 | 23250 | 4 | 31000
| xiii | Single phase 33 kV PT | 7132230057 | Each | 16371 | 3 | 49113 | 3 | 49113 | 3 | 49113 | Old Bin Code-7132230482
| xiv | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 64587 | 1 | 64587 | 1 | 64587 | 1 | 64587
| xv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 29949 | 2 | 59898 | 2 | 59898 | 3 | 89847
| xvi | Single phase 11 kV PT's | 7132230056 | Each | 8903 | 6 | 53418 | 6 | 53418 | 9 | 80127 | Old Bin Code-7132230472
| xvii | LT Meter (CT Operated) 100/5 A with CT's | 4: No; 5: 3492; 6: 1; 8: 1; 10: 1
|  | (i) LT Meter (CT Operated) 100/5 A | 7131310997 | No | 2487 | 1 | 2487 | 1 | 2487 | 1 | 2487
|  | (ii) LT CT 100/5 A | 7132230016 | No | 335 | 3 | 1005 | 3 | 1005 | 3 | 1005
| xviii | H.T. STATIC TRIVECTOR METERS | 4: No; 5: 15880; 6: 3; 8: 3; 10: 4
|  | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | 7131310033 | No | 3970 | 4 | 15880 | 4 | 15880 | 4 | 15880
| xix | Lead Acid Battery with automatic charger | 4: No; 5: 58477; 6: 1; 8: 1; 10: 1
|  | (i) Lead Acid Battery | 7132404366 | No | 49161 | 1 | 49161 | 1 | 49161 | 1 | 49161
| 1 | (ii) Battery Charger | 7132468558 | No | 9316 | 1 | 9316 | 1 | 9316 | 1 | 9316
| xx | 33/0.4 kV station transformer (50 kVA) | 7132210215 | Each | 146905 | 2 | 293810 | 2 | 293810 | 2 | 293810
| xxi | LT Distribution box for 63 kVA X'mer | 7131950065 | Each | 13758 | 1 | 13758 | 1 | 13758 | 1 | 13758
| xxii | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 6 Nos = 2448.6 Kgs | 7130601958 | Kg | 44.989 | 2448.6 | 110160.0654 | 2448.6 | 110160.0654 | 2448.6 | 110160.0654 | Replaced -Steel tubular poles 12 Meter long | 7130800068
| xxiii | Control cable
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr. | 125.719 | 180 | 22629.42 | 240 | 30172.56 | 300 | 37715.7
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr. | 67.671 | 780 | 52783.38 | 900 | 60903.9 | 1020 | 69024.42
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr. | 39.708 | 180 | 7147.44 | 240 | 9529.92 | 300 | 11912.4
| xxiv | Tee Clamp for Dog Conductor | 7130830585 | No | 239 | 99 | 23661 | 99 | 23661 | 105 | 25095
| xxv | Bi-metallic clamps | 7130830052 | No | 534 | 7 | 3738 | 7 | 3738 | 7 | 3738
| xxvi | Danger Board for 33 kV & 11 kV equipment/ supply pole | 7130880041 | No | 74 | 10 | 740 | 10 | 740 | 10 | 740
| xxvii | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 47.741 | 300 | 14322.3 | 300 | 14322.3 | 300 | 14322.3
| xxviii | Marshelling Box | 7130352046 | No. | 3096 | 6 | 18576 | 6 | 18576 | 7 | 21672
|  | Sub-total - 2 | 7: 2477573.6054; 9: 4075684.7454; 11: 5266887.8854
3 |  | STRUCTURE AND BUS BAR ARRANGEMENTS: -
| i | 8 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) ie 37.1x8 mtr =296.8 kg/pole x 10 Nos = 2968 Kgs. | 7130601958 | Kg | 44.989 | 2968 | 133527.352 | 2968 | 133527.352 | 3561.6 | 160232.8224
| ii | 7 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) ie 37.1x7mtr = 259.7 Kg/pole x 4 Nos = 1038.8 Kgs. | 7130601958 | Kg | 44.989 | 1038.8 | 46734.5732 | 1038.8 | 46734.5732 | 1038.8 | 46734.5732
| iii | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 8 Nos = 3264.8 Kgs | 7130601958 | Kg | 44.989 | 3264.8 | 146880.0872 | 3264.8 | 146880.0872 | 4081 | 183600.109
| iv | MS DC Cross arm (100 x 50 x 6 mm Channel) 5.2 Mtr long Set | 7130810684 | No | 8457 | 22 | 186054 | 22 | 186054 | 28 | 236796
| v | MS DC Cross arm (100 x 50 x 6 mm Channel) 3.8 Mtr long Set | 7130810006 | No | 6808 | 8 | 54464 | 8 | 54464 | 8 | 54464
| vi | MS DC Cross arm (100 x 50 x 6 mm Channel) 2.7 Mtr long Set | 7130810608 | No | 5377 | 7 | 37639 | 7 | 37639 | 9 | 48393
| vii | ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr | 64.842 | 500 | 32421 | 500 | 32421 | 600 | 38905.2
| viii | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 388 | 6 | 2328 | 6 | 2328 | 9 | 3492 | Earlier- 33 kV Pin Insulator
| ix | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 157 | 9 | 1413 | 12 | 1884 | 12 | 1884 | Earlier- 11 kV Pin Insulator
| x | Polymer Disc Insulator for 33 kV Side | 7130820011 | Each | 354 | 81 | 28674 | 81 | 28674 | 81 | 28674 | Earlier- Porcelain Disc Insulator
|  | 33 kV Strain Hardware fitting | 7130820248 | Each | 255 | 81 | 20655 | 81 | 20655 | 102 | 26010
| xi | Polymer Disc insulator for 11 kV side (double disc) | 7130820010 | Each | 140 | 108 | 15120 | 108 | 15120 | 150 | 21000 | Earlier-Porcelain Disc Insulator
|  | 33 kV Strain Plate 8 mm thick | 7130810624 | Each | 90 | 198 | 17820 | 198 | 17820 | 246 | 22140
|  | Sub-total - 3 | 7: 723730.0124; 9: 724201.0124; 11: 872325.7046
4 |  | OTHER MISCELLANEOUS ITEMS: -
| i | Concreting of structures & foundation (1:3:6) | 4: Cmt
|  | (i) Cement | 7130200401 | Kg | 5.36 | 10233.6 | 54852.096 | 12147.2 | 65108.992 | 13395.2 | 71798.272
| ii | 70 Sqmm, 3.5 Core PVC cable | 7130311054 | Mtr. | 213.718 | 10 | 2137.18 | 10 | 2137.18 | 10 | 2137.18
| iii | 16 Sqmm 4-core Cable for Switch yard lighting, tripping arrangement & system control (armoured) | 7130311084 | Mtr. | 99.916 | 300 | 29974.8 | 300 | 29974.8 | 300 | 29974.8
| iv | Mercury vapour lamp for Gate lighting 2 Nos. | 7131230128 | No | 1967 | 4 | 7868 | 4 | 7868 | 4 | 7868
| v | Earthing of Sub-station including Distribution Transformer earthing. | bar: 4; 6; 8; 10
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4169 | 21 | 87549 | 21 | 87549 | 21 | 87549
|  | (ii) GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 820 | 40 | 32800 | 40 | 32800 | 40 | 32800
|  | (iii) MS flat 50x6 mm size (2.5 kg per meter) | 7130600173 | Kg | 40.214 | 1000 | 40214 | 1000 | 40214 | 1000 | 40214
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 55.094 | 31 | 1707.914 | 31 | 1707.914 | 31 | 1707.914
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 89 | 25 | 2225 | 25 | 2225 | 25 | 2225
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 89 | 10 | 890 | 10 | 890 | 10 | 890 | CORRECTED FROM 16X60
|  | (vii) GI Spring washers | 7130622922 | Kg | 127 | 5 | 635 | 5 | 635 | 5 | 635
|  | MS Nuts & Bolts | 4: Kg; 6: 186; 8: 270; 10: 270
|  | (i) MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 64 | 10 | 640 | 15 | 960 | 15 | 960
|  | (ii) MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 63 | 5 | 315 | 10 | 630 | 10 | 630
|  | (iii) MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 63 | 15 | 945 | 25 | 1575 | 25 | 1575
|  | (iv) MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 62 | 66 | 4092 | 85 | 5270 | 85 | 5270
|  | (v) MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 62 | 80 | 4960 | 110 | 6820 | 110 | 6820
|  | (vi) MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 62 | 10 | 620 | 25 | 1550 | 25 | 1550
| vi | Furniture
|  | (i) Table 4'x2.5' | 7132476002 | No | 3940 | 1 | 3940 | 1 | 3940 | 1 | 3940 | Rate for Bin code not maintained
|  | (ii) Chair | 7132409061 | No | 2998 | 2 | 5996 | 2 | 5996 | 2 | 5996
|  | (iii) Small Steel Almirah 50'' | 7132401672 | No | 5128 | 1 | 5128 | 1 | 5128 | 1 | 5128
| vii | Fire fighting equipments | bar: 4
|  | (i) Fire fighting equipments (dry chemical powder type 5 Kg capacity) | 7132490006 | No | 4619 | 2 | 9238 | 2 | 9238 | 2 | 9238
|  | (ii) Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | 7132421002 | No | 5166 | 2 | 10332 | 2 | 10332 | 2 | 10332
| viii | Electrically insulated 11 kV mats infront of electrical control panel | 7132448003 | No | 3710 | 3 | 11130 | 3 | 11130 | 3 | 11130 | Old Bin Code-7132448851
|  | Sub-total - 4 | 7: 318188.99; 9: 333678.886; 11: 340368.166
5 |  | Total including Civil works | 7: 6045032.6078; 9: 7659104.6438; 11: 9005121.756
6 |  | Total excluding Civil works | 7: 3519492.6078; 9: 5133564.6438; 11: 6479581.756
7 |  | Incidental Charges @ 9 % on "6" above | 5: 0.09; 7: 316754.3347; 9: 462020.8179; 11: 583162.358
| (i) | Services on S/s earthing |  | No | 18292.8554 | 1 | 18292.8554 | 1 | 18292.8554 | 1 | 18292.8554
| (ii) | Services on Cable trench (separate trench for power cable & control cable). |  | Mtr. | 1569.8592 | 70 | 109890.1421 | 70 | 109890.1421 | 80 | 125588.7338
| (iii) | Services on Painting of structures |  | No | 11773.9438 | 1 | 11773.9438 | 1 | 11773.9438 | 1 | 11773.9438
| (iv) | Services on Labelling of equipments |  | No | 9811.6198 | 1 | 9811.6198 | 1 | 9811.6198 | 1 | 9811.6198
| (v) | Services on concreting |  | Cmt | 2968.461 | 49.2 | 146048.2803 | 58.4 | 173358.1213 | 64.4 | 191168.8872
8 |  | Labour charges as per sch. (BL-1+BL-3) | 7: 147968; 9: 157391; 11: 179539
9 |  | Transport charges | 7: 32933.5555; 9: 32933.5555; 11: 36592.8394
10 |  | Total cost of Sub-station (Including Civil works) | 7: 6838505.3394; 9: 8634576.6997; 11: 10161051.9935
11 |  | Total Cost (Rs In lakhs) | 7: 68.3851; 9: 86.3458; 11: 101.6105
12 |  | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] | 5: 0.11; 7: 387144.1869; 9: 564692.1108; 11: 712753.9932
13 |  | Grand Total cost of S/s. | 7: 7225649.5263; 9: 9199268.8105; 11: 10873805.9867
14 |  | Grand Total (Rounded off) | 7: 7225650; 9: 9199269; 11: 10873806
15 |  | Grand Total cost (Rs in LAKHS) | 7: 72.2565; 9: 91.9927; 11: 108.7381
Note:
| (1) | All the rates are with considering price variation clause.
| (2) | In case of non-availability of H-Beam for structure double welded RS Joist may be used (1) 8 meter long double welded RS Joist and cost of it shall be taken in place of cost of item No.3 (i) unit rate as Rs 10640.00 & quantity should be 10 Nos for 3.15 & 1.6 MVA and 12 Nos for 5 MVA (2) 7 meter long double welded RS Joist and cost of it shall be taken as in place of cost of item No.3 (ii) unit rate as Rs 9372.00 & quantity should be 04 Nos each for 3.15 & 1.6 MVA and 5 MVA
| (3) | The cost of land is not taken in to account since normally CSPDCL acquires Govt. land at negligible cost. How ever needs to be procure other than Govt. land then should be added actual cost.
DELETED IN 2015-16
|  | 33 kV G.I. Pin | 3: 7130820158; 4: Each
|  | 11 kV G.I. Pin | 3: 7130820155; 4: Each

## B-2
COST SCHEDULE B-2
2015-16
( 33 kV SUB-STATION )
POWER TRANSFORMERS
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | 1600 kVA | 3150 kVA | 5000 kVA
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Cost of Transformer as per Schedule of rates
| Power Transformer 1600 kVA | 7132220091 | No | 841136 | 1 | 841136
| Power Transformer 3150 kVA | 7132220095 | No | 2112952 | 1 |  | 2112952
| Power Transformer 5000 kVA | 7132220097 | No | 3010759 | 1 |  |  | 3010759
2 | SUB TOTAL-1 |  |  |  |  | 841136 | 2112952 | 3010759
3 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 75702.24 | 190165.68 | 270968.31
4 | Services for Painting |  |  |  |  | 3862.8425 | 6180.5479 | 6180.5479
5 | Labour charges as per Schedule BL-3 |  |  |  |  | 41020.06 | 48758.82 | 56756.45
6 | Transport charges upto 50 Km average lead from Area Store to construction camp including site transport (Transport Sch T-2) |  |  |  |  | 3407.3422 | 9821.5181 | 15321.9708
7 | SUB TOTAL-2 |  |  |  |  | 965128.4847 | 2367878.566 | 3359986.2787
8 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 92524.96 | 232424.72 | 331183.49
9 | Total cost |  |  |  |  | 1057653.4447 | 2600303.286 | 3691169.7687
10 | Total Cost (Rounded off) |  |  |  |  | 1057653 | 2600303 | 3691170
Note: | All the rates are with considering price variation clause.

## B-3
COST SCHEDULE B-3
|  |  | ( 33 kV SUB-STATIONS ) |  |  |  |  | 2015-16
SCHEDULE FOR INSTALLATION OF ADDITIONAL TRANSFORMER FOR PARALLEL OPERATION WITH TWO ADDITIONAL BAY ON 11 kV SIDE
S. No. | S.No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | Sub-station capacity
[7 empty] | 1.6 MVA | 3.15 MVA | 5.0 MVA
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 |  | EQUIPMENTS
| i | Power Transformer 33/11 kV
|  | Power Transformer 1.6 MVA | 7132220091 | No | 841136 | 1 | 841136
|  | Power Transformer 3.15 MVA | 7132220095 | No | 2112952 | 1 |  | 2112952
|  | Power Transformer 5 MVA | 7132220097 | No | 3010759 | 1 |  |  | 3010759
| ii | 33 kV VCB with CT's and panels. |  | No | 317003
|  | (i) 33 kV VCB ( without CT's and panels) | 7131943380 | No | 226584 | 1 |  | 226584 | 226584
|  | (ii) 33 kV Control Panel | 7131960524 | No | 39815 | 1 |  | 39815 | 39815
|  | (iii) 33 kV CT's 200-100/5A | 7132230265 | No | 16868 | 3 |  | 50604 | 50604
| iii | 11 kV VCB for X'mer protection with CT's and panels. |  | No | 177261 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | Each | 110737 | 1 | 110737 | 110737 | 110737
|  | (ii) 11 kV Control Panel for X-mer Protection | 7131960522 | Each | 39815 | 1 | 39815 | 39815 | 39815
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | Each | 8903 | 3 | 26709 | 26709 | 26709
| iv | 11 kV VCB for feeder protection with CT's and panels. |  | No | 163777 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | No | 110737 | 1 | 110737 | 110737 | 110737
|  | (ii) 11 kV Control Panel for feeder protection | 7131960008 | Each | 26331 | 1 | 26331 | 26331 | 26331
|  | (iii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 8903 | 3 | 26709 | 26709 | 26709
| v | 33 kV DO Fuse Unit | 7131930415 | Each | 2918 | 3 | 8754
| vi | 33 kV isolator, 600 A. Without earth switch | 7131930752 | No | 35789 | 2 | 71578 | 71578 | 71578
| vii | 11 kV isolator, 600 A | 7131930663 | No | 20680 | 5 | 103400 | 103400 | 103400
| viii | 33 kV Polymer Lightning Arrestor | 7130840021 | Each | 3483 | 3 | 10449 | 10449 | 10449
| ix | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 425 | 9 | 3825 | 3825 | 3825
| x | H.T. STATIC TRIVECTOR METERS |  | No | 15880
|  | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | 7131310033 | No | 3970 | 4 | 15880 | 15880 | 15880
| xi | 33 kV Single Phase PT | 7132230057 | Each | 16371 | 3 | 49113 | 49113 | 49113 | Old Bin Code-7132230482
| xii | 11 kV Single Phase PT | 7132230056 | Each | 8903 | 6 | 53418 | 53418 | 53418 | Old Bin Code-7132230472
| xiii | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 64587 | 1 | 64587 | 64587 | 64587
| xiv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 29949 | 2 | 59898 | 59898 | 59898
| xv | 33 kV AB switch | 7131930321 | Each | 18624 | 1 | 18624 | 18624 | 18624
| xvi | Marshelling Box | 7130352046 | No. | 3096 | 6 | 18576 | 18576 | 18576
2 |  | STRUCTURE AND BUS BAR ARRANGEMENT
| (i) | DO fuse supporting structure set on 7 Mtr long H- Beam 37.1 kg/mtr 33 kV & 11 kV side (2 No. each side) i.e. 37.1 kg x 7 = 259.7 kg/pole x 4 Nos = 1038.8 Kgs | 7130601958 | Kg | 44.989 | 1038.8 | 46734.5732 | 46734.5732 | 46734.5732
| (ii) | 33 kV additional bay ( 02 No H-Beam 152x152 mm 08 mtr long) with 6 Nos, 5.2 Mtr channel |  | Set | 121066.9408 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.20 Kgs | 7130601958 | Kg | 44.989 | 1187.2 | 53410.9408 | 53410.9408 | 53410.9408
|  | (ii) D.C.Cross arm Channel 5.2 mtr 100x50 mm | 7130810684 | No | 8457 | 8 | 67656 | 67656 | 67656
| (iii) | 11 kV, 2 Addl. bus bar structure 08 mtr long H- Beam 37.1 Kg/mtr with 4 Nos, 5.2 Mtr long DC cross arm (100 x 50 mm) |  | Set | 154894.9408 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.2 Kgs. | 7130601958 | Kg | 44.989 | 1187.2 | 53410.9408 | 53410.9408 | 53410.9408
|  | (ii) H-Beam 152x152 mm 11 mtr long 37.1 kg/mtr i.e.= 408.1 kg/pole x 4 No = 1632.40 Kgs | 7130601958 | Kg | 44.989 | 1632.4 | 73440.0436 | 73440.0436 | 73440.0436
|  | (iii) D.C.Cross arm Channel 5.2 mtr 100x50 mm (set) | 7130810684 | No | 8457 | 12 | 101484 | 101484 | 101484
|  | (iv) D.C.Cross arm 2.7 Meter 100x50 mm Channel | 7130810517 | No | 4547 | 7 | 31829 | 31829 | 31829
| (iv) | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 47.741 | 300 | 14322.3 | 14322.3 | 14322.3
| (v) | ACSR Dog conductor | 7130830063 | Mtr | 64.842 | 300 | 19452.6 | 19452.6 | 19452.6
| (vi) | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 388 | 3 | 1164 | 1164 | 1164 | Earlier- 33 kV Pin Insulator
| (vii) | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 157 | 6 | 942 | 942 | 942 | Earlier- 11 kV Pin Insulator
| (viii) | Bi-metallic clamps for transformer | 7130830052 | No | 534 | 7 | 3738 | 3738 | 3738
| (ix) | Bi-metallic clamps for VCBs | 7130830054 | No | 312 | 24 | 7488 | 7488 | 7488
| (x) | Strain hardware with strain set suitable for Dog conductor: -
|  | (a) 33 kV side with 3 disc insulator per phase. |  | Set | 41427 | 18
|  | (i) 33 kV Polymer Disc insulator . | 7130820011 | No | 354 | 63 | 22302 | 22302 | 22302 | Earlier- 33 kV Disc Insulator
|  | (ii) 33 kV Strain Hardware | 7130820248 | Each | 255 | 75 | 19125 | 19125 | 19125
|  | (b) 11 kV side with 2 disc insulator per phase. |  | Set | 25380 | 48
|  | (i) 11 kV Polymer Disc insulator | 7130820010 | No | 140 | 108 | 15120 | 15120 | 15120 | Earlier- 11 kV Disc Insulator
|  | (ii) Strain plate 8 mm thick | 7130810624 | No | 90 | 114 | 10260 | 10260 | 10260
| (xi) | T-clamp for jumper connection with AB Switches & DO fuses / Isolator. | 7130830585 | No | 239 | 66 | 15774 | 15774 | 15774
3 |  | OTHER MISCELLANEOUS ITEMS
| i | Cement for Concreting of structure @ 0.45 Cmt. per bus structure (1:3:6) = 7.2 Cmt for 16 Nos structure. | 7130200401 | Kg | 5.36 | 1497.6 | 8027.136 | 8027.136 | 8027.136
| ii | Cement for Con. Of X'mer foundation (1:3:6) = 15 cmt | 7130200401 | Kg | 5.36 | 3120 | 16723.2 | 16723.2 | 16723.2
| iii | Cement for Concreting of foundation of 11 kV VCB (1:3:6) =12 cmt. | 7130200401 | Kg | 5.36 | 2496 | 13378.56 | 13378.56 | 13378.56
| iv | Cement for Concreting of foundation of 33 kV VCB (1:3:6) =7 cmt. | 7130200401 | Kg | 5.36 | 1456 | 7804.16 | 7804.16 | 7804.16
| v | Cable trench for addl two VCB & Xmer | Services |  | 3630 | LS
| vi | Control cable for Xmer & VCB
|  | a) 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 125.719 | 180 | 22629.42 | 22629.42 | 22629.42
|  | b) 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 67.671 | 720 | 48723.12 | 48723.12 | 48723.12
|  | c) 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.708 | 180 | 7147.44 | 7147.44 | 7147.44
| vii | Earthing for addl X'mer & VCB |  | LS | 120000 | LS
Document – As per W/o of G.S. Flat mesh earthing of 33/11 kV S/s as per No. CE/RR/TR/4328/9029 Raipur, Dt. 05/03/2007 (Rate taken from Sch.- III)
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4169 | 21 | 87549 | 87549 | 87549
|  | (ii) GI Pipe of 40 mm dia 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 820 | 40 | 32800 | 32800 | 32800
|  | (iii) MS flat 50x6 mm size | 7130600173 | Kg | 40.214 | 400 | 16085.6 | 16085.6 | 16085.6
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 55.094 | 31 | 1707.914 | 1707.914 | 1707.914
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 89 | 25 | 2225 | 2225 | 2225
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 89 | 10 | 890 | 890 | 890
|  | (vii) GI Spring washers | 7130622922 | Kg | 127 | 5 | 635 | 635 | 635
| viii | M.S. Nut- Bolts |  | Kg |  | 125
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 64 | 10 | 640 | 640 | 640
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 63 | 8 | 504 | 504 | 504
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 63 | 25 | 1575 | 1575 | 1575
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 62 | 70 | 4340 | 4340 | 4340
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 62 | 80 | 4960 | 4960 | 4960
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 62 | 20 | 1240 | 1240 | 1240
4 |  | SUB TOTAL-A (1+2+3) |  |  |  |  | 2497513.9484 | 4077578.9484 | 4975385.9484
5 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 224776.2554 | 366982.1054 | 447784.7354
|  | (i) Services on Earthing |  | No. | 18292.8554 | 1 | 18292.8554 | 18292.8554 | 18292.8554
|  | (ii) Services on Painting |  | No. | 11773.9438 | 1 | 11773.9438 | 11773.9438 | 11773.9438
|  | Services on Labelling of equipments |  | No | 9811.6198 | 1 | 9811.6198 | 9811.6198 | 9811.6198
|  | Services on Concreting of structure @ 0.45 cmt/bus structure |  | Cmt | 2968.461 | 7.2 | 21372.9191 | 21372.9191 | 21372.9191
|  | Services on X'mer foundation [2.5(L)*2(W)*3(H)] |  | Cmt | 2968.461 | 15 | 44526.9147 | 44526.9147 | 44526.9147
|  | Services on foundation of 11 kV VCB [2(L)*2(W)*1.5(H)] |  | Cmt | 2968.461 | 12 | 35621.5318 | 35621.5318 | 35621.5318
|  | Services on foundation of 33 kV VCB [2(L)*2(W)*1.75(H)] |  | Cmt | 2968.461 | 7 | 20779.2269 | 20779.2269 | 20779.2269
|  | Services on Cable trench for addl. two VCB & X-mer |  | No | 1569.8592 | 30 | 47095.7752 | 47095.7752 | 47095.7752
6 |  | Labour charges: - |  |  |  |  | 120761.61 | 128500.61 | 136497.61
| i | X'mer erection (Labour sch BL-3) |  |  |  |  | 41020 | 48759 | 56756
| ii | Other items as per schedule [Labour Schedule BL-2+(3*BL-4)] |  |  |  |  | 79741.61 | 79741.61 | 79741.61
7 |  | Transport charges upto 50 Km lead from area stores to construction site for addl. lead refer Schedule T-2
| i | For Transformer only |  |  |  |  | 3306.7119 | 9485.4129 | 13500.9281
| ii | For other material (Excluding Power Transformer) |  |  |  |  | 7732.4329 | 9660.5096 | 10976.0222
8 |  | SUB TOTAL-B |  |  |  |  | 3063365.7452 | 4801482.3729 | 5793420.0307
9 |  | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 274726.5343 | 448533.6843 | 547292.4543
10 |  | Grand Total cost of S/s. |  |  |  |  | 3338092.2795 | 5250016.0572 | 6340712.485
11 |  | Grand Total cost of S/s. (Rounded off) |  |  |  |  | 3338092 | 5250016 | 6340712
Note: |  | (1) All the rates are with considering price variation clause.
(2) In case of non-availability of H-Beam for structure double welded RS Joist may be used and cost should be taken on actual material used
DELETED IN 2015-16
|  | 33 kV G.I. Pin | 7130820158 | Each
|  | 11 kV G.I. Pin | 7130820155 | Each
*

## B-4
COST SCHEDULE B-4
(33/11 kV SUB-STATIONS)
11 kV OUT DOOR YARD EXTENSION FOR ADDL. BAY WITH CIRCUIT BREAKER
2015-16
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | 1.6 MVA & Above
[6 empty] | Qnty | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | H-Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 No = 593.6 Kgs | 7130601958 | Kg | 44.989 | 593.6 | 26705.4704
2 |  | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1 x 11 mtr = 408.1 kg/pole x 2 Nos = 816.2 Kgs. | 7130601965 | Kg | 44.989 | 816.2 | 36720.0218 | Old Bin Code-7130601958
3 |  | MS DC Cross arm (100x50 mm), 5.2 Mtr long for bus bar | 7130810684 | Set | 8457 | 6 | 50742
4 |  | MS DC Cross arm (100x50 mm), 8' centre for bus bar | 7130810517 | Set | 4547 | 2 | 9094
5 |  | Strain set with hardware suitable for 100 Sqmm ACSR conductor for 11kV bus. |  | Set |  | 21
| (i) | 11 kV Polymer Disc insulator for double disc | 7130820010 | No | 140 | 42 | 5880 | Earlier- 11 kV Disc Insulator
| (ii) | Hardware suitable for 100 Sqmm ACSR Dog conductor for 11 kV bus. | 7130820248 | No | 255 | 21 | 5355
6 |  | 11 kV Polymeric Pin insulator with Pin | 7130820008 | Each | 157 | 3 | 471 | Earlier-11 kV Pin Insulator
7 |  | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 425 | 3 | 1275 | Earlier-11 kV Lightning Arrestor
8 |  | 11 kV Isolator (600 A.) | 7131930663 | Set | 20680 | 2 | 41360
9 |  | 11 kV AB Switch | 7131930221 | Each | 7750 | 1 | 7750
10 | Concreting of structure (1:3:6) |  |  | Cmt
| (i) | Cement | 7130200401 | Kg | 5.36 | 374.4 | 2006.784
11 |  | ACSR 100 Sqmm Al. Eq. Dog Conductor | 7130830063 | Mtr | 64.842 | 50 | 3242.1
12 |  | Terminal clamp for jumpering of 100 Sqmm Al. Eq ACSR Conductor / Isolator | 7130830585 | No | 239 | 24 | 5736
13 |  | 11 kV feeder control VCB with CT's (One 11 kV VCB controlling two feeders) with control panel. |  | No | 163777 | 1
| (i) | 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 110737 | 1 | 110737
| (ii) | 11 kV feeder Control Panel | 7131960008 | No | 26331 | 1 | 26331 | Old Bin Code-7131960494
| (iii) | 11 kV CT's 300-150/5 Amps | 7132230188 | No | 8903 | 3 | 26709
| (iv) | Marshelling Box | 7130352046 | No. | 3096 | 1 | 3096
14 |  | Foundation VCB |  | Cmt |  | 6
|  | (i) Cement | 7130200401 | Kg | 5.36 | 1248 | 6689.28
15 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 125.719 | 60 | 7543.14
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 67.671 | 120 | 8120.52
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.708 | 60 | 2382.48
16 |  | H.T. STATIC TRIVECTOR METER for feeder metering. |  | No | 3970 | 1
|  | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | 7131310033 | No | 3970 | 1 | 3970
17 |  | 11 kV CT/PT unit 200-100/5 Amp. | 7132230412 | Each | 29949 | 1 | 29949
18 |  | M.S. Nuts & Bolts |  | Kg |  | 30
| a | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 64 | 3 | 192
| b | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 63 | 2 | 126
| c | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 63 | 2 | 126
| d | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 62 | 6 | 372
| e | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 62 | 15 | 930
| f | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 62 | 2 | 124
19 |  | SUB TOTAL-1 |  |  |  |  | 423734.7962
20 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 38136.1317
21 | a | Services on Concreting of structure |  | Cmt | 2968.461 | 1.8 | 5343.2298
| b | Services on Concreting of VCB |  | Cmt | 2968.461 | 6 | 17810.7659
| c | Services on Painting of structure |  | No | 2747.2536 | 1 | 2747.2536
| d | Services on Cable trench for control kiosks |  | No | 3924.6479 | 1 | 3924.6479
22 |  | Labour charges as per Schedule No. BL-4 |  |  |  |  | 19544.61
23 |  | Transport charges upto 50 Km lead from area stores to construction site for addl. lead refer Schedule T-2. |  |  |  |  | 3848.103
24 |  | SUB TOTAL-2 |  |  |  |  | 515089.538
25 |  | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 46610.8276
26 |  | Total cost: - |  |  |  |  | 561700.3656
27 |  | Total cost (Rounded off): - |  |  |  |  | 561700
Note :- |  | All the rates are with considering price variation clause.
DELETED IN 2015-16
|  | 11 kV G.I. Pin | 7130820155 | Each

## B-5
COST SCHEDULE B-5
| (33/11 kV SUB-STATIONS) |  |  |  | 2015-16
33 kV OUT DOOR YARD EXTENSION FOR ADDITIONAL BAY.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 Nos = 593.6 Kgs | 7130601958 | Kg | 44.989 | 593.6 | 26705.4704
2 | MS DC cross arm (100x50 mm), 5.2 Mtr. long for bus bar | 7130810684 | Set | 8457 | 6 | 50742
3 | Strain set with hardware suitable for 80 Sqmm ACSR conductor for 33 kV bus(3 disc insulator per disc) |  | Set | 19755 | 15
| (i) 33 kV Polymer Disc Insulator | 7130820011 | No | 354 | 45 | 15930 | Earlier -Disc Insulator
| (ii) 33 kV Hardware | 7130820248 | Each | 255 | 15 | 3825
4 | 33 kV Isolator (600 A.) with earth switch | 7131930109 | No | 40392 | 2 | 80784
5 | Terminal clamp for isolators | 7130830585 | No | 239 | 12 | 2868
6 | T-clamps for bus jumper | 7130830585 | No | 239 | 6 | 1434
7 | ACSR 100 Sqmm Al. Eq. Conductor | 7130830063 | Mtr | 64.842 | 50 | 3242.1
8 | Concreting of structure (1:3:6) |  | Cmt
| (i) Cement | 7130200401 | Kg | 5.36 | 187 | 1002.32
9 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | Each | 388 | 6 | 2328 | Earlier- 33 kV Pin Insulator
10 | M.S. Nuts & Bolts |  | Kg |  | 40
| MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 64 | 2 | 128
| MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 63 | 3 | 189
| MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 63 | 5 | 315
| MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 62 | 15 | 930
| MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 62 | 10 | 620
| MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 62 | 5 | 310
11 | SUB TOTAL-1 |  |  |  |  | 191352.8904
12 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 17221.7601
13 | Services on Concreting of structure |  | Cmt | 2968.461 | 0.9 | 2671.6149
14 | Services on Painting on structure |  | No | 2747.2536 | 1 | 2747.2536
15 | Labour charges as per Schedule No BL-5 |  |  |  |  | 15162.64
16 | Transport charges upto 50 Km lead from Area stores to construction site for addl lead refer Schedule T-2. |  |  |  |  | 3848.103
17 | SUB TOTAL-2 |  |  |  |  | 233004.262
18 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 21048.8179
19 | Total cost: - |  |  |  |  | 254053.0799
20 | Total cost (Rounded off): - |  |  |  |  | 254053
Note: -For the provision of 33 kV VCB installation, the cost Schedule No.- B-6 may be referred to. All the rates are with considering price variation clause
DELETED IN 2015-16
| 33 kV G.I. Pin | 7130820158 | Each

## B-6
COST SCHEDULE B-6
2015-16
INSTALLATION OF 33 kV VCB
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | 33 kV VCB with control panel & CT |  | No | 323243 | 1
| (i) | 33 kV VCB (without CT's & Panel) | 7131943380 | No | 226584 | 1 | 226584
| (ii) | 33 kV Control Panel | 7131960524 | No | 39815 | 1 | 39815
| (iii) | 33 kV CT's 300-150/5 Amps | 7132230263 | No | 18948 | 3 | 56844
| (iv) | Marshelling Box | 7130352046 | No | 3096 | 1 | 3096
2 |  | Foundation of 33 kV breaker |  | Cmt |  | 7
| (i) | Cement | 7130200401 | Kg | 5.36 | 1456 | 7804.16
3 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 125.719 | 60 | 7543.14
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 67.671 | 120 | 8120.52
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.708 | 60 | 2382.48
4 |  | Terminal clamps | 7130830585 | No | 239 | 6 | 1434
5 |  | Tee clamp for jumper | 7130830585 | No | 239 | 6 | 1434
6 |  | SUB TOTAL-1 |  |  |  |  | 355057.3
7 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 31955.157
8 |  | Services on Concreting for foundation of VCB. |  | Cmt | 2968.461 | 7 | 20779.2269
9 |  | Labour charges as per Schedule No BL-6 |  |  |  |  | 5736.04
10 |  | Transportation charges |  |  |  |  | 6586.7027
11 |  | SUB TOTAL-2 |  |  |  |  | 420114.4266
12 |  | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 39056.303
13 |  | Grand Total |  |  |  |  | 459170.7296
14 |  | Grand Total (Rounded off): - |  |  |  |  | 459171

## B-7
COST SCHEDULE - B-7
INSTALLATION OF SINGLE PHASE A.B. SWITCH ON EXISTING FEEDER OUT GOING D.P. FROM 33/11 kV SUB-STATION
2015-16
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Single phase A.B. Switch with complete fitting | 7131930221 | No | 12911 | 1 | 12911
2 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 157 | 3 | 471 | Earlier- 11 kV Pin Insulator
3 | Rabbit (50 Sqmm) ACSR conductor for jumpering | 7130830057 | Mtr | 33.544 | 20 | 670.88
4 | Tee clamp for jumper | 7130830586 | No | 191 | 6 | 1146
5 | Back clamps | 7130810692 | No | 294 | 4 | 1176
6 | Binding wire and tape | 7130830006 | Kg | 139 | 0.4 | 55.6
7 | M.S. Nut- Bolts |  | Kg |  | 10
| MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 64 | 1 | 64
| MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 63 | 4 | 252
| MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 63 | 4 | 252
| MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 62 | 1 | 62
8 | SUB TOTAL-1 |  |  |  |  | 17060.48
9 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 1535.4432
10 | Labour charges as per Schedule No BL-7 |  |  |  |  | 2796.71
11 | Transportation charges |  |  |  |  | 2520.168
12 | SUB TOTAL-2 |  |  |  |  | 23912.8012
13 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 1876.6528
14 | Grand Total |  |  |  |  | 25789.454
15 | Grand Total (Rounded off): - |  |  |  |  | 25789
Note:-- All the rates are with considering price variation clause.
DELETED IN 2015-16
| 11 kV G.I. Pin | 7130820155 | Each

## B-8
COST SCHEDULE B-8
AUGMENTATION OF 33/11 kV SUB-STATION CAPACITY BY REPLACEMENT OF POWER TRANSFORMER
2015-16
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | 1.6 to 3.15 MVA |  | 3.15 to 5.0 MVA without 33 kV VCB |  | 3.15 to 5.0 MVA with 33 kV VCB
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 33/11 kV 3.15 MVA X-mer | 7132220095 | No | 2112952 | 1 | 2112952 | -- | -- | -- | --
2 | 33/11 kV 5.0 MVA X-mer | 7132220097 | No | 3010759 | -- | -- | 1 | 3010759 | 1 | 3010759
3 | 33 kV VCB (With CT's and control panel) |  | No |  | 1 |  | -- | -- | 1
| (i) 33 kV VCB (without CT's and panels) | 7131943380 | No | 226584 | 1 | 226584 |  |  | 1 | 226584
| (ii) 33 kV Control Panel | 7131960524 | No | 39815 | 1 | 39815 |  |  | 1 | 39815
| (iii) 33 kV CT's (300-150/5) Amps | 7132230263 | No | 18948 | 3 | 56844 |  |  | 3 | 56844
4 | Foundation for 33 kV VCB (1:3:6) |  | Cmt |  | -- | -- | -- | -- | 7
| (i) Cement | 7130200401 | Kg | 5.36 |  |  |  |  | 1456 | 7804.16
5 | Control cabling
a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 125.719 | 60 | 7543.14 | 60 | 7543.14 | 60 | 7543.14
b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 67.671 | 120 | 8120.52 | 120 | 8120.52 | 120 | 8120.52
c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.708 | 60 | 2382.48 | 60 | 2382.48 | 60 | 2382.48
6 | Terminal clamp for transformer | 7130830586 | No | 191 |  |  |  |  | 7 | 1337
7 | T-clamps for jumper | 7130830586 | No | 191 | -- | -- | -- | -- | 3 | 573
8 | SUB TOTAL-1 |  |  |  |  | 2454241.14 |  | 3028805.14 |  | 3361762.3
9 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 220881.7026 |  | 272592.4626 |  | 302558.607
| (i) Services on concreting |  | Cmt | 2968.461 |  | 0 |  | 0 | 7 | 20779.2269
10 | Labour charges for transformer |  |  |  |  | 132967.0719 |  | 160454.1287 |  | 160454.1287
11 | Transport charges for transformer upto 50 Kms lead |  |  |  |  | 11198.1407 |  | 20105.9356 |  | 20105.9356
12 | Labour & transport charges for VCB |  |  |  |  | 72307.1031 |  | 0 |  | 72307.1031
13 | SUB TOTAL-2 |  |  |  |  | 2891595.1584 |  | 3481957.6669 |  | 3937967.3013
14 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 269966.5254 |  | 333168.5654 |  | 369793.853
15 | (-) Cost of Old Transformer assuming 25 years of life & 5 years in service. |  |  |  |  | 584300.84 |  | 1491844.86 |  | 1491844.86
16 | Net cost of Augmentation |  |  |  |  | 2577260.8438 |  | 2323281.3723 |  | 2815916.2943
17 | Net cost of Augmentation (Rounded off) |  |  |  |  | 2577261 |  | 2323281 |  | 2815916
Note:- All the rates are with considering price variation clause.

## B-9
COST SCHEDULE B-9
INSTALLATION OF 1.6 MVA 33/11 kV SUB-STATION ON LINE
2015-16
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | CIVIL WORKS
| 1 | Land |  | Sq Mtr | LS
| 2 | Fencing for Sub-station with barbed wire. |  | RM | 396 | 32 | 12672
| 3 | Iron gate on RCC column. |  | Each | 39600 | 1 | 39600
|  | Total of 01 : - |  |  |  |  | 52272
2 |  | EQUIPMENTS AND BUS BAR ARRANGEMENT
| 1 | Power Transformer 1.6 MVA | 7132220091 | No | 841136 | 1 | 841136
| 2 | PCC supports 280 Kg; 9.0 Mtr. long | 7130800033 | No | 3129 | 2 | 6258
| 3 | 33 kV "V" cross arm | 7130810595 | No | 2332 | 2 | 4664
|  | (i) Cross arm clamp | 7130810361 | No | 282 | 2 | 564
| 4 | 33 kV Top clamp | 7130810676 | No | 388 | 5 | 1940
| 5 | 33 kV A.B. Switch | 7131930321 | Set | 18624 | 1 | 18624
| 6 | 33 kV D.O. Fuse Unit | 7131930415 | Each | 2918 | 3 | 8754
| 7 | 33 kV Polymer Lightning Arrestor | 7130840021 | Each | 3483 | 3 | 10449 | Earlier- 33 kV Lightning Arrestor
| 8 | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 388 | 9 | 3492 | Earlier- 33 kV Pin Insulator
| 9 | MS Channel 100x50 mm, 5.2 Mtr. Long for D.O., A.B. switch and LA mounting. | 7130810684 | Set | 8457 | 2 | 16914
| 10 | PCC supports 140 Kg; 8.0 Mtr. for 11 kV Bus | 7130800012 | No | 1654 | 8 | 13232
| 11 | MS Channel 5.2 Mtr. long | 7130810684 | No | 8457 | 16 | 135312
| 12 | 11 kV AB Switch complete | 7131930221 | Each | 7750 | 3 | 23250
| 13 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 425 | 3 | 1275 | Earlier- 11 kV Lightning Arrestor
| 14 | 11 kV Strain set with hardware |  | Set |  | 21
|  | 11 kV Polymer Disc insulator | 7130820010 | No | 140 | 21 | 2940 | Earlier- 11 kV Disc Insulator
|  | 11 kV Hardware | 7130820241 | No | 123 | 21 | 2583
| 15 | ACSR Conductor 80 Sqmm Al. Eq. Raccoon Conductor | 7130830060 | Mtr. | 50.002 | 20 | 1000.04
| 16 | T-clamps for Raccoon Conductor | 7130830586 | No | 191 | 27 | 5157
| 17 | Bimetallic Clamps for Transformer & auto recloser | 7130830052 | No | 534 | 12 | 6408
| 18 | M.S. Nut- Bolts |  | Kg |  | 100
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 64 | 2 | 128
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 63 | 2 | 126
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 63 | 25 | 1575
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 62 | 40 | 2480
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 62 | 50 | 3100
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 62 | 6 | 372
| 19 | M.S. Flat 50x6 mm | 7130600173 | Kg | 40.214 | 100 | 4021.4
| 20 | Earthing of Sub-station |  | LS | 20000
|  | (i) G.I. Pipe of 40 mm dia. 3.04 Mtr. long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | 7130642039 | No | 820 | 12 | 9840
|  | (ii) MS flat 50x6 mm size | 7130600173 | Kg | 40.214 | 60 | 2412.84
|  | (iii) G.I. Wire 8 SWG | 7130870043 | Kg | 55.094 | 10 | 550.94
|  | (iv) G.I. Nuts and bolts 16x40 mm | 7130620133 | Kg | 89 | 5 | 445
|  | (v) G.I. Nuts and bolts 16x65 mm | 7130620140 | Kg | 89 | 4 | 356
|  | (vi) G.I. Spring washers | 7130622922 | Kg | 127 | 1 | 127
|  | Total of 02 : - |  |  |  |  | 1129486.22
3 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 101653.7598
4 |  | Services On Earthing of sub-station. |  | No | 2117.526 | 1 | 2117.526
5 |  | Labour charges as per Schedule No BL-9 |  |  |  |  | 67276.04
6 |  | Transportation charges |  |  |  |  | 25201.6801
7 |  | SUB TOTAL-2 |  |  |  |  | 1325735.2258
8 |  | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 124243.4842
9 |  | Total cost including Civil Works. |  |  |  |  | 1502250.71
10 |  | Total Cost (Round off) : - |  |  |  |  | 1502251
Note:- All the rates are with considering price variation clause.
DELETED IN 2015-16
|  | 33 kV G.I. Pin | 7130820158 | Each