## Sample Schedule A-1
SAMPLE COST SCHEDULE A-1
1 KM OF 33 kV LINE ON PCC POLES / H-BEAMS WITH MAXIMUM SPAN OF 100 METERS USING RACCOON CONDUCTOR
2019-20
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4402.65 | 44026.5
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 53.8792 | 259859.2851
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7605.2 | 76052
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2429.24 | 24292.4 | 10 | 2429.24 | 24292.4 | 10 | 2429.24 | 24292.4
5 | Back Clamp for Cross Arm
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 10 | 300.41 | 3004.1 |  |  |  | 10 | 300.41 | 3004.1
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 10 | 333.29 | 3332.9
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 404.18 | 4041.8 | 10 | 404.18 | 4041.8 | 10 | 404.18 | 4041.8
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 118.52 | 1185.2 | 10 | 118.52 | 1185.2 | 10 | 118.52 | 1185.2
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 325.76 | 9772.8 | 30 | 325.76 | 9772.8 | 30 | 325.76 | 9772.8
9 | Raccoon ACSR Conductor (80 Sqmm, Al. Eq) with 3% sag | 7130830060 | Mtr | 3100 | 51.3096 | 159059.667 | 3100 | 51.3096 | 159059.667 | 3100 | 51.3096 | 159059.667
10 | Jointing Sleeves suitable ( for 80 Sqmm, Al. Eq. ACSR cond.) | 7130830050 | No | 6 | 37.29 | 223.74 | 6 | 37.29 | 223.74 | 6 | 37.29 | 223.74
11 | (i) Stay set 20 mm | 7130860033 | No | 3 | 829.62 | 2488.86 | 3 | 829.62 | 2488.86 | 3 | 829.62 | 2488.86
| (ii) Stay Clamp For PCC Pole | 7130810193 | No | 3 | 300.41 | 901.23 |  |  |  | 3 | 300.41 | 901.23
| (iii) Stay Clamp For "H" Beam | 7130810692 | Pair |  |  |  | 3 | 333.29 | 999.87
| (iv) Stay Wire 7/8 SWG @ 8.5 kg/ stay | 7130860076 | Kg | 25.5 | 71.9816 | 1835.5318 | 25.5 | 71.9816 | 1835.5318 | 25.5 | 71.9816 | 1835.5318
12 | Concreting of supports @ 0.6 Cmt. Per pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC; and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole. (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Material cost including GST but excluding labour.
13 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 151.45 | 212.03 | 6 | 151.45 | 908.7 | 1.4 | 151.45 | 212.03
14 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 338.4 | 507.6 | 6 | 338.4 | 2030.4 | 1.5 | 338.4 | 507.6
15 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 78.5018 | 1570.0366 | 20 | 78.5018 | 1570.0366 | 20 | 78.5018 | 1570.0366
16 | Danger Board | 7130880041 | No | 10 | 92.6 | 926 | 10 | 92.6 | 926 | 10 | 92.6 | 926
17 | Binding wire and tape | 7130830006 | Kg | 3.5 | 160.41 | 561.435 | 3.5 | 160.41 | 561.435 | 3.5 | 160.41 | 561.435
18 | M.S. Nuts and Bolts |  | Kg | 17 |  |  | 17 |  |  | 18
| 16x65 mm | 7130620614 | Kg |  | 70.4 |  | 7 | 70.4 | 492.8 |  | 70.4
| 16x90 mm | 7130620619 | Kg | 3 | 70.4 | 211.2 |  | 70.4 |  | 3.5 | 70.4 | 246.4
| 16x140 mm | 7130620625 | Kg |  | 69.2 |  | 10 | 69.2 | 692 |  | 69.2
| 16x160 mm | 7130620627 | Kg | 14 | 69.2 | 968.8 |  | 69.2 |  | 14.5 | 69.2 | 1003.4
19 | Guarding 33 kV |  | Rs |  |  | 12522.6544 |  |  | 12522.6544 |  |  | 12522.6544
| (i) G.I. Wire 6 SWG | 7130870045 | Kg | 49 | 65.0097 | 3185.4733 | 49 | 65.0097 | 3185.4733 | 49 | 65.0097 | 3185.4733
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 20 | 65.0097 | 1300.1932 | 20 | 65.0097 | 1300.1932 | 20 | 65.0097 | 1300.1932
| (iii) 33 kV guarding channel | 7130897759 | Set | 1 | 3453.23 | 3453.23 | 1 | 3453.23 | 3453.23 | 1 | 3453.23 | 3453.23
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 333.29 | 999.87 | 3 | 333.29 | 999.87 | 3 | 333.29 | 999.87
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 69.2 | 83.04 | 1.2 | 69.2 | 83.04 | 1.2 | 69.2 | 83.04
| (vi) I--Bolt Big Size | 7130620013 | No | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 829.62 | 1659.24 | 2 | 829.62 | 1659.24 | 2 | 829.62 | 1659.24
| (viii) Stay wire 7/8 SWG & 8.5 Kg/stay | 7130860076 | Kg | 17 | 71.9816 | 1223.6879 | 17 | 71.9816 | 1223.6879 | 17 | 71.9816 | 1223.6879
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 70.4 | 105.6 | 1.5 | 70.4 | 105.6 | 1.5 | 70.4 | 105.6
20 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 274251.5848 |  |  | 510556.08 |  |  | 321196.8848
21 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 232416.5973 |  |  | 432674.6441 |  |  | 272200.7499 | NEW ROW ADDED
22 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 20568.8689 |  | 0.075 | 38291.706 |  | 0.075 | 24089.7664 | Earlier name was - Incidental Charges @ 9%
23 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 389.1481 | 3891.4812 | 0 | 0 | 0 | 0 | 0 | 0
24 | Labour charges as per Schedule No.- AL-1 |  |  |  |  | 47398.72 |  |  | 55457.81 |  |  | 52789.87
25 | Labour charges for concreting |  | Cmt | 2 | 609.1748 | 1218.3496 | 8 | 609.1748 | 4873.3984 | 7 | 609.1748 | 4264.2236
26 | Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 13635.8014 |  |  | 13635.8014 |  |  | 13635.8014
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 20, 22, 23, 24, 25, 26 |  |  |  |  | 45120.6007 |  |  | 77851.8495 |  |  | 51997.0683
28 | Total Estimated Cost excluding GST (Row 21, 22, 23, 24, 25, 26, 27) |  |  |  |  | 364250.4191 |  |  | 622785.2092 |  |  | 418977.4794
29 | Applicable CGST @ 9% on Row 28 |  |  |  | 0.09 | 32782.5377 |  | 0.09 | 56050.6688 |  | 0.09 | 37707.9731
30 | Applicable SGST @ 9% on Row 28 |  |  |  | 0.09 | 32782.5377 |  | 0.09 | 56050.6688 |  | 0.09 | 37707.9731
31 | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 429815.4945 |  |  | 734886.5469 |  |  | 494393.4257
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 429815 |  |  | 734887 |  |  | 494393
Note:-
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on B46: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on F48: Barun Chakraborty: Earlier - 0.09
Note on I48: Barun Chakraborty: Earlier - 0.09
Note on L48: Barun Chakraborty: Earlier - 0.09