## Sheet1 (hidden)
COMPARATIVE STATEMENT OF RATES FROM YEAR 2016-17 to 2017-18
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2016-17 | 2017-18 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
PART-I, 33 kV LINES AND D.P. STRUCTURES
(A) |  | 33 kV line on PCC Pole / H-Beam poles with Raccoon conductor.
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-1(i) | Per Km | 290208 | 294651 | 1.531
| ii | On H-Beam 152 x 152 mm 37.1 Kg/ Mtr 13 Mtr long | A-1(ii) | Per Km | 459820 | 457540 | -0.49585
| iii | On 365 Kg 11 Mtrs long PCC poles | A-1(iii) | Per Km | 332390 | 327410 | -1.4982
(B) |  | 33 kV Four Pole structure on PCC / H-Beam Pole | A-2 (A)
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-2 (A) (i) | Each | 234974 | 229401 | -2.3718
| ii | H-Beam Pole | A-2 (A) (ii) | Each | 292201 | 287977 | -1.4456
(C) |  | 33 kV DP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-2 (B)(i) | Each | 57588 | 54683 | -5.0445
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-2 (B)(ii) | Each | 88088 | 86977 | -1.2612
| iii | On 365 Kg 11 Mtrs long PCC poles | A-2 (B)(iii) | Each | 62662 | 61014 | -2.63
(D) |  | 33 kV line on PCC Pole / H-Beam Pole with Dog conductor.
| i | On 280 Kg, 9.1 Mtrs long PCC poles | A-3(i) | Per Km | 335828 | 346806 | 3.2689
| ii | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3(ii) | Per Km | 507332 | 509694 | 0.46557
| iii | On 365 Kg 11 Mtrs long PCC poles | A-3(iii) | Each | 378854 | 378457 | -0.10479
(E) |  | Augmentation of 1 km. of 33 kV line from Raccoon to Dog conductor. | A-3 (A) | Per Km | 217937 | 223794 | 2.6875
(F) |  | Additional (Mid Span) Pole for 33 kV Line | A-3 (B)
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3 (B)(i) | Per No. | 28510 | 28207 | -1.0628
(G) |  | 33 kV line on H-Beam supports suspension type with Panther Conductor (Maximum span of 50 Mtrs) | A-4
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-4 (i) | Per Km | 1418591 | 1401138 | -1.2303
(H) |  | 33 kV DP Structure on H-Beam supports with Panther Conductor | A-5
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-5 (i) | Each | 102479 | 101776 | -0.68599
(I) |  | 33 kV Under ground cable crossing under existing Railway track / Road for 60 Mtr long Corridor / route length of HDPE pipe under 2.5 M. deep for ground level single feeder line | A-6 | 60 Mtr
| a | Using HDD Technique
| i | With 3 core U/G XLPE 240 sqmm Cable | A-6(i) | 60 Mtr | 1036752 | 1078165 | 3.9945
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-6(ii) | 60 Mtr | 1158328 | 1200627 | 3.6517
| b | Using Pipe Pushing Method.
| i | With 3 core U/G XLPE 240 sqmm Cable | A-6(iii) | 60 Mtr | 2526667 | 2655984 | 5.1181
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-6(iv) | 60 Mtr | 2648242 | 2778446 | 4.9166
(J) |  | 33 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level single feeder line | A-6 (A) | 50 Mtr | 621183 | 622997 | 0.29202
(K) |  | Last span cabling of 33 kV H.T. Connection
|  | Using H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-7
| i | With 3x185 sq.mm AB XLPE Cable | A-7(i) | 50 Mtr | 181872 | 186985 | 2.8113
| ii | With 3x240 sq.mm AB XLPE Cable | A-7(ii) | 50 Mtr | 204432 | 209751 | 2.6018
(L) |  | 33 kV MEDP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-8 (i) | Each | 81715 | 79259 | -3.0056
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-8 (ii) | Each | 106547 | 106353 | -0.18208
(M) |  | Last span cabling of 33 kV line using Covered Conductor of size
| i | 70 sq.mm (207 Amp) | A-9 (i) | 50 Mtr | 124984 | 129377 | 3.5148
| ii | 99 sq.mm (258 Amp) | A-9 (ii) | 50 Mtr | 129998 | 134391 | 3.3793
(N) |  | Schedule for 33 kV Underground Cable crossing under Railway Track / Road for 60 Mtr. Long Corridor / Route Length of HDPE Pipe, under 2.5 Mtr. Deep from Ground Level Single Feeder Line Using Open Trench Method. | A-10 (i)
| i | With 3 core U/G XLPE 240 sqmm Cable | A-10(i) | 60 Mtr | 906066.3082 | 939768 | 3.7196
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-10(ii) | 60 Mtr | 1027642.0326 | 1062230 | 3.3658
Part-II, 33/11 kV SUB-STATIONS
(A) |  | New Sub-stations:
| i | 1.6 MVA, 33/11 kV S/s expandable to 2 x 1.6 MVA with control room | B-1(i) | Each | 6866103 | 6913029 | 0.68344
| ii | 3.15 MVA, 33/11 kV S/s expandable to 2 x 3.15 MVA with control room | B-1(ii) | Each | 8595749 | 8571098 | -0.28678
| iii | 5 MVA, 33/11 kV S/s expandable to 2 x 5 MVA with control room | B-1(iii) | Each | 10290155 | 10257514 | -0.31721
(B) |  | 33/11 kV Power Transformer
| i | 1.6 MVA | B-2(i) | Each | 933187 | 892025 | -4.4109
| ii | 3.15 MVA | B-2(ii) | Each | 2283793 | 2177129 | -4.6705
| iii | 5.0 MVA | B-2(iii) | Each | 3239383 | 3100279 | -4.2942
(C) |  | Installation of additional transformer for parallel operation with one additional bay on 11 kV side
| i | 1.6 MVA | B-3(i) | Each | 2893992 | 3379693 | 16.7831
| ii | 3.15 MVA | B-3(ii) | Each | 4572396 | 4999595 | 9.343
| iii | 5.0 MVA | B-3(iii) | Each | 5527838 | 5922555 | 7.1405
(D) |  | 11 kV Out door yard extension for additional bay with circuit breaker. | B-4 | Each | 483256 | 490515 | 1.5021
(E) |  | 33 kV Out door yard extension for additional bay without circuit breaker. | B-5 | Each | 212243 | 214257 | 0.94891
(F) |  | Installation of 33 kV VCB | B-6 | Each | 417910 | 418353 | 0.106
(G) |  | Augmentation of Power Transformer
| i | 1.6 to 3.15 MVA | B-8(i) | Each | 2660176 | 2562548 | -3.67
| ii | 3.15 to 5.0 MVA without 33 kV VCB | B-8(ii) | Each | 3251545 | 3113230 | -4.2538
| iii | 3.15 to 5.0 MVA with 33 kV VCB | B-8(iii) | Each | 3642023 | 3503832 | -3.7943
H) |  | Installation of 1.6 MVA 33/11 kV Sub-Station ON LINE | B-9 | Each | 1265650 | 1232202 | -2.6428
PART-III, 11 kV LINES AND D.P.STRUCTURES
(A) |  | 11 kV line on 140 Kg 8.0 Mtr long PCC poles with
| i | Rabbit conductor | C-1(I) | Per Km | 225086 | 224725 | -0.16038
| ii | Weasel conductor | C-1(II) | Per Km | 182425 | 183048 | 0.34151
(B) |  | 11 kV DP structure on 140 Kg, 8.0 Mtr long PCC poles | C-2 | Each | 35616 | 34966 | -1.825
PART-IV, 11 kV LINES AND D.P.STRUCTURES ON RAIL & H-BEAM
(A) |  | 11 kV line on H-Beam / PCC Pole with Rabbit conductor
| i | On H-Beam 11 meter long | C-3(i) | Per Km | 400368 | 394185 | -1.5443
| ii | On 365 Kg 11 Mtrs long PCC poles | C-3(ii) | Per Km | 284712 | 275498 | -3.2363
(B) | ii | Additional (Mid span) Poles for 11 kV Line on H-Beam | C-3 (A) | Per No. | 22159 | 21448 | -3.2086
(C) | iii | 11 kV Line on A.B.Cable | C-3 (B)
| a | Using H-Beam 152x152 mm, 37.1Kg/mtr 11 Mtrs long supports.
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[i] | Per Km | 1200223 | 1191557 | -0.72203
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[ii] | Per Km | 1335256 | 1328211 | -0.52761
| b | Using 200 Kg; 9.0 Mtr long PCC Pole
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[iii] | Per Km | 748914 | 772395 | 3.1353
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[iv] | Per Km | 883946 | 909049 | 2.8399
(D) | iv | Augmentation of 11 kV Line from Weasel to Raccoon Conductor | C-3 (C) | Per Km | 161933 | 165350 | 2.1101
(E) | v | Augmentation of 11 kV Line from Weasel to Rabbit Conductor | C-3 (D) | Per Km | 115754 | 118860 | 2.6833
(F) | vi | 11 kV Overhead XLPE Cable Line on H-Beam Pole with average span 30 Mtrs. | C-3 (E) | Per Km | 2396943 | 2430693 | 1.408
(G) |  | 11 kV DP structure on
| i | H-Beam 11 meter long | C-4(i) | Each | 67035 | 65741 | -1.9303
| ii | On 365 Kg 11 Mtrs long PCC poles | C-4(ii) | Each | 47583 | 45755 | -3.8417
(H) |  | 11 kV line on RS Joist (175X85 mm) 11.0 Meters long with
| i | Rabbit conductor | C-5(I) | Per Km | 300939 | 300432 | -0.16847
| ii | Weasel conductor | C-5(II) | Per Km | 260829 | 261456 | 0.24039
(I) |  | 11 kV DP structure on RS Joist 175X85 mm 11.0 Mtr. long | C-6 | Each | 50509 | 49946 | -1.1147
(J) |  | 11 kV line on PCC pole
| a | On 365 Kg 11 Mtrs long PCC poles
| i | Using Raccoon conductor | C-8(I) | Per Km | 327385 | 318489 | -2.7173
| ii | Using Dog conductor | C-8(II) | Per Km | 371815 | 366833 | -1.3399
(K) |  | 11 kV line on H-Beam (152x152 mm) 13 meter long with
| i | Raccoon conductor | C-9(I) | Per Km | 474359 | 468479 | -1.2396
| ii | Dog conductor | C-9(II) | Per Km | 518789 | 516824 | -0.37877
(L) |  | Additional (Mid Span) Poles for new 11 kV Line with Raccoon Conductor | C-9(A) | Per No. | 24793 | 24082 | -2.8677
(M) |  | 11 kV under ground cable crossing under railway track for 60 mtr length, under 2.5 mtr deep for ground level | C-12
| i | Using HDD Technique | C-12 (i) | 60 Mtr | 781977 | 819848 | 4.843
| ii | Using Pipe Pushing Method. | C-12 (ii) | 60 Mtr | 2271892 | 2397667 | 5.5361
(N) |  | 11 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level | C-12 (A) | 50 Mtr | 333362 | 334544 | 0.35457
(O) |  | Laying of 1 Km 11 kV Line using
| i | 3 Core 95 Sqmm underground cable | C-15(I) | Per Km | 926447 | 1061168 | 14.5417
| ii | 3 Core 240 Sqmm underground cable | C-15(II) | Per Km | 1407717 | 1555528 | 10.5001
| iii | 3 Core 400 Sqmm underground cable | C-15(III) | Per Km | 1982562 | 2146102 | 8.2489
(P) |  | D.T. Capacitors on existing DTR's (Retained & shifted) | C-16
| i | LT Capacitor for 25 kVA DT | C-16 (i) | Per No. | 1984 | 1984 | 0
| ii | LT Capacitor for 63 kVA DT | C-16 (ii) | Per No. | 3766 | 3766 | 0
| iii | LT Capacitor for 100 kVA DT | C-16 (iii) | Per No. | 4486 | 4486 | 0
| iv | LT Capacitor for 200 kVA DT | C-16 (iv) | Per No. | 4486 | 4486 | 0
| v | LT Capacitor for 315 kVA DT | C-16 (v) | Per No. | 4486 | 4486 | 0
(Q) |  | 11 kV MEDP Structure on H-Beam Pole
| i | 37.1 Kg /Mtrs 11 Mtrs long H-Beam supports | C-17 (i) | Each | 73838 | 72854 | -1.3326
(R) |  | New Automated 11 kV Capacitor Bank at 33/11 kV Sub-stations
| i | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. | C-18 (i) | Each | 1051129 | 1124599 | 6.9896
| ii | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . | C-18 (ii) | Each | 872674 | 946173 | 8.4223
(S) |  | Schedule for installation of compact R.M.U. 11 kV Class SF6 / VCB type (1 Incoming + 2 Breaker + 1 Outgoing) | C-19 | Each | 1166351 | 1166226 | -0.010717
(T) |  | Schedule for Chemical Earthing of Metering Equipment installed in the premises of HT consumers in normal / hard rock soil. | C-20 | Each | 12140 | 12854 | 5.8814
PART-V, 11/0.4 kV Transformer S/s.
A (A-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(I) | Each | 119446 | 113690 | -4.8189
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(II) | Each | 172454 | 169813 | -1.5314
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(III) | Each | 251071 | 241686 | -3.738
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(IV) | Each | 378952 | 373318 | -1.4867
(B-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(I) | Each | 143836 | 137866 | -4.1506
| ii | 63 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(II) | Each | 196844 | 193989 | -1.4504
| iii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11mtr long | C-7(B-1)(III) | Each | 250890 | 241328 | -3.8112
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(IV) | Each | 379297 | 373557 | -1.5133
(B-1) A |  | Relocation of 11/0.4 kV Out-door type Transformer Sub-station using H-Beam Pole and 3.5 Core PVC Cable [Based on Cost Schedule C-7 (B-1) except X-mer Cost]
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (I) | Each | 89146 | 86714 | -2.7281
| ii | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (II) | Each | 105263 | 103139 | -2.0178
| iii | 100 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (III) | Each | 123707 | 121207 | -2.0209
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr,11 mtr long | C-7(B-1) A (IV) | Each | 156292 | 153161 | -2.0033
(B-1) B |  | Renovation of Existing Distribution Transformer
| i | 25 kVA Transformer | C-7(B-1) B (I) | Each | 19827 | 22140 | 11.6659
| ii | 63 kVA Transformer | C-7(B-1) B (II) | Each | 35897 | 38302 | 6.6997
| iii | 100 kVA Transformer | C-7(B-1) B (III) | Each | 45084 | 47174 | 4.6358
| iv | 200 kVA Transformer | C-7(B-1) B (IV) | Each | 76498 | 77886 | 1.8144
| v | 315 kVA Transformer | C-7(B-1) B (V) | Each | 88994 | 90321 | 1.4911
(A-2) |  | 11/0.4 kV Out-door type Transformer sub-station using 1 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(I) | Each | 119679 | 113817 | -4.8981
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(II) | Each | 172408 | 169440 | -1.7215
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(III) | Each | 249131 | 240586 | -3.4299
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(IV) | Each | 368657 | 364826 | -1.0392
(B-2) | v | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(I) | Each | 144069 | 137992 | -4.2181
| vi | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(II) | Each | 196797 | 193616 | -1.6164
| vii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(III) | Each | 249394 | 240227 | -3.6757
| viii | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(IV) | Each | 369446 | 365065 | -1.1858
(B) |  | Augmentation of 11/.4 kV S/s capacity (Assuming 25 years of life & 10 years in service)
| i | 25 kVA to 63 kVA | C-10 (I) | Each | 130670 | 132602 | 1.4785
| ii | 63 kVA to 100 kVA | C-10 (II) | Each | 209641 | 208698 | -0.44982
| iii | 100 kVA to 200 kVA | C-10 (III) | Each | 339624 | 342792 | 0.9328
(C) | i | 11/.4 kV Out door Sub-station (16 kVA Transformer) | C-11 | Each | 115010 | 112364 | -2.3007
(D) |  | Single pole mounted low capacity Single phase / Three phase 11/.4 kV Distribution Transformer Sub-station
| i | 16 kVA Three phase | C-13(III) | Each | 92936 | 93434 | 0.53585
(E) |  | Plinth mounted 11/.4 kV Outdoor Sub-station
| i | 63 kVA Transformer | C-14(I) | Each | 223352 | 211937 | -5.1108
| ii | 100 kVA Transformer | C-14(II) | Each | 277122 | 258939 | -6.5614
| iii | 200 kVA Transformer | C-14(III) | Each | 427457 | 412870 | -3.4125
PART-VI, L.T. LINES
(A) |  | 3 phase, 5 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 4 Rabbit + 1 Squirrel | D-1(I) | Per Km | 265563 | 268958 | 1.2784
| ii | 3 Rabbit + 2 Squirrel | D-1(II) | Per Km | 245947 | 250089 | 1.6841
| iii | 4 Weasel + 1 Squirrel | D-1(III) | Per Km | 213106 | 218059 | 2.3242
| iv | 3 Weasel + 2 Squirrel | D-1(IV) | Per Km | 206605 | 211915 | 2.5701
| v | 5 Squirrel | D-1(V) | Per Km | 187100 | 193485 | 3.4126
(B) |  | 3 phase, 4 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 3 Rabbit + 1 Squirrel | D-2(I) | Per Km | 228470 | 231205 | 1.1971
| ii | 3 Weasel + 1 Squirrel | D-2(II) | Per Km | 189127 | 193031 | 2.0642
| iii | 4 Squirrel | D-2(III) | Per Km | 169622 | 174601 | 2.9354
(C) |  | 1 phase, 3 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-3(I) | Per Km | 177557 | 179745 | 1.2323
| ii | 2 Weasel + 1 Squirrel | D-3(II) | Per Km | 164442 | 167020 | 1.5677
| iii | 3 Squirrel | D-3(III) | Per Km | 151439 | 154733 | 2.1751
(D) |  | 3 Phase, 5 Wire LT line on 125 x 70 mm, 9.3 Mtrs long R.S. Joist with 3 Rabbit & 2 Weasel conductors (Span upto 45 Meters) | D-4(I) | Per Km | 362955 | 360452 | -0.68962
(E) |  | 3 Phase, 5 Wire LT line on 175 x 85 mm, 9.3 Mtrs long R.S. Joist with 3 Raccoon & 2 Weasel conductors (Span upto 65 Meters) | D-4(II) | Per Km | 395690 | 395890 | 0.050545
(F) |  | 1 Phase, 3 Wire LT line on 9.3 Mtrs long 125x70 mm R.S. Joist with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-5(I) | Per Km | 261626 | 254915 | -2.5651
| ii | 2 Weasel + 1 Squirrel | D-5(II) | Per Km | 248512 | 242190 | -2.5439
| iii | 3 Squirrel | D-5(III) | Per Km | 235509 | 229904 | -2.38
(G) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (i) | Per Km | 339492 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (ii) | Per Km | 273723 | 264172 | -3.4893
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (iii) | Per Km | 461479 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (iv) | Per Km | 395711 | 387798 | -1.9997
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (v) | Per Km | 589306 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (vi) | Per Km | 523537 | 510840 | -2.4252
(H ) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (i) | Per Km | 433821 | 369101 | -14.9186 | Cable rate reduced by 23%
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| ii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (ii) | Per Km | 556663 | 493582 | -11.332
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| iii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (iii) | Per Km | 684490 | 616623 | -9.915
(I) |  | 1 phase 3 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x25+1x16+1x25 sq.mm. | D-6 [3] | Per Km | 245263 | 239794 | -2.2299
(J) |  | 3 phase 4 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 3x16+1x25 sq.mm. | D-6 [4] | Per Km | 280146 | 274079 | -2.1657
(K) |  | 3 phase 5 Wire L.T. Line on R.S.Joist (175x85) mm, 9.3 Mtr. Long (By replacement of existing bare LT conductor) for Urban area using AB XLPE Cable of size
| i | 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6(A) (i) | Per Km | 273057 | DELETED
(L) |  | Additional pole of R.S. Joist (125x70) mm (Mid span) for L.T.Line with A.B.Cable. | D-6(B) | Per No. | 9780 | 9209 | -5.8384
(M) |  | HVDS system of 200 kVA parent DTR taking 4 KM LT to be converted | D-7 | 4 Km | 1917922 | 1945906 | 1.4591
(N) |  | HVDS system of 100 kVA parent DTR taking 3 KM LT to be converted | D-8 | 3Km | 960861 | 935426 | -2.6471
(O) |  | HVDS system of 63 kVA parent DTR taking 2 KM LT to be converted | D-9 | 2Km | 692611 | 676802 | -2.2825
(P) |  | Conversion of 1 Km LT line into 11 kV line | D-10 | Per Km | 78149 | 76543 | -2.055
(Q) |  | LT line conversion using Rabbit conductor maximum span of 45 mtrs
| i | 1 phase 2 wire to 1 phase 3 wire conversion | D-11(I) |  | 66251 | 68984 | 4.1252
| ii | 1 phase 2 wire to 3 phase 4 wire conversion | D-11(II) |  | 106799 | 110491 | 3.457
| iii | 1 phase 3 wire to 3 phase 4 wire conversion | D-11(III) |  | 68889 | 71635 | 3.9861
| iv | 1 phase 3 wire to 3 phase 5 wire conversion | D-11(IV) |  | 109350 | 113054 | 3.3873
(R) |  | Conversion of 1 Km 1 Phase 3 wire LT line into 11 kV line | D-12 | Per Km | 194760 | 197052 | 1.1768
(S) |  | Conversion of 1 Km 3 Phase 5 wire LT line into 11 kV line | D-13 | Per Km | 220985 | 223565 | 1.1675
(T) |  | Distribution Box on existing LT Lines for Service Connections.
| i | Single phase Distn. Box for 09 Connections | D-14 (i) | Per No. | 1350 | 1091 | -19.1852
| ii | Three phase Distn. Box for 05 Connections | D-14 (ii) | Per No. | 1577 | 1295 | -17.8821
(U) |  | 1 phase 2 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x16+1x25 sq.mm. | D-15 | Per Km | 253584 | DELETED
PART-VII, METERING
(A) |  | Metering of 11/0.4 kV Distribution X'mer
| i | 25 kVA Transformer | E-1(I) | Each | 8957 | 9574 | 6.8885
| ii | 63 kVA Transformer | E-1(II) | Each | 8957 | 9574 | 6.8885
| iii | 100 kVA Transformer | E-1(III) | Each | 8957 | 9574 | 6.8885
| iv | 200 kVA Transformer | E-1(IV) | Each | 8678 | 9282 | 6.9601
Meter modernisation- Replacing the existing meters with electronic meters which are highly capable of improving billing efficiency.
(B) | i | Cost of meter replacement of single phase consumer along with shifting of meter outside the premises. | E-2 | Each
| i | With Armoured service cable | E-2(i) | Each | 2629 | 2653 | 0.91289
| ii | With Unarmoured service cable | E-2(ii) | Each | 2335 | 2359 | 1.0278
(C) | ii | Cost of meter replacement of three phase consumer along with shifting of meter outside the premises. | E-3 | Each
| i | With Armoured service cable | E-3(i) | Each | 4947 | 5011 | 1.2937
| ii | With Unarmoured service cable | E-3(ii) | Each | 4718 | 4782 | 1.3565
(D) | iii | Cost of meter replacement of three phase consumer CT Operated meter along with shifting of meter outside the premises. | E-4 | Each | 2600 | 2618 | 0.69231
(E) | iv | Meter shifting of Single phase consumer to outside of premises with New Service Cable. | E-5 | Each
| i | With Armoured service cable | E-5(i) | Each | 1649 | 1673 | 1.4554
| ii | With Unarmoured service cable | E-5(ii) | Each | 1355 | 1379 | 1.7712
(F) | v | Meter shifting of Three phase consumer to outside of premises with New Service Cable. | E-6 | Each
| i | With Armoured service cable | E-6(i) | Each | 2767 | 2831 | 2.313
| ii | With Unarmoured service cable | E-6(ii) | Each | 2538 | 2602 | 2.5217
[5 empty] | Total Hike in % |  | 0.1

## SOR RATE
RATE OF STOCK MATERIALS IN SoR OF 2018-19
| RATE OF ALL MATERIALS AR INCLUSIVE OF G.S.T. UNLESS MENTIONED SPECIFICALLY IN REMARKS COLUMN | [5 empty] | Updated SoR 2017-18 | Value
Material Code | Description | Unit | Unit rate for 2018-19 | SAP DESCRIPTION | REMARKS |  | Material Code | Value
7130200201 | 1:1.5:3 Ratio | Cmt | 3298 |  |  | Earlier Total cost consisted of material and labour as a whole, now only material cost (excluding labour & G.S.T.) is taken.
7130200202 | 1:3:6 Ratio | Cmt | 2510.8 |  | * | Earlier Total cost consisted of material and labour as a whole, now only material cost (excluding labour & G.S.T.) is taken.
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 176.87 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 240.64 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Each | 33
7130210809 | Aluminium Paint | Ltr. | 327.94 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 251.07
7130211158 | Red Oxide Paint | Ltr. | 146.77 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 155833.08 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5 | ISI MARK
7130310007 | 70 Sqmm. | Km. | 50410.97 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V | ISI MARK
7130310008 | 120 Sqmm. | Km. | 90389.05 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100 | ISI MARK
7130310020 | 3x400 Sq.mm. | km | 2150624.22 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 28156.59 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V | ISI MARK
7130310022 | 50 Sqmm. | Km. | 36754.4 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V | ISI MARK
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 70032.16 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM | ISI MARK
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 76711.73 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM | ISI MARK
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 88905.8 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM | ISI MARK
7130310038 | 2.5 Sqmm. | Per Mtr. | 6.89 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 29.08 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 60.26 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 102715.58 | 11KV PVC INSULATED 150SQMM SINGLE CORE X | ISI MARK
7130310042 | 16.0 Sqmm. | km | 39339.51 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 55892.5 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310048 | 25 Sq.mm. | Mtr. | 88826.17
7130310049 | 120 Sq.mm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310050 | 400 Sqmm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310051 | 3x95 Sq.mm. | km | 920903.65 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1130461.76
7130310053 | 3x185 Sq.mm. | km | 1292072.61 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 1643003.83 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 17826.52
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 25466.45
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 314067.63 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 444325.88
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 664391.87
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 626686.74
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 3890.71 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 4094.35 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 41184.18 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 112761 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM | ISI MARK
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 123896.74 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 50684.56 | LT AB CABLEB 3X16+1X25 SQMM | ISI MARK
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 57407.11 | LT AB CABLEB 3X25+1X25 SQMM | ISI MARK
7130310075 | 3x240 Sq.mm. | km | 1967969.25 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 525190.66
7130310077 | 95 Sq.mm | km | 531363.19 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 792369.6 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 960042.67 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 1479179.02 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310652 | 2 Core (UNARMOURED) | Km. | 36259.28 | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310654 | 4 Core (UNARMOURED) | Km. | 62758.54 | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310658 | 8 Core (UNARMOURED) | Km. | 119188.38 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310681 | 10 Core (UNARMOURED) | Km. | 148732.16 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC |  | BIN CODE Changed. Old Bin 7130310660
7130310660 | 10 Core (ARMOURED) | Km. | 205733.24 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 161612.87 | CONTROL CABLE COP 12 CORE 2.5 SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 18174.64 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 42707.22 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 57599 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 110492.79 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 215644.03 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 267750.7 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC |  | ITEM DELETED: NOT TO BE USED
7130311057 | 150 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV |  | ITEM DELETED: NOT TO BE USED
7130311061 | 300 Sqmm. | km |  | Power Cable ARM ALU 3.5CORE 300/150SQMM |  | ITEM DELETED: NOT TO BE USED
7130311084 | 16.0 Sqmm. | km | 58813.87 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 10186.59
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 12733.23 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 15279.87 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 17826.52 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 19099.85
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 22919.81
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 801.73 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 866.03
7130320045 | Cable tie for AB Cable | Each | 25.72
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | Set | 3863.4 | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 2464.11 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 2595.95
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 5.38 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 34129.38 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 826.38
7130352031 | 16 Sq.mm, 4 Core | Set | 826.38 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 887.47
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1247.6
7130352034 | 150 Sq.mm, 3.5 Core | Set | 1859.61
7130352035 | 300 Sq.mm, 3.5 Core | Set | 3005.39
7130352036 | 400 Sq.mm, 3.5 Core | Set | 3840.33
7130352037 | End terminating jointing kit upto 240 sqmm XLPE cable | Set | 23009.06 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x50 Sq.mm | Set | 13753.61
7130352039 | 3x95 Sq.mm | Set | 13753.61 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 18210.23 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 19916.04 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 19916.04 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 7149.38 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 8630.52 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 8878.79 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box (with 10 No. connectors) | No. | 3036.33 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 2.17 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 2.17 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 4.34
7130354277 | 32 Sq mm | Nos. | 5.42
7130354278 | 50 Sq mm | Nos. | 8.69 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 13.03 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 16.29 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 22.81 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 26.06 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 41.26
7130354284 | 225 Sq mm | Nos. | 46.69
7130354285 | 240 Sq mm | Nos. | 67.32
7130354286 | 300 Sq mm | Nos. | 79.27 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 102.07
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 661.1 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 84.3 | INSULATING PIERCING CONNECTOR AB CABLE(S
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 109.82 | INSULATING PIERCING CONNECTOR FOR AB CAB
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 153.07 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 119.8 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 169.29 | STRAIGHT THROUGH JOINT
7130390019 | End cap for 50/70 Sq.mm | Nos. | 28.93 | END CLAMP CAP FOR 50/70 SQMM
7130600023 | 50 x 50 x 6 mm | MT | 41788.76 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 41788.76 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 41788.76 | M S ANGLE 75X75X6 MM
7130600166 | 75x40 mm | MT | 41788.76 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 45476.44 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 41788.76 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 45476.44 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT | 39505.14 | R.S.JOIST 125 x 70 mm
7130600675 | 175 x 85 mm | MT | 44915.52 | R S JOIST 175X85 MM | ISI MARK
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 50674.4 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 50674.4 | RAIL 60 KG PER METER
7130601958 | 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 46403.88 | H BEAMS 152X152MM; 37.1 KG/MTR. | ISI MARK
7130601965 | 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 46403.88 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR | ISI MARK
7130610206 | Barbed wire | MT | 76075.03 | G.I. WIRES: - Barbed wire.
7130620013 | I-Bolt (big size) | No | 124.12 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 69.38
7130620133 | 16x40 mm | Kg | 95.97 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 95.97 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 69.38 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 70.53 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 70.53 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 69.38 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 68.22 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 68.22 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 67.06 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 67.06 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt | No | 415.5 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 149.07 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | RM | 1079.16 | G.I. PIPE 200MM FOR 400MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 935.03 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 3618.29 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | Caping of RCC Pipe on both end of pipe with Concreting and Bricks work | Cmt | 3618.67 |  |  | NEW BIN CODE ALLOTED
7130640031 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 600 mm | Each | 2617 |  |  | BIN CODE Changed. Old Bin 7130640030
7130640036 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 900 mm | Each | 5032 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG)
7130640037 | M.S.Pipe 200 mm dia with collars | RM (medium) | 1326.73 |  |  | NEW BIN CODE ALLOTED
7130640038 | M.S.Pipe 200 mm dia with collars | RM (light) | 1036.11 | M.S. PIPE 200 MM DIA WITH COLLARS |  | BIN CODE Changed. Old Bin 7130640037
7130640171 | G.I. Bend 40 mm | Each | 104.16 |  |  | NEW BIN CODE ALLOTED
7130641396 | Gl Pipe 40 mm | Per Mtr | 215.22 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | No | 849.08 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 4315.55 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing (TATA Make) 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. T&D/DRG/MISC/2 Revision -2 | RM | 2024.88
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 133.7333
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 590.97 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 428.94 | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 2255.2 | PCC POLE 140 KG; 8,0 MTR LONG
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 280 Kg; 9.1 Mtr long | Each | 4402.65 | PCC POLE 280 KG; 9,1 MTR LONG
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each |  | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT |  | ITEM DELETED: NOT TO BE USED
7130800672 | 350 Kg; 7.0 Mtr long | Each |  | PCC POLE 350 KG; 7,0 MTR LONG |  | ITEM DELETED: NOT TO BE USED
7130810005 | Through Bolt | No | 87.31 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr 100 x 50 mm. | Set | 6872.65 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810026 | Stay clamp for 140 kG PCC Pole | Pair | 155.99 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 291.13 | Stay clamp LT/Pair
7130810060 | LT U CLAMP | No. | 78 | LT U CLAMP
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 70.96 | Strain Plate
7130810077 | Pole Clamp | No. | 433.92 | POLE CLAMP
7130810102 | Service Ring | No. | 344.82 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 291.13 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 309.8 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 309.8 | HT STAY CLAMP R S JOIST A TYPE
7130810251 | Stay Clamp Rail "B" type | Pair | 309.8 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 309.8 | 33 KV TOP CLAMP SEMIFINISHED
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 623.86 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 742.99 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 862.11 | LT FIVE PIN CROSS ARM
7130810495 | 11 kV Cross Arm Cleat type | No. | 1057.95 | 11 KV V CROSS ARM
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 1676.77 | D.O. / LA Mounting channel 75x40 mm.
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2508.6 | 1.1 MTR DPDC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 3977.41 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 2889.17 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 4060.2 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 4590.18 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 2354.14 | 33 KV V CROSS ARM
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 5428.06 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 93.9 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 391.69 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 296.79 | 11 kV top clamp
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 3257.64 | 11 kV Cut point channel paint
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 8537.3 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 322.98 | Stay clamp for 'H' Beam
7130820008 | 11 kV Pin insulator with Pin | Each | 142.14 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 351.44 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 128.45 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 236.53 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 4.05 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 448.04 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 1832.27 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 32.16
7130820030 | Disc insulator | Each | 215.81 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 43.03 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 217.7 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 11.31 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 12.82 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 10.78 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 71.32 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 237.31 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 35.61 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 35.7 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 40.64 | HARDWARE FOR 75X90 MM LT SHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 119.62 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 248.51 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2129.35 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 155.45 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km |  | CONDUCTOR AAA SQURREL |  | ITEM DELETED: NOT TO BE USED
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km |  | CONDUCTOR AAA WEASEL |  | ITEM DELETED: NOT TO BE USED
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km |  | CONDUCTOR AAA RABBIT |  | ITEM DELETED: NOT TO BE USED
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km |  | CONDUCTOR AAA RACOON |  | ITEM DELETED: NOT TO BE USED
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 36.14 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 141.07 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 650.6
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 14066.3 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq) | ISI MARK
7130830054 | Bimetallic clamp for VCB | Each | 379.95
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 20604.63 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq) | ISI MARK
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 379.95
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 33948.58 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q) | ISI MARK
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 193.15
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 50185.79 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E | ISI MARK
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 66185.04 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq) | ISI MARK
7130830070 | 0.2 Sq inch ( 130 Sqmm Al.Eq.)(Panther) | Km | 147387.66 | CONDUCTOR ACSR PANTHER 130 sq mm | ISI MARK
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km |  | CONDUCTOR AAA DOG |  | ITEM DELETED: NOT TO BE USED
7130830585 | T-Clamp for Dog Conductor. | Each | 266.98 | T-CLAMPS FOR ACSR CONDUCTOR Dog Condutor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 213.35 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830586 | T-Clamp for Panther Conductor. | Each | 312.45 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 283.36 | Bimetallic clamps for transformer & kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 29.14 | SLEEVE JOINTING ALUMINIUM FOR 0.03 SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 218.02 | SLEEVE REPAIR ALUMINIUM FOR .2 SQ INCH AC
7130840021 | 33 kV Polymer Lightning Arrestor | Each | 4545.92 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 504.66 | LIGHTNING ARRESTORS 11 KV gapless type.
7130850198 | GI Structure for complete Equipment | Kg | 82.25 |  |  | NEW BIN CODE ALLOTED
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 4590.18 | Transformer mounting 100 x 50 mm channel
7130850201 | Transformer Mounting with Belting for Addl. X-Arm | No. | 4434.72 | Transformer mounting 100 x 50 mm channel
7130860017 | I-Bolt - 16 mm | No. | 105.19 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 441.23 | STAY SET WITHOUT STAY WIRE 16 mm Paint 11 KV
7130860033 | Stay Set 20 mm (Painted) | Each | 803.97 | STAY SET WITHOUT STAY WIRE 20 mm (Painted)
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 69756.41 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 70439.64 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 764.89
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 114.85 | EARTHING COIL 8SWG GI WIRE 50 MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 358.38 | Earthing rod 25mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 63044.96 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 62999.96 | G.I. WIRES: - 4,0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 62999.96 | G.I. WIRES: - 5,0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 2183.26
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 978.57 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 2334.43 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2075.04 | Jointing Kit&HW LT ABC CableStraight Sus
7130880006 | Cable marker for U/G cable | No. | 126.51 | CABLE MARKER FOR U/G CABLE
7130880006 | Pad Connector (for Panther conductor) | No. | 139.39 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 89.74 | Danger boards 33 KV & 11 KV.
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 5151.35 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 6499.75
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 14741.43 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 15443.4 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 57.3143 | LT LINE SPACERS
7130890973 | Stainless steel strap with buckle (for installation of Service Distribution Box) | Set | 58.95
7131961526 | GSM Modem | Nos. | 3696.94 | GSM MODEM
7130893004 | Eye Hook | No. | 176.78 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 3346.47 | 33 KV guarding channel 100x50 mm.
7131210001 | Panel lndication lamps | Nos. | 119.5288
7131210010 | LED 7 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210018 | LED 12 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210019 | LED 14 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210020 | LED 15 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210021 | LED Lamps with COMPLETE FITTING - 15 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210022 | LED LAMPS WITH COMPLETE FITTING - 20 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210852 | CFL 7 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210881 | 250 Watt Metal Halide | Each |  | METAL HALIDE LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131220182 | Tube Light Rod (T5 type) | Each |  | LAMPS: -Tube Light (40 Watts.) |  | ITEM DELETED: NOT TO BE USED
7131230003 | 250 Watt Sodium Vapour | Each |  | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER |  | ITEM DELETED: NOT TO BE USED
7131230116 | 250 Watt Mercury Vapour | Each |  | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO |  | ITEM DELETED: NOT TO BE USED
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each |  | S/ V HIGH PRESSURE LAMP 400W 230/250V |  | ITEM DELETED: NOT TO BE USED
7131280006 | CFL 15 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280007 | CFL 20 Watts | Each |  | CFL 20 WATTS LAMP |  | ITEM DELETED: NOT TO BE USED
7131280008 | CFL 23 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280009 | 125 Watt Mercury Vapour | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280010 | Halogen Filament (1000 Watts) | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280012 | Street Light fitting with tube light | Each |  | STREET LIGHT FITTING WITH TUBE LIGHT |  | ITEM DELETED: NOT TO BE USED
7131280013 | Street Light fitting with CFL | Each |  | STREET LIGHT FITTING WITH CFL |  | ITEM DELETED: NOT TO BE USED
7131280014 | HPSV lamp 150 watt | Each |  | HPSV LAMP 150 WATT |  | ITEM DELETED: NOT TO BE USED
7131280015 | HPSV Choke 250 watt | Each |  | HPSV LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each |  | 150 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each |  | 250 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280882 | CFL 11 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 1621.45 | ENERGY METER ENECTRONIC 10-60 AMPS | ISI MARK
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for __/110 Volts; __/1 Amps; or __/5 Amps) | Each | 1081589.85 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 169.52 |  |  | RATE EXCLUDING G.S.T.
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 728.2286 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 695.5 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A | ISI MARK
7131300881 | CMRI (Common Meter Reading Instrument) | Each | 26218.87 | Common Meter Reading Instrument CMRI
7131310013 | 3 Ø 4 Wire 0.5S Consumer meter | Each | 3829.1 | HT TRIVECTOR METER 5 AMPS | ISI MARK
7131310015 | CT operated electronic static meters with AMR (Composite Unit) with LTCTs / Modem / Meter / Meter Box. | Each | 11958.83 | ELECTORNIC LTCT METER 3X4 100/5 A | ISI MARK
7131310033 | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | Each | 3500.23 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310034 | 3 Ø 4 Wire 0.5S with DLMS Protocol category B | Each | 3500.23 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310035 | 3 Ø 3 Wire 0.2S bulk consumer meter | Each | 16457.11 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310036 | 3 Ø 4 Wire 0.2S bulk consumer meter | Each | 16457.11 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310042 | 3 Ø 4 Wire 0.2S 5A bulk consumer meter | Each | 16457.11 |  | ISI MARK
7131310037 | Test terminal Box (TTB) | Each | 894.97 | TTB
7131310997 | CT operated electronic static meters 100/5 Amp. With data storage. | Each | 1639.61 | 3 PHASE 4 WIRE LTCT OPERATED METER | ISI MARK
7131320009 | Digital Multimeter Electronic Type | Nos. | 3034.29 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) | Nos. | 3752.28 |  |  | RATE EXCLUDING G.S.T.
7131324780 | Megger 500 V | Nos. | 3641.1429
7131324806 | Megger up to 2.5 kV | Nos. | 5487.7591 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 6159.6
7131334001 | Set of 3 O.C. relays instantaneous high set feature | Nos. | 7516.15 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH
7131334002 | Set of 2 O.C.+ 1 earth fault relay without instantaneous high set feature | Nos. | 7576.27 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO
7131399007 | Master trip relays | Nos. | 1598.39
7131338004 | Transformer Oil Dielectric Breakdown testkit | Nos. | 61560 |  |  | RATE EXCLUDING G.S.T.
7131338025 | Neon tester | Nos. | 57.396 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 242.7429
7131387502 | Thermometer (Wall Mounted) | Nos. | 480.2521 | THERMOMETER (WALL MOUNTED)
7131390014 | Earthing Coil for messenger wire | Nos. | 185.97
7131390015 | Anchor sleeve for messenger wire | Nos. | 32.16
7131390016 | Universal hook & Bolts & nuts | Nos. | 450.51
7131820031 | LT Single Phase MCB 5 Amps. | Each | 103.08
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 103.08 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 436.86
7131820034 | LT Three Phase MCB 32 Amps. | Each | 436.86
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 2910.04
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 3152.97
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 3152.97
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2303.75
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 5275.03 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900004 | Locally fabricated - 3 Phase fuse units (Robust fuse for circuit base). | Each | 722.16 | LT ROBUST POLE FUSE UNIT |  | BIN CODE Changed. Old Bin 7131900005
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 7.46 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 299.63 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 460.65 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 12.78 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 13.85 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 295.38 | H.R.C. FUSE UNITS: -100 Amps.
7131900876 | H.R.C. Fuse 100 Amps. | Each | 115.17 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 742.17 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 821.08 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 577.24 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 10 SWG
7131900974 | T.C. Fuse Wire 8 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 8 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 44.41 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 87.76 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 25.38 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 246.62 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 474.95 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 1052.32 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920112 | 11 kV Kiosk VCB | Each | 315791 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 755.6 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 1814.36 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  |  |  |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 3509.55 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  |  |  |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 4927.03 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  |  |  |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 6684.69 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  |  |  |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 10097.04 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  |  |  |  | 51.2435
7131930109 | 33 kV ; 600 Amps with earth switch. | Each |  | 33 KV 600 AMPS WITH EARTH SWITCH ISOLATO |  | ITEM DELETED: NOT TO BE USED
7131930221 | 11 kV Porcelain A.B. Switch | Each | 8496 | AB Switch with complete fitting 11 KV
7131930321 | 33 kV Porcelain A.B. Switch | Each | 18863.48 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1177.88 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 2886.87 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 22623.4 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 39152.26 | 33 KV Isolator 800A without earth switch
7131931091 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure | Set | 27806.59 |  |  | NEW BIN CODE ALLOTED
7131931095 | Mounting GI structure for above isolator | Set | 14225.81 |  |  | NEW BIN CODE ALLOTED
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 2425.2 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 23039.46 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 23039.46
7131940871 | Indoor Type Automatic Control Unit along with APFC Relay | No. | 46692.4 |  |  | NEW BIN CODE ALLOTED
7131941762 | 11 kV VCB without control panel & CT's. | Each | 117747.13 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 235869.4 | 33KV VCB FOR 30 VOLT DC
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 990.47 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1193.13 | DISTRIBUTION BOX 3 PH 4 CONNECTOR |  |  | 7131910653 | 56.3592
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 40920.98
7131950016 | 11 kV Sectionalizer. | Each | 351072.13
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 15292.16 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 19116 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 38230.4 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 32804 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 26222.61 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 28818.87 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 25950.06 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 27166.71 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960010 | 11 kV Control & Relay Panel for Capacitor Bank | Each | 83478.19 |  |  | NEW BIN CODE ALLOTED
7131960520 | 2 Feeder Control (Static Relays) | Each | 38863.78 | 11KV MULTICIRCUIT (2F) CONTROL PANELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 38863.78 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 38863.78 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm;3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 207.33
7132004003 | Hack saw frames + B185 | Nos. | 133.7333
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 11.23
7132011171 | Cable Cutter | Nos. | 493.04 |  |  | NEW BIN CODE ALLOTED
7132013331 | Discharge Rod | Nos. | 477.619 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 3034.2857
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 1111.44
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 343.89
7132061858 | Combination Plier | Nos. | 229.58 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 73.8 | SCREW DRIVER 250MM
7132072007 | Screw driver 200 mm | Nos. | 69.11 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 64.43 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. |  | SCREW DRIVER INSULATED 255MM (DELETED) |  | ITEM DELETED: NOT TO BE USED
7132074032 | Ring Spanners (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 1607.09 | RING SPANNER
7132074033 | Tube Spanners | Set. | 664.15
7132074034 | Double end spanner (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 760.2 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 493.13
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F& tommy Bar) | Set. | 1464.18 | BOX SPANNER |  |  | 7130830054 | 358.7748
7132088614 | Pipe Wrench 24 inches size | Nos. | 1220.46 |  |  |  | 7130830056 | 358.7748
7132088615 | Pipe Wrench 18 inches size | Nos. | 669.79 |  |  |  | 7130830058 | 182.3872
7132200014 | 1089 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 | Each | 141355.63 | 11 KV CAPACITOR 600KVAR |  |  | 7130830603 | 267.5812
7132200812 | 5 kVAR | Each | 1561.71 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 3122.45 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 3751.83 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT |  |  | 7130800068 | 11746.105
7132200815 | 20 kVAR | Each | 6226.32 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT |  |  | 7130800014 | 7010.0389
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 186917.23 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each |  | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 25KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED | 7130890008 | 57.3143
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 63KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED | 7131387501 | 242.7429
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 100KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 200KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED | 7131387502 | 480.2521
7132210012 | 315 kVA (CEA Design) Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | XMER 315KVA 11/0.43KV CEA REG. CU WOUND |  | ITEM DELETED: NOT TO BE USED | 7132014014 | 3034.2857
7132210015 | 500 kVA [CEA Design] Copper Wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | 500 kVA [CEA Design] (4 Star) Copper Wound Transformer |  | ITEM DELETED: NOT TO BE USED | 7131324780 | 3641.1429
7132210106 | 0.2% Reactor suitable for 363 kVAR step | Set | 6864.39 |  |  | NEW BIN CODE ALLOTED
7132210108 | 0.2% Reactor suitable for 726 kVAR step | Set | 8380.18 |  |  | NEW BIN CODE ALLOTED
7132210215 | 50 kVA (Copper winding) | Each | 132374.78 | TRANSFORMER 33/.4KV 50KVA |  |  | 7131324806 | 5487.7591
7132220091 | Power Transformer 1600 kVA | Each | 780829.7 | TRANSFORMER 33/11KV 1.6 MVA POWER |  |  | 7131210001 | 119.5288
7132220095 | Power Transformer 3150 kVA | Each | 2241066.5 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 5000 kVA | Each | 3165338.45 | TRANSFORMER 33/11KV 5 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 229882.12 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 345.07 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 212181.48 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 345.07 | L.T. C.T.200/5 Amps. |  |  | 7132004003 | 133.7333
7132230021 | L.T.C.T. 300/5 Amps. | Each | 276.27 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 276.27 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1-1A | No. | 584046.53 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 24401.32 | 33KV CT 400-200/5-5A |  |  | 7132013331 | 477.619
7132230065 | 132 kV C.T. 600-300/1-1A | No. | 316935.3 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV |  |  | 7131338025 | 57.396
7132230075 | 132 kV C.T. 150-75/1-1A | No. | 361851.93 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1-1A | No. | 797258.43 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1-1A | No. | 521788.66 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1-1A | No. | 482699.81 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 36899.97
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 83670.61 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 12913.58 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 13463.75 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 25367.66 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5) Amps oil filled | Each | 19713.76 | 33KV CT's(200-100/5)A oil filled OD Type |  |  | 7131338004
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each |  | 33KV CT's (100-50/5)A oil filled OD Type |  | ITEM DELETED: NOT TO BE USED
7132230330 | 132 kV C.T. 100-50/1-1A | No. | 358156.27 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE |  |  | 7131300082 | 728.2286
7132230332 | 132 kV C.T. 200-100/1-1A | No. | 331433.7 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1-1A | No. | 290070.6 | CURRENT X-MER 300-150/1/1A - 132KV |  |  | 7130670027 | 133.7333
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A |  | ITEM DELETED: NOT TO BE USED
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 37970.88 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A |  | ITEM DELETED: NOT TO BE USED
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 36896.64 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 37368.74 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A |  | ITEM DELETED: NOT TO BE USED
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 36485.4 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230414 | 11 kV CTPT Unit 50/5 A | Each | 37635.9 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 82470.05 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 80471.17 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A |  | ITEM DELETED: NOT TO BE USED
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 86805.48 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A |  | ITEM DELETED: NOT TO BE USED
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 80181.91 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 80838.25 | OIL IMM 3 PH CTPT UNITS 33 KV-100&200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 80181.91 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 82412.42 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230471 | 11 kV 3 PH Residual Voltage Transformer | Each | 33323.81 |  |  | NEW BIN CODE ALLOTED
7132230473 | 11 kV PT Station Type | No. |  |  |  | ITEM DELETED: NOT TO BE USED
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 10336.32 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 16586.32 | VOLTAGE TRANSFORMER 33 KV / 110 VOLTS SINGLE
7132230501 | 132 kV P.T. | No. | 247996.79 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 584046.53 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132401672 | Small Steel Almirah 50'' | No. | 5408.9 | STEEL ALMIRAH SMALL SIZE
7132404015 | Safety belts | Nos. | 617.31 | SAFETY BELTS |  |  | 7130211121 | 272.3474
7132404016 | Safety helmets | Nos. | 139.59 | SAFETY HELMETS
7132404366 | Battery (Low Maintenance SAN controller) | No. | 51840 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 147.22 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 2580.37 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406420 | Pilfer proof SMC/FRPP/PPO LTCT meter box | Each | 3258.27
7132406425 | Universal Meter Box for HT meters. | Each | 2614.17 | Universal Meter Box for HT meters.
7132406721 | CT operated electronic static meters with DLMS. | Each | 2590.64 | LTCT METER WITH DLMS | ISI MARK
7132409830 | Office Chair cane seat & back with full arms rest | No. | 2649.94 | S-TYPE STEEL CHAIR WITH TEAK WOOD HAND
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 534.34 | RUBBER HAND GLOVES |  |  | 7130650001
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 5805.2 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 734.29 | RAIN COATS WITH HOODS |  | RATE EXCLUDING G.S.T.
7132427635 | Gum Boots | Nos. | 494.35 | GUM BOOTS |  | RATE EXCLUDING G.S.T.
7132438002 | Silica gel | Kg | 182.73 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 6.73 | POLYCARBONATE SEAL
7132444007 | Grounding Sticks (Galvanised Earthing Rods 25 mm, 3 Mtr. long) | Set. | 1003.21
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 4622.46 | METTING RUBBER 1900X1800X12MM
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 307.92
7132457798 | Transformer Oil In Barrel | KL | 67850 | TRANSFORMER OIL In Tanker/barrel
7132457798 | Transformer Oil In Tanker | KL | 58410 | TRANSFORMER OIL In Tanker/barrel
7132459005 | Poly Carbonate seal double anker type | Each | 5.85 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | 1146.75 | HDPE PIPE 200MM ID; 240MM OD |  |  | 7132401667 | 13429.5238
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 417 | JOINTING ARRANGEMENT OF HDPE PIPE |  |  | 7132409830 | 2649.9429
7132468558 | Battery charger | Each | 10952.19 | 30 Volt 100 AH lead acid battery charger |  |  | 7132476797 | 18542.8571
7132475019 | Files of sizes | Set. | 347.89 |  |  |  | 7132476795 | 21914.2857
7132475019 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 124.76 |  |  | RATE EXCLUDING G.S.T. | 7132420412 | 9630.4762
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 14.29 | PVC INSULATION TAPES 19 MM WIDE AND IN R |  | RATE EXCLUDING G.S.T. | 7132488810 | 53028.5714
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 67.62 |  |  | RATE EXCLUDING G.S.T. | 7132486195 | 32914.2857
7132478004 | Tong tester | Nos. | 1518.07 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI |  |  | 7132486151 | 7979.0476
7132478011 | Hand Torch 5 cell | Nos. | 599.94 |  |  |  | 7131880133 | 74240
7132478012 | Hand Torch 3 cell | Nos. | 393.33 | HAND TORCH 3 CELLED |  |  | 7131880134 | 40228.5714
7132478012 | Cotton Waste | Kg | 61.9 | HAND TORCH 3 CELLED |  | RATE EXCLUDING G.S.T.
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 5191.41 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 56.19 |  |  | RATE EXCLUDING G.S.T.
7132490053 | Bitumen compound | Kg | 101.14
7132498006 | River sand | Cmt | 903 | RIVER SAND
7130310027 | 11 kV Covered Conductor 50 Sqmm XLPE insulation | Mtr. | 489.36 | 11KV COVERED CONDUCTOR XLPE 50SQMM
7130310029 | 11 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 589.88 | 11KV COVERED CONDUCTOR XLPE 70SQMM
7130310043 | 11 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 753.26 | 11KV COVERED CONDUCTOR XLPE 99SQMM
7130310047 | 33 kV Covered Conductor 157 Sqmm XLPE insulation | Mtr. | 1111.21 | 33KV COVERED CONDUCTOR XLPE 157SQMM
7130310048 | 33 kV Covered Conductor 241 Sqmm XLPE insulation | Mtr. | 1565.71 | 33KV COVERED CONDUCTOR XLPE 241SQMM
7130310045 | 33 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 694.74 | 33KV COVERED CONDUCTOR XLPE 70SQMM
7130310046 | 33 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 790.12 | 33KV COVERED CONDUCTOR XLPE 99SQMM
7130310025 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 13494.42 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310026 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 21384.67 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310034 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 137519.06 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310035 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 210046.77 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7131310168 | Spot Billing Machine | Each | 11569.13
11 kV Oil Immersed 3 Phase CT-PT Unit of capacity --
7132230410 | 200/5 Amp | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7132230403 | 100/5 Amp | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131960919 | 33 kV 2 feeder control panel (Static Relays) | Each | 38863.78
7130870040 | G.I.Strip 25x3 mm | Kg | 85.92 |  |  | NEW BIN CODE ALLOTED
7132444005 | Numerical Poly Carbonate seals | No | 8.99
7130820013 | 33 kV Polymer Disc Insulator (45 kN) | No | 236.53 |  |  | BIN CODE Changed. Old Bin 7130820011
7131930110 | D.O.Fuse Polymer unit 11 kV | Each | 1561.44
7131930111 | D.O.Fuse Polymer unit 33 kV | Each | 2234.66
7130800001 | PCC Pole 200 kG; 9.0 Mtr. Long | Each | 3046.2
7130800002 | PCC Pole 365 kG; 11 Mtr. Long | Each | 7605.2
7130820001 | 11 kV Polymer Post Insulator | Nos. | 231.83
7130820002 | 33 kV Polymer Post Insulator | Nos. | 803.65
7130820010 | Silicon rubber composite insulator / 11 kV 45 kN Polymeric Insulator | Nos. | 128.45
7131930107 | Polymer A.B.Switch with complete fitting 11 kV | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131930108 | Polymer A.B.Switch with complete fitting 33 kV | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 200 Kg 8.0 Meter long PCC Pole | No | 2552.95
7130311023 | 2.5 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 22.32 | 2.5 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311024 | 4.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 26.78 | 4.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311025 | 6.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 39.05 | 6.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311026 | 6.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 46.86 | 6.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311027 | 8.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 56.91 | 8.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311028 | 10 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 68.07 | 10 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311029 | 16 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 89.27 | 16 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311030 | 25 sqmm. Four Core PVC insulated three phase Armoured service Cable | Mtr. | 113.82 | 25 sqmm 4C 3ɸ Armour PVC insulated service Cable
7132210017 | 16 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 44158.56 | XMER 16KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210018 | 25 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 49457.85 | XMER 25KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210019 | 63 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 89213.04 | XMER 63KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210020 | 100 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 117398.25 | XMER 100KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210021 | 200 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 220752.68 | XMER 200KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132220081 | 315 kVA, Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 546827.89 |  | ISI MARK
7132220082 | 500 kVA, Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 826555.57 |  | ISI MARK
7130640008 | RCC Block (with 6 mm MS Bar) * | Each | 158 |  |  | RATE EXCLUDING G.S.T.
7131210011 | LED 9 Watt Lamp | Each | 70 | LED 9 W lamp with holder
7131210023 | LED Lamps with complete fitting-24 W | Nos. |  | 24 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210024 | LED Lamps with complete fitting-48 W | Nos. |  | 48 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210025 | LED Lamps with complete fitting-60 W | Nos. |  | 60 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131941763 | 3 Way RMU, 2OD + 1VL, One Incomer + One Breaker + One Outgoing, 350 MVA, 650 Amps. | Unit | 760396.12 | 11 kV RMU 3 WAY,2 OD+1 VL, 350 MVA, 650 A.
7131941764 | 4 Way RMU, 2OD + 2VL, (One Incomer + Two Breakers + One Outgoing, 350 MVA, 650 Amps. | Unit | 1080119.04 | 11 kV RMU 4 WAY,2 OD+2 VL, 350 MVA, 650 A.
7131941765 | 5 Way RMU, 2OD + 3VL, (One Incomer + Three Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 1394147.12 | 11 kV RMU 5 WAY,2 OD+3 VL, 350 MVA, 650 A.
7131941766 | 6 Way RMU, 2OD + 4VL,(One Incomer + Four Breakers + One Outgoing, 350 MVA, 650 Amps. | Unit | 1708175.2 | 11 kV RMU 6 WAY,2 OD+4 VL, 350 MVA, 650 A.
7131941767 | 1OD for RMU | Unit | 273605.75 | 1OD for RMU
7131941768 | 1VL for 350 MVA, 650 Amps RMU | Unit | 319722.92 | 1VL for 350 MVA, 650 Amps RMU
7132230009 | Indoor Type 33 kV Metering Cubical CTPT Unit 10/5 A | Each | 212181.48 | INDOOR TYPE 33 KV 10/5A CT:PT CUBICAL UNIT
7132230011 | Indoor Type 33 kV Metering Cubical CTPT Unit 25/5 A | Each | 212181.48 | INDOOR TYPE 33 KV 25/5A CT:PT CUBICAL UNIT
7132230012 | Indoor Type 33 kV Metering Cubical CTPT Unit 200/5 A | Each | 229882.12 | INDOOR TYPE 33 KV 200/5A CT:PT CUBICAL UNIT
7132230008 | Indoor Type 11 kV Metering Cubical CTPT Unit 10/5 A | Each | 69481.96 | INDOOR TYPE 11 KV 10/5A CT:PT CUBICAL UNIT
7132230010 | Indoor Type 11 kV Metering Cubical CTPT Unit 25/5 A | Each | 69481.96 | INDOOR TYPE 11 KV 25/5A CT:PT CUBICAL UNIT
7131980004 | (0+1) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH ONE 630 A LOAD BREAK SWITCH. | No. | 231096.84
7131980005 | (0+3) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH THREE 630 A LOAD BREAK SWITCHES. | No. | 427328.6
7131980006 | (0+4) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR 630 A LOAD BREAK SWITCHES. | No. | 518467.28
7131980007 | (0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER IN BETWEEN AFTER ISOLATOR. | No. | 826173.17
7131980008 | (0+2)+BC+(0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH SIX NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER WITH LBS IN BETWEEN AFTER ISOLATOR. | No. | 1306570.86
7131980001 | 12 kV, Outdoor type Vacuum Capacitor switches | No. | 67737.07 |  |  | NEW BIN CODE ALLOTED
7131920028 | AC Distribution board for AC/DC Supply | No. | 10907.7 |  |  | NEW BIN CODE ALLOTED
7132486843 | Chem Rod Earthing electrode (Chemical Earthing) | No. | 8945.71 |  |  | RATE EXCLUDING G.S.T.
7130840003 | Surge Arrestor | No. | 825.74 |  |  | NEW BIN CODE ALLOTED
7131950396 | Ground connection for Messenger Wire | No. | 125.46 |  |  | NEW BIN CODE ALLOTED
7132406800 | 33/11 kV S/S (Name Plate) Board | Job | 9412.76 |  |  | NEW BIN CODE ALLOTED
7131210840 | 11 kV Fault Passage Indicator for Overhead line | No. | 14104.76 |  |  | NEW BIN CODE ALLOTED; RATE EXCLUDING G.S.T.
[7 empty] | 7130650001 | 1076.9743
[7 empty] | 7131338004 | 61560
Note on B163: 89326879: Earlier name - 600 mm
Note on B164: 89326879: Earlier name - 900 mm
Note on B316: 89326879: Earlier name- 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for 132 kV)
Note on B321: 89326879: Earlier name - 3 Ø 4 Wire 0.5S Non DLMS
Note on B322: 89326879: Earler name was - CT operated electronic static meters with AMR (Composite Unit)
Note on B325: 89326879: Earlier name- 3 Ø 3 Wire 0.2S Non DLMS
Note on B326: 89326879: Earlie name- 3 Ø 4 Wire 0.2S Non DLMS
Note on B338: 89326879: Earlier name - Transil oil Dielectric Breakdown testkit
Note on B461: 89326879: Earlier capacity was -- 220 kV C.T. 800-400/1
Note on B463: 89326879: Earlier capacity was - 132 kV C.T. 600-300/1
Note on B464: 89326879: Earlier capacity was - 132 kV C.T. 150-75/1
Note on B465: 89326879: Earlier capacity was -- 220 kV C.T. 150-75/1
Note on B466: 89326879: Earlier capacity was -- 220 kV C.T. 300-150/1
Note on B467: 89326879: Earlier capacity was -- 220 kV C.T. 600-300/1
Note on B475: 89326879: Earlier capacity was - 132 kV C.T. 100-50/1
Note on B476: 89326879: Earlier name was --132 kV C.T. 200-100/1
Note on B477: 89326879: Earlier capacity was -- 132 kV C.T. 300-150/1
Note on B517: 89326879: Earlier named as--Grounding Sticks (Earthing Rods)
Note on C8: 89326879: Earlier unit was - Per 1000
Note on C171: 89326879: Earlier unit- Sq.mtr

## A-1
COST SCHEDULE A-1
1 KM OF 33 kV LINE ON PCC POLES / H-BEAMS WITH MAXIMUM SPAN OF 100 METERS USING RACCOON CONDUCTOR
2018-19
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4402.65 | 44026.5
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 46.4039 | 223805.9132
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7605.2 | 76052
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2354.14 | 23541.4 | 10 | 2354.14 | 23541.4 | 10 | 2354.14 | 23541.4
5 | Back Clamp for Cross Arm
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 10 | 291.13 | 2911.3 |  |  |  | 10 | 291.13 | 2911.3
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 10 | 322.98 | 3229.8
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 391.69 | 3916.9 | 10 | 391.69 | 3916.9 | 10 | 391.69 | 3916.9
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 114.85 | 1148.5 | 10 | 114.85 | 1148.5 | 10 | 114.85 | 1148.5
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 351.44 | 10543.2 | 30 | 351.44 | 10543.2 | 30 | 351.44 | 10543.2
9 | Raccoon ACSR Conductor (80 Sqmm, Al. Eq) with 3% sag | 7130830060 | Mtr | 3100 | 50.1858 | 155575.949 | 3100 | 50.1858 | 155575.949 | 3100 | 50.1858 | 155575.949
10 | Jointing Sleeves suitable ( for 80 Sqmm, Al.Eq. ACSR cond.) | 7130830050 | No | 6 | 36.14 | 216.84 | 6 | 36.14 | 216.84 | 6 | 36.14 | 216.84
11 | (i) Stay set 20 mm | 7130860033 | No | 3 | 803.97 | 2411.91 | 3 | 803.97 | 2411.91 | 3 | 803.97 | 2411.91
| (ii) Stay Clamp For PCC Pole | 7130810193 | No | 3 | 291.13 | 873.39 |  |  |  | 3 | 291.13 | 873.39
| (iii) Stay Clamp For "H" Beam | 7130810692 | Pair |  |  |  | 3 | 322.98 | 968.94
| (iv) Stay Wire 7/8 SWG @ 8.5 kg/ stay | 7130860076 | Kg | 25.5 | 69.7564 | 1778.7885 | 25.5 | 69.7564 | 1778.7885 | 25.5 | 69.7564 | 1778.7885
12 | Concreting of supports @ 0.6 Cmt. Per pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC; and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole. (1:3:6) | 7130200202 | Cmt | 2 | 2510.8 | 5021.6 | 8 | 2510.8 | 20086.4 | 7 | 2510.8 | 17575.6 | only material cost (excluding labour & G.S.T.)
13 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 146.77 | 205.478 | 6 | 146.77 | 880.62 | 1.4 | 146.77 | 205.478
14 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 327.94 | 491.91 | 6 | 327.94 | 1967.64 | 1.5 | 327.94 | 491.91
15 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 76.075 | 1521.5006 | 20 | 76.075 | 1521.5006 | 20 | 76.075 | 1521.5006
16 | Danger Board | 7130880041 | No | 10 | 89.74 | 897.4 | 10 | 89.74 | 897.4 | 10 | 89.74 | 897.4
17 | Binding wire and tape | 7130830006 | Kg | 3.5 | 155.45 | 544.075 | 3.5 | 155.45 | 544.075 | 3.5 | 155.45 | 544.075
18 | M.S. Nuts and Bolts |  | Kg | 17 |  |  | 17 |  |  | 18
| 16x65 mm | 7130620614 | Kg |  | 68.22 |  | 7 | 68.22 | 477.54 |  | 68.22
| 16x90 mm | 7130620619 | Kg | 3 | 68.22 | 204.66 |  | 68.22 |  | 3.5 | 68.22 | 238.77
| 16x140 mm | 7130620625 | Kg |  | 67.06 |  | 10 | 67.06 | 670.6 |  | 67.06
| 16x160 mm | 7130620627 | Kg | 14 | 67.06 | 938.84 |  | 67.06 |  | 14.5 | 67.06 | 972.37
19 | Guarding 33 kV |  | Rs |  |  | 12135.4882 |  |  | 12135.4882 |  |  | 12135.4882
| (i) G.I. Wire 6 SWG | 7130870045 | Kg | 49 | 63 | 3086.998 | 49 | 63 | 3086.998 | 49 | 63 | 3086.998
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 20 | 63 | 1259.9992 | 20 | 63 | 1259.9992 | 20 | 63 | 1259.9992
| (iii) 33 kV guarding channel | 7130897759 | Set | 1 | 3346.47 | 3346.47 | 1 | 3346.47 | 3346.47 | 1 | 3346.47 | 3346.47
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 322.98 | 968.94 | 3 | 322.98 | 968.94 | 3 | 322.98 | 968.94
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 67.06 | 80.472 | 1.2 | 67.06 | 80.472 | 1.2 | 67.06 | 80.472
| (vi) I--Bolt Big Size | 7130620013 | No | 4 | 124.12 | 496.48 | 4 | 124.12 | 496.48 | 4 | 124.12 | 496.48
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 803.97 | 1607.94 | 2 | 803.97 | 1607.94 | 2 | 803.97 | 1607.94
| (viii) Stay wire 7/8 SWG & 8.5 Kg/stay | 7130860076 | Kg | 17 | 69.7564 | 1185.859 | 17 | 69.7564 | 1185.859 | 17 | 69.7564 | 1185.859
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 68.22 | 102.33 | 1.5 | 68.22 | 102.33 | 1.5 | 68.22 | 102.33
20 | SUB TOTAL-1 |  |  |  |  | 268905.6293 |  |  | 466319.4045 |  |  | 313552.7693
21 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 24201.5066 |  | 0.09 | 41968.7464 |  | 0.09 | 28219.7492
22 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 369.7721 | 3697.7207 | 0 | 0 | 0 | 0 | 0 | 0
23 | Labour charges as per Schedule No.- AL-1 |  |  |  |  | 45038.69 |  |  | 52696.51 |  |  | 50161.41
24 | Labour charges for concreting |  | Cmt | 2 | 578.8434 | 1157.6868 | 8 | 578.8434 | 4630.7472 | 7 | 578.8434 | 4051.9038
25 | Transport charges upto 50 Kms average lead form area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 13390.7506 |  |  | 13390.7506 |  |  | 13390.7506
26 | SUB TOTAL-2 |  |  |  |  | 356391.984 |  |  | 579006.1587 |  |  | 409376.5829
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 33613.2037 |  | 0.125 | 58289.9256 |  | 0.125 | 39194.0962
28 | Cost per Km for non-guaranteed works |  |  |  |  | 390005.1876 |  |  | 637296.0843 |  |  | 448570.6791
29 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 390005 |  |  | 637296 |  |  | 448571
Note:-
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on D40: 89326879: Earlier unit was - No.

## A-2 (A)
COST SCHEDULE A-2 (A)
| 33 kV FOUR POLE STRUCTURE ON PCC / H-BEAM POLE | [5 empty] | 2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty | PCC Pole 280 kg 9.1 Mtr. Long | H-Beams 37.1 Kg/Mtr., 13 Mtr. Long
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 280 Kg.,9.1 Mtrs. long PCC Poles | 7130800033 | No | 4402.65 | 4 | 17610.6
2 | H-Beams 152 X 152 mm., 37.1 Kg/Mtr 13 Mtr. Long (482.3 Kg x 4 No = 1929.2 Kgs) | 7130601958 | Kg | 46.4039 | 1929.2 |  | 89522.3653
3 | D.C.cross- arm of 100 X 50 X 6 mm. suitable for 5' centre DP | 7130810608 | Set | 5428.06 | 2 | 10856.12 | 10856.12
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 248.51 | 24 | 5964.24 | 5964.24
5 | 33 kV Polymer Disc Insulator | 7130820013 | No | 236.53 | 24 | 5676.72 | 5676.72 | BIN CODE Changed. Old Bin 7130820011
6 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 66.185 | 50 | 3309.252 | 3309.252
7 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No. | 351.44 | 8 | 2811.52 | 2811.52
8 | DC cross arm 3.8 Mtr. Channel of 100x50 mm | 7130810006 | Set | 6872.65 | 8 | 54981.2 | 54981.2
9 | (i) Stay Clamp For PCC Pole | 7130810193 | No | 291.13 | 16 | 4658.08
| (ii) Stay Clamp For "H" Beam | 7130810692 | Pair | 322.98 | 16 |  | 5167.68
10 | 33 kV AB Switch | 7131930321 | Each | 18863.48 | 4 | 75453.92 | 75453.92
11 | Concreting of supports @ 0.5 Cmt Per pole for PCC Pole and @ 0.05 Cmt per pole for base padding for PCC pole (1:3:6) | 7130200202 | Cmt. | 2510.8 | 2.2 | 5523.76 |  | only material cost (excluding labour & G.S.T.)
| Concreting of supports @ 0.6 Cmt. Per pole for H-Beam and @ 0.05 Cmt per pole for base padding for H-Beam pole (1:3:6) | 7130200202 | Cmt. | 2510.8 | 2.6 |  | 6528.08
12 | M.S.Angle 75x75x6 mm (for bracing 4 No. @ 60 kg each) | 7130600051 | Kg | 41.7888 | 60 | 2507.3256 | 2507.3256
13 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 114.85 | 4 | 459.4 | 459.4
14 | Red oxide paint | 7130211158 | Ltr | 146.77 | 6 |  | 880.62
15 | Aluminium paint | 7130210809 | Ltr | 327.94 | 6 |  | 1967.64
16 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 76.075 | 8 | 608.6002 | 608.6002
17 | Danger Board | 7130880041 | No | 89.74 | 4 | 358.96 | 358.96
18 | Strain Plate (65x8) mm | 7130810624 | No | 93.9 | 12 | 1126.8 | 1126.8
19 | M.S.Nuts and Bolts |  | Kg
| 16x40 mm | 7130620609 | Kg | 69.38 | 2 |  | 138.76
| 16x65 mm | 7130620614 | Kg | 68.22 | 2 |  | 136.44
| 16x90 mm | 7130620619 | Kg | 68.22 | 10 | 682.2 | 682.2
| 16x200 mm | 7130620631 | Kg | 67.06 | 15 | 1005.9 | 1005.9
20 | T-Clamp for Dog Conductor. | 7130830585 | No | 266.98 | 6 | 1601.88 | 1601.88
21 | SUB TOTAL-1 |  |  |  |  | 195196.4778 | 271745.6231
22 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 17567.683 | 24457.1061
23 | Labour charges for concreting of PCC Pole |  | Cmt | 578.8434 | 2.2 | 1273.4555
24 | Labour charges for concreting of H-Beam Pole |  | Cmt | 578.8434 | 2.6 |  | 1504.9928
25 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 369.7721 | 4 | 1479.0883 | 0
26 | Labour charges as per Schedule No.- AL-2(A) |  |  |  |  | 24271.4 | 23400.19
27 | Transportation charges |  |  |  |  | 13168.6726 | 13168.6726
28 | SUB TOTAL-2 |  |  |  |  | 252956.7772 | 334276.5847
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 24399.5597 | 33968.2029
30 | Cost per D.P. |  |  |  |  | 277356.3369 | 368244.7875
31 | Cost per D.P. (Rounded Off) |  |  |  |  | 277356 | 368245
Note on C19: 89326879: 2.6 cmt for H-Beam and 2.2 Cmt for PCC Pole
Note on C20: 89326879: 2.6 cmt for H-Beam and 2.2 Cmt for PCC Pole

## A-2 (B)
COST SCHEDULE A-2 (B)
2018-19
33 kV DP STRUCTURE ON PCC POLES / H-BEAM POLE (TO BE SUPPLEMENTED WITH EVERY 1.0 KM OF LINE OF RACCOON / DOG CONDUCTOR)
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg/Mtr 13.0 Mtr long H-Beam |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 4402.65 | 8805.3
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 46.4039 | 44761.1826
| (iii) 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 2 | 7605.2 | 15210.4
2 | DC cross arm of 100x50 mm Channel 5' Center | 7130810608 | Set | 1 | 5428.06 | 5428.06 | 1 | 5428.06 | 5428.06 | 1 | 5428.06 | 5428.06
3 | 33 kV Polymer Disc Insulator | 7130820013 | No | 18 | 236.53 | 4257.54 | 18 | 236.53 | 4257.54 | 18 | 236.53 | 4257.54 | BIN CODE Changed. Old Bin 7130820011
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 6 | 248.51 | 1491.06 | 6 | 248.51 | 1491.06 | 6 | 248.51 | 1491.06
5 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 351.44 | 1054.32 | 3 | 351.44 | 1054.32 | 3 | 351.44 | 1054.32
6 | Horizontal & cross bracing 5' centre with set of 4 back clamps |  | No | 1 | 3671.8456 |  | 1 | 3799.2456 |  |  | 3671.8456
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 4 | 291.13 | 1164.52 |  |  |  | 4 | 291.13 | 1164.52
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 4 | 322.98 | 1291.92
| (iii) M.S.Angle 65X65x6 mm | 7130600032 | Kg | 60 | 41.7888 | 2507.3256 | 60 | 41.7888 | 2507.3256 | 60 | 41.7888 | 2507.3256
7 | (i) Stay set 20 mm | 7130860033 | No | 6 | 803.97 | 4823.82 | 6 | 803.97 | 4823.82 | 6 | 803.97 | 4823.82
| (ii) Stay Clamp for PCC Pole | 7130810193 | No | 6 | 291.13 | 1746.78 |  |  |  | 6 | 291.13 | 1746.78
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 6 | 322.98 | 1937.88
| (iv) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 51 | 69.7564 | 3557.5769 | 51 | 69.7564 | 3557.5769 | 51 | 69.7564 | 3557.5769
8 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 93.9 | 563.4 | 6 | 93.9 | 563.4 | 6 | 93.9 | 563.4
9 | Concreting @ 0.6 Cmt per pole for H-Beam supports and 0.5 Cmt per pole for 365 kG 11 Mtr. Long PCC @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam (1:3:6) | 7130200202 | Cmt | 1.9 | 2510.8 | 4770.52 | 3.1 | 2510.8 | 7783.48 | 2.9 | 2510.8 | 7281.32 | only material cost (excluding labour & G.S.T.)
10 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 2 | 114.85 | 229.7 | 2 | 114.85 | 229.7 | 2 | 114.85 | 229.7
11 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 146.77 | 73.385 | 2 | 146.77 | 293.54 | 0.5 | 146.77 | 73.385
12 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 327.94 | 163.97 | 2 | 327.94 | 655.88 | 0.5 | 327.94 | 163.97
13 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001
14 | Danger Board | 7130880041 | No | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
15 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 69.38 | 34.69 | 0.5 | 69.38 | 34.69 | 0.5 | 69.38 | 34.69
| 16x65 mm | 7130620614 | Kg | 0.5 | 68.22 | 34.11 | 0.5 | 68.22 | 34.11 | 0.5 | 68.22 | 34.11
| 16x90 mm | 7130620619 | Kg |  | 68.22 |  | 2.5 | 68.22 | 170.55 |  | 68.22
| 16x140 mm | 7130620625 | Kg | 2 | 67.06 | 134.12 |  |  |  | 2 | 67.06 | 134.12
| 16x200 mm | 7130620631 | Kg | 4 | 67.06 | 268.24 | 3.5 | 67.06 | 234.71 | 4 | 67.06 | 268.24
16 | SUB TOTAL-1 |  |  |  |  | 41502.4776 |  |  | 81504.7853 |  |  | 50418.3776
17 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 3735.223 |  |  | 7335.4307 |  | 0.09 | 4537.654
18 | Labour charges for concreting |  | Cmt | 1.9 | 578.8434 | 1099.8025 | 3.1 | 578.8434 | 1794.4145 | 2.9 | 578.8434 | 1678.6459
19 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 2 | 369.7721 | 739.5441
20 | Labour charges as per Schedule No.- AL-2 |  |  |  |  | 10556.67 |  |  | 11076.4 |  |  | 11315.6
21 | Transport charges upto 50 Kms average lead from Area Store to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 5267.4711 |  |  | 5267.4711 |  |  | 5267.4711
22 | SUB TOTAL-2 |  |  |  |  | 62901.1883 |  |  | 106978.5016 |  |  | 73217.7486
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 5187.8097 |  | 0.125 | 10188.0982 |  | 0.125 | 6302.2972
24 | Cost per DP for non-guaranteed works |  |  |  |  | 68088.998 |  |  | 117166.5997 |  |  | 79520.0458
25 | Cost per DP for non-guaranteed works (Round off) |  |  |  |  | 68089 |  |  | 117167 |  |  | 79520
Note:
1 | This Schedule is to be supplemented with Schedule A-1 & A-3.
2 | All the rates are with considering price variation clause.
Note on D11: 89326879: Earlier unit was - No.

## A-3
COST SCHEDULE - A-3
1 KM OF 33 kV LINE ON PCC POLES / H-BEAM SUPPORT WITH MAXIMUM SPAN OF 100 METERS USING DOG CONDUCTOR
2018-19
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152 mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4402.65 | 44026.5
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 46.4039 | 223805.9132
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7605.2 | 76052
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2354.14 | 23541.4 | 10 | 2354.14 | 23541.4 | 10 | 2354.14 | 23541.4
5 | Back Clamp for Cross Arm
| (i) Stay Clamp For PCC Pole | 7130810193 | No | 10 | 291.13 | 2911.3 |  |  |  | 10 | 291.13 | 2911.3
| (ii) Stay Clamp For H-Beam Pole | 7130810692 | Pair |  |  |  | 10 | 322.98 | 3229.8
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 391.69 | 3916.9 | 10 | 391.69 | 3916.9 | 10 | 391.69 | 3916.9
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 114.85 | 1148.5 | 10 | 114.85 | 1148.5 | 10 | 114.85 | 1148.5
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 351.44 | 10543.2 | 30 | 351.44 | 10543.2 | 30 | 351.44 | 10543.2
9 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 3100 | 66.185 | 205173.624 | 3100 | 66.185 | 205173.624 | 3100 | 66.185 | 205173.624
10 | Jointing Sleeves (suitable for 100 Sqmm, Al. Eq. ACSR cond.) | 7130830051 | No | 6 | 141.07 | 846.42 | 6 | 141.07 | 846.42 | 6 | 141.07 | 846.42
11 | Stay set 20 mm | 7130860033 | No | 3 | 803.97 | 2411.91 | 3 | 803.97 | 2411.91 | 3 | 803.97 | 2411.91
12 | Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 3 | 291.13 | 873.39 |  |  |  | 3 | 291.13 | 873.39
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 3 | 322.98 | 968.94
13 | Stay Wire 7/8 SWG @ 8.5 kg Per stay | 7130860076 | Kg | 25.5 | 69.7564 | 1778.7885 | 25.5 | 69.7564 | 1778.7885 | 25.5 | 69.7564 | 1778.7885
14 | Concreting of H-Beam supports @ 0.6 cmt. Per pole and @ 0.3 Cmt per stay and @ 0.05 cmt per pole for base padding for PCC / H- Beam pole (1:3:6) | 7130200202 | Cmt | 2 | 2510.8 | 5021.6 | 8 | 2510.8 | 20086.4 | 7 | 2510.8 | 17575.6 | only material cost (excluding labour & G.S.T.)
15 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 146.77 | 205.478 | 6 | 146.77 | 880.62 | 1.4 | 146.77 | 205.478
16 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 327.94 | 491.91 | 6 | 327.94 | 1967.64 | 1.5 | 327.94 | 491.91
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 76.075 | 1521.5006 | 20 | 76.075 | 1521.5006 | 20 | 76.075 | 1521.5006
18 | Danger Boards | 7130880041 | No | 10 | 89.74 | 897.4 | 10 | 89.74 | 897.4 | 10 | 89.74 | 897.4
19 | Binding wire and tape | 7130830006 | Kg | 3.5 | 155.45 | 544.075 | 3.5 | 155.45 | 544.075 | 3.5 | 155.45 | 544.075
20 | M.S. Nuts and Bolts |  | Kg | 18 |  |  | 18 |  |  | 18
| 16x40 mm | 7130620609 | Kg |  | 69.38 |  | 0.5 | 69.38 | 34.69 |  | 69.38
| 16x65 mm | 7130620614 | Kg |  | 68.22 |  | 7.5 | 68.22 | 511.65 |  | 68.22
| 16x90 mm | 7130620619 | Kg | 3.5 | 68.22 | 238.77 |  | 68.22 |  | 3.5 | 68.22 | 238.77
| 16x140 mm | 7130620625 | Kg |  | 67.06 |  | 10 | 67.06 | 670.6 |  | 67.06
| 16x160 mm | 7130620627 | Kg | 14.5 | 67.06 | 972.37 |  | 67.06 |  | 14.5 | 67.06 | 972.37
21 | Guarding |  |  |  | 12135.4882 |  |  | 12135.4882 |  |  | 12135.4882
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 63 | 3086.998 | 49 | 63 | 3086.998 | 49 | 63 | 3086.998
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 63 | 1259.9992 | 20 | 63 | 1259.9992 | 20 | 63 | 1259.9992
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 1 | 3346.47 | 3346.47 | 1 | 3346.47 | 3346.47 | 1 | 3346.47 | 3346.47
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 322.98 | 968.94 | 3 | 322.98 | 968.94 | 3 | 322.98 | 968.94
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 67.06 | 80.472 | 1.2 | 67.06 | 80.472 | 1.2 | 67.06 | 80.472
| (vi) I-Bolt Big Size | 7130620013 | No | 4 | 124.12 | 496.48 | 4 | 124.12 | 496.48 | 4 | 124.12 | 496.48
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 803.97 | 1607.94 | 2 | 803.97 | 1607.94 | 2 | 803.97 | 1607.94
| (viii) Stay wire 7/8 SWG & 8.5 Kg/ stay | 7130860076 | Kg | 17 | 69.7564 | 1185.859 | 17 | 69.7564 | 1185.859 | 17 | 69.7564 | 1185.859
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 68.22 | 102.33 | 1.5 | 68.22 | 102.33 | 1.5 | 68.22 | 102.33
22 | SUB TOTAL-1 |  |  |  |  | 319200.5243 |  |  | 516615.4595 |  |  | 363780.0243
23 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 28728.0472 |  | 0.09 | 46495.3914 |  | 0.09 | 32740.2022
24 | Labour charges for concreting |  | Cmt | 2 | 578.8434 | 1157.6868 | 8 | 578.8434 | 4630.7472 | 7 | 578.8434 | 4051.9038
25 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 369.7721 | 3697.7207
26 | Labour charges as per Schedule No.- AL-3 |  |  |  |  | 46771.57 | -- | -- | 54429.13 |  |  | 50566.29
27 | Transport charges upto 50 Kms average lead form area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 16596.3437 |  |  | 16596.3437 |  |  | 16596.3437
28 | SUB TOTAL-2 |  |  |  |  | 416151.8926 |  |  | 638767.0718 |  |  | 467734.7639
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 39900.0655 |  | 0.125 | 64576.9324 |  | 0.125 | 45472.503
30 | Cost per Km for non-guaranteed works |  |  |  |  | 456051.9581 |  |  | 703344.0042 |  |  | 513207.267
31 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 456052 |  |  | 703344 |  |  | 513207
Note:
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on D42: 89326879: Earlier unit was - No.

## A-3 (A)
COST SCHEDULE -- A-3 (A)
2018-19
SCHEDULE FOR AUGMENTATION OF 1 kM OF 33 kV LINE FROM RACCOON TO DOG CONDUCTOR
S.No. | Particulars | New SAP Bin Code | Unit | Qty | Cost per Unit | Cost
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | ACSR Dog Conductor 100 sq.mm | 7130830063 | Km | 3.1 | 66185.04 | 205173.624
2 | Jointing Sleeves suitable for Dog ACSR Conductor | 7130830051 | No | 6 | 141.07 | 846.42
3 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 6 | 351.44 | 2108.64
4 | Guarding
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 63 | 3086.998
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 63 | 1259.9992
| (iii) 33 kV Guarding Channel (Set) | 7130897759 | Set | 1 | 3346.47 | 3346.47
| (iv) M.S Nut & Bolt 16x140 mm. | 7130620625 | Kg | 1.2 | 67.06 | 80.472
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 124.12 | 496.48
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 803.97 | 1607.94
| (vii) Stay Wire 7/8 SWG @ 8.5 Kg. Stay | 7130860076 | Kg | 17 | 69.7564 | 1185.859
| (viii) MS Nut & Bolt 16x90 mm | 7130620619 | Kg | 1.5 | 68.22 | 102.33
5 | Concreting of Stay Set @ 0.3 Cmt per stay (1:3:6) | 7130200202 | Cmt | 0.6 | 2510.8 | 1506.48 | only material cost (excluding labour & G.S.T.)
6 | SUB TOTAL-1 |  |  |  |  | 220801.7122
7 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 19872.1541
8 | Labour charges for concreting |  | Cmt | 0.6 | 578.8434 | 347.306
9 | Labour Charges |  |  |  |  | 22349.175
| Stay erection |  | No | 2 | 202.12 | 404.24
| Stringing of Dog Conductor |  | Ckt Km | 1 | 12993.71 | 12993.71
| Labour Charge for Carpet Guarding |  | Span | 1 | 2454.37 | 2454.37
| Dismantling Charges |  | Ckt Km | 1 | 6496.855 | 6496.855
10 | SUB TOTAL-2 |  |  |  |  | 263370.3473
11 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 27600.214
12 | Returnable cost of old conductor assuming 25 years of life & 20 years in service |  |  | 3.1 | 5229.36 | 16211.016
13 | Cost per Km |  |  |  |  | 274759.5454
14 | Cost (Rounded Off) |  |  |  |  | 274760
Note on D13: 89326879: Earlier unit was - No.

## A-3 (B)
COST SCHEDULE -- A-3 (B)
2018-19
COST SCHEDULE FOR ADDITIONAL (MID SPAN) POLE FOR 33 kV LINE USING 37.1 KG / MTR 13 M. LONG H-BEAM SUPPORT
S. No. | PARTICULARS | New SAP Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) H-Beam
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 482.3 | 46.4039 | 22380.5913
2 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 1 | 2354.14 | 2354.14
3 | Cross Arm Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 1 | 322.98 | 322.98
4 | 33 kV Top Clamp | 7130810676 | No | 1 | 391.69 | 391.69
5 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 1 | 114.85 | 114.85
6 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 351.44 | 1054.32
7 | Concreting of H-Beam support @ 0.6 Cmt. per pole and @ 0.05 Cmt per pole for base padding of H-Beam pole (1:3:6). | 7130200202 | Cmt | 0.65 | 2510.8 | 1632.02 | only material cost (excluding labour & G.S.T.)
8 | Red Oxide Paint | 7130211158 | Ltr | 1 | 146.77 | 146.77
9 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94
10 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 2 | 76.075 | 152.1501
11 | Danger Boards | 7130880041 | No | 1 | 89.74 | 89.74
12 | Binding wire and tape | 7130830006 | Kg | 0.5 | 155.45 | 77.725
13 | M.S. Nuts and Bolts |  | Kg | 2.5
| 16x40 mm | 7130620609 | Kg | 0.5 | 69.38 | 34.69
| 16x65 mm | 7130620614 | Kg | 1 | 68.22 | 68.22
| 16x90 mm | 7130620619 | Kg |  | 68.22
| 16x140 mm | 7130620625 | Kg | 1 | 67.06 | 67.06
| 16x160 mm | 7130620627 | Kg |  | 67.06
14 | SUB TOTAL-1 |  |  |  |  | 29214.8864
15 | Incidental Charges @ 9 % : - |  |  |  | 0.09 | 2629.3398
16 | Labour charges for concreting |  | Cmt | 0.65 | 578.8434 | 376.2482
17 | Labour charges as per Schedule No.- AL-3 (B) (Revised for one Pole) |  |  |  |  | 3178.43
18 | Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 1659.6354
19 | SUB TOTAL-2 |  |  |  |  | 37058.5398
20 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 3651.8608
21 | Cost of erection of 1 No. of H-Beam Pole for 33 kV Line |  |  |  |  | 40710.4006
22 | Cost (Rounded Off) |  |  |  |  | 40710

## A-4
COST SCHEDULE A-4
1 KM OF 33 kV LINE ON 37.1 KG / MTR 13 M. LONG H-BEAM SUSPENSION TYPE WITH PANTHER CONDUCTOR (WITH MAXIMUM SPAN OF 50 METERS)
2018-19
S. No. | PARTICULARS | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M long (482.30 Kg) x 20 No = 9646 Kgs | 7130601958 | Kg | 9646 | 46.4039 | 447611.8265
2 | DC Cross arm (100x50 mm) Channel 2.4 Mtr. (1.5 X 20 = 30) | 7130810512 | No. | 30 | 3977.41 | 119322.3
3 | 33 kV Suspension Hardware suitable for Panther Conductor (3x20=60) | 7130820312 | Set | 60 | 2129.35 | 127761
4 | 33 kV Polymer Disc Insulator (9x20=180) | 7130820013 | No. | 180 | 236.53 | 42575.4 | BIN CODE Changed. Old Bin 7130820011
5 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 20 | 114.85 | 2297
6 | ACSR Panther Conductor with 5% sag | 7130830070 | Mtr. | 3150 | 147.3877 | 464271.129
7 | Jointing Sleeves suitable for Panther conductor | 7130830971 | No. | 6 | 218.02 | 1308.12
8 | Stay Set 20 mm Complete | 7130860033 | Set. | 12 | 803.97 | 9647.64
9 | Stay Clamp for "H" Beam | 7130810692 | Pair | 100 | 322.98 | 32298
10 | Stay Wire 7/8 SWG @ 8.5 Kg/Stay | 7130860076 | Kg. | 170 | 69.7564 | 11858.5897
11 | Concreting of H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt. per Pole for base Padding & @ 0.3 Cmt. Per stay (1:3:6) | 7130200202 | Cmt. | 17.2 | 2510.8 | 43185.76 | only material cost (excluding labour & G.S.T.)
12 | Red Oxide Paint | 7130211158 | Ltr. | 26 | 146.77 | 3816.02
13 | Aluminium Paint | 7130210809 | Ltr. | 26 | 327.94 | 8526.44
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg. | 40 | 76.075 | 3043.0012
15 | Danger Boards | 7130880041 | No. | 20 | 89.74 | 1794.8
16 | Binding Wire & Tape | 7130830006 | Kg. | 8 | 155.45 | 1243.6
17 | MS Nut & Bolts |  | Kg. | 123
| 16x40 mm | 7130620609 | Kg. | 2 | 69.38 | 138.76
| 16x65 mm | 7130620614 | Kg. | 30 | 68.22 | 2046.6
| 16x90 mm | 7130620619 | Kg. | 20 | 68.22 | 1364.4
| 16x140 mm | 7130620625 | Kg. |  | 67.06
| 16x160 mm | 7130620627 | Kg. | 1 | 67.06 | 67.06
| 16x200 mm | 7130620631 | Kg. |  | 67.06
| 16x250 mm | 7130620637 | Kg. | 70 | 67.06 | 4694.2
18 | MS Angle 65x65x6 for Tie | 7130600032 | Kg. | 435 | 41.7888 | 18178.1106
19 | Strain Plate (65x8 mm) | 7130810624 | No. | 120 | 93.9 | 11268
20 | Guarding 33 kV for single span
| (i) G.I. Wire 6 SWG | 7130870045 | Kg. | 40 | 63 | 2519.9984
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg. | 20 | 63 | 1259.9992
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 2 | 3346.47 | 6692.94
| (iv) M.S Nut & Bolt 16x250 mm. | 7130620637 | Kg. | 5 | 67.06 | 335.3
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 124.12 | 496.48
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 803.97 | 1607.94
| (vii) Stay Wire 7/8 SWG & 8.5 Kg. Stay | 7130860076 | Kg. | 17 | 69.7564 | 1185.859
| (viii) Stay Clamp for "H" Beam | 7130810692 | Pair | 2 | 322.98 | 645.96
| (ix) MS Nut & Bolt 16x90 mm | 7130620619 | Kg. | 1 | 68.22 | 68.22
21 | SUB TOTAL-1 |  |  |  |  | 1373130.4535
22 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 123581.7408
23 | Labour charges for concreting |  | Cmt | 17.2 | 578.8434 | 9956.1065
24 | Labour Charges per Km as per Schedule - AL-4 |  | Km | 1 |  | 150368.94
25 | Transport Charges up to 50 km average lead from area Stores to Construction Camp Including Side Transport |  | LS | LS |  | 31380.1709
26 | SUB TOTAL-2 |  |  |  |  | 1688417.4117
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 171641.3067
28 | Cost per Km for Non- guaranteed Works |  |  |  |  | 1860058.7184
29 | Cost per Km for Non- guaranteed Works (Rounded off ) |  |  |  |  | 1860059
Note on D38: 89326879: Earlier unit was - No.

## A-5
COST SCHEDULE A-5
33 kV D.P. STRUCTURE ON 13 M. LONG H-BEAM POLE FOR PANTHER CONDUCTOR (TO BE SUPPLEMENTED WITH EVERY 0.3 kM OF SUSPENSION LINE)
2018-19
S. No. | Particulars | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg. | 964.6 | 46.4039 | 44761.1826
2 | DC Cross arm (100x50 mm) Channel 5' Center | 7130810608 | Set | 1 | 5428.06 | 5428.06
3 | 33 kV Tension Hardware suitable for Panther Conductor | 7130870318 | No. | 6 | 978.57 | 5871.42
4 | 33 kV Suspension Hardware suitable for Panther Conductor | 7130820312 | No. | 3 | 2129.35 | 6388.05
5 | 33 kV Polymer Disc Insulator | 7130820013 | No. | 27 | 236.53 | 6386.31 | BIN CODE Changed. Old Bin 7130820011
6 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 2 | 114.85 | 229.7
7 | Horizontal & Cross bracing |  | No. | 1
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 322.98 | 1291.92
| (ii) M.S. Angle 65X65x6 mm | 7130600032 | Kg | 60 | 41.7888 | 2507.3256
8 | Stay Set 20 mm complete | 7130860033 | Set. | 6 | 803.97 | 4823.82
9 | Stay Clamp for "H" Beam | 7130810692 | Pair | 9 | 322.98 | 2906.82
10 | Stay Wire 7/8 SWG @ 8.5 Kg./pole | 7130860076 | Kg. | 51 | 69.7564 | 3557.5769
11 | Concreting of H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt per Pole for base Padding & @ 0.3 Cmt. Per stay (1:3:6) | 7130200202 | Cmt. | 3.1 | 2510.8 | 7783.48 | only material cost (excluding labour & G.S.T.)
12 | Red Oxide Paint | 7130211158 | Ltr. | 2 | 146.77 | 293.54
13 | Aluminium Paint | 7130210809 | Ltr. | 2 | 327.94 | 655.88
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 76.075 | 304.3001
15 | Danger Board | 7130880041 | No | 2 | 89.74 | 179.48
16 | Strain Plate (65x8 mm) | 7130810624 | No. | 4 | 93.9 | 375.6
17 | MS Nut & Bolts |  | Kg. | 15
| 16x40 mm | 7130620609 | Kg. | 1 | 69.38 | 69.38
| 16x65 mm | 7130620614 | Kg. | 3 | 68.22 | 204.66
| 16x90 mm | 7130620619 | Kg. | 1 | 68.22 | 68.22
| 16x140 mm | 7130620625 | Kg. | 2 | 67.06 | 134.12
| 16x160 mm | 7130620627 | Kg. | 2 | 67.06 | 134.12
| 16x200 mm | 7130620631 | Kg. | 2 | 67.06 | 134.12
| 16x250 mm | 7130620637 | Kg. | 4 | 67.06 | 268.24
18 | SUB TOTAL-1 |  |  |  |  | 94757.3253
19 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 8528.1593
20 | Labour charges for concreting |  | Cmt | 3.1 | 578.8434 | 1794.4145
21 | Labour Charges as per Schedule AL-2 |  |  |  |  | 11076.4
22 | Transport Charges up to 50 km. average lead from area Stores to Construction Camp including Side Transport (Transport Schedule T-1) |  |  |  |  | 5267.4711
23 | SUB TOTAL-2 |  |  |  |  | 121423.7702
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 11844.6657
25 | Cost per DP for Non- guaranteed Works |  |  |  |  | 133268.4358
26 | Cost per DP for Non- guaranteed Works (Rounded off ) |  |  |  |  | 133268
Note on D11: 89326879: Earlier unit was - No.

## A-6
COST SCHEDULE A-6
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER EXISTING RAILWAY TRACK / ROAD FOR 60 MTR. LONG RAIL / ROAD CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | Using HDD Technique (for Railway works) on 3x400 sq.mm AB XLPE Cable | Using HDD Technique (for Road crossing works) on 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 8 | 10
1 | HDPE Pipe 200 mm ID; 240 mm OD; 6 Mtr long | 7132461004 | Mtr | 1146.75 | 120 | 137610 | 137610
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 417 | 18 | 7506 | 7506
3 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2150.6242 | 190 | 408618.6018 | 408618.6018
4 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 34129.38 | 4 | 136517.52 | 136517.52
5 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1079.16 | 24 | 25899.84 | 25899.84
6 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
7 | M.S.Flat (50x6) mm | 7130600173 | kg | 45.4764 | 100 | 4547.644 | 4547.644
8 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 4 | 2224 | 2224
9 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 80 | 2640 | 2640
10 | Sand | 7132498006 | Cmt | 903 | 1.2 | 1083.6 | 1083.6
11 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 4545.92 | 6 | 27275.52 | 27275.52
12 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 50.1858 | 18 | 903.3442 | 903.3442
13 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 266.98 | 6 | 1601.88 | 1601.88
14 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 849.08 | 10 | 8490.8 | 8490.8
15 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway authorities including liaisoning work etc. |  | LS | LS | LS | 25000
16 | SUB TOTAL-1 |  |  |  |  | 795918.75 | 770918.75
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 71632.6875 | 69382.6875
18 | Service in lieu of Earthing Coal & Sand etc |  | No | 2628.1669 | 10 | 26281.6694 | 26281.6694
19 | Labour Charges for laying of HDPE Pipe (using HDD Technique ** ) as per Schedule AL-5 |  |  |  |  | 344766 | 344766
20 | Labour Charges for excavation of cable trench beyond the length of HDPE Pipe upto DP Structure |  | CMT | 254.0989 | 12 | 3049.1863 | 3049.1863
21 | Transportation Charges |  |  |  |  | 79242.8549 | 79242.8549
22 | SUB TOTAL-2 |  |  |  |  | 1320891.1481 | 1293641.1481
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 99489.8438 | 96364.8438
24 | Charges payable to Railway including supervision charges etc. | 15% |  |  |  | 198133.6722
25 | Municipality Charges payable to Local bodies as per Demand note |  | LS
26 | Cost per 60 Mtr for non guaranteed works |  |  |  |  | 1618514.6641 | 1390005.9919
27 | Cost per 60 Mtr for non guaranteed works (Rounded off ) |  |  |  |  | 1618515 | 1390006
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
** | Horizontal Directional Drilling (HDD) Technique
This schedule is prepared for 60 Mtr Corridor of Railway / Road crossing. Estimate may be framed as per actual site conditions and actual width of the rail / road corridor.
*** | The charges to be paid for according railway permission shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note on E15: 89326879: Assuming 2 kg M-seal @ Rs 450/- per kg + PVC Plate 10 mm thick
Note on G28: 89326879: ***
Note on H34: 89326879: Fill appropriate cost here
*
***
Fill appropriate cost

## A-7
COST SCHEDULE A-7
2018-19
SCHEDULE FOR LAST SPAN CABLING OF 33 kV H.T. CONNECTION
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 3x185 sq.mm AB XLPE Cable | 3x240 sq.mm AB XLPE Cable
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 46.4039 | 482.3 | 22380.5913 | 22380.5913
2 | 3x185 sq.mm 33 kV AB XLPE Cable | 7130310053 | Mtr. | 1292.0726 | 50 | 64603.6305
3 | 3x240 sq.mm 33 kV AB XLPE Cable | 7130310054 | Mtr. | 1643.0038 | 50 |  | 82150.1915
4 | 33 kV Termination Kit for 3x185 sqmm AB XLPE Cable * | 7130320039 | Set | 15279.87 | 2 | 30559.74
5 | 33 kV Termination Kit for 3x240 sqmm AB XLPE Cable * | 7130320040 | Set | 17826.52 | 2 |  | 35653.04
6 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 114.85 | 1 | 114.85 | 114.85
7 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | Set | 3257.64 | 2 | 6515.28 | 6515.28
8 | Stay Set 20 mm | 7130860033 | No | 803.97 | 2 | 1607.94 | 1607.94
9 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 69.7564 | 17 | 1185.859 | 1185.859
10 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay (1:3:6) | 7130200202 | Cmt | 2510.8 | 1.25 | 3138.5 | 3138.5 | only material cost (excluding labour & G.S.T.)
11 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 1 | 146.77 | 146.77
12 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 1 | 327.94 | 327.94
13 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 76.075 | 2 | 152.1501 | 152.1501
14 | Danger Board | 7130880041 | No | 89.74 | 1 | 89.74 | 89.74
15 | Stay Clamp for "H" Beam | 7130810692 | Pair | 322.98 | 4 | 1291.92 | 1291.92
16 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 69.38 | 5 | 346.9 | 346.9
17 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 68.22 | 1 | 68.22 | 68.22
18 | Dead end Assembly (Suitable for all size cable) | 7130320044 | No. | 866.03 | 2 | 1732.06 | 1732.06
19 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 849.08 | 2 | 1698.16 | 1698.16
20 | Cable tie for AB Cable | 7130320045 | No | 25.72 | 25 | 643 | 643
21 | SUB TOTAL-1 |  |  |  |  | 136603.2509 | 159243.1119
22 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 12294.2926 | 14331.8801
23 | Labour Charges |  |  | 46344.6309 | 1 | 46344.6309 | 46344.6309
24 | Transport Charges |  |  | 14407.7881 | 1 | 14407.7881 | 14407.7881
25 | Labour charges for concreting |  | Cmt | 578.8434 | 1.25 | 723.5543 | 723.5543
26 | Service in lieu of Earthing Coal & Sand etc |  | No | 2628.1669 | 2 | 5256.3339 | 5256.3339
27 | SUB TOTAL-2 |  |  |  |  | 215629.8505 | 240307.299
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 17075.4064 | 19905.389
29 | GRAND TOTAL |  |  |  |  | 232705.2569 | 260212.688
30 | GRAND TOTAL (Round Off) |  |  |  |  | 232705 | 260213
* | Note -- Appropriate size of termination kit and 33 kV AB XLPE Cable may be used for S.No 04 and 05 acccording to the load of HT connection.
Note on D14: 89326879: Earlier unit was - No.

## A-8
COST SCHEDULE A-8
33 kV MEDP STRUCTURE ON PCC POLE / H-BEAM POLE (TO BE SUPPLEMENTED FOR H.T. CONNECTION)
2018-19
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg / Mtr 13.0 Mtr long H-Beam
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 4402.65 | 8805.3
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr; 13 Mtr long (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 46.4039 | 44761.1826
2 | DC cross arm of 100x50 mm Channel (3.8 Mtr. Long) | 7130810608 | Set | 2 | 5428.06 | 10856.12 | 2 | 5428.06 | 10856.12
3 | 33 kV Polymer Disc Insulator | 7130820013 | No | 18 | 236.53 | 4257.54 | 18 | 236.53 | 4257.54 | BIN CODE Changed. Old Bin 7130820011
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 6 | 248.51 | 1491.06 | 6 | 248.51 | 1491.06
5 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 351.44 | 1054.32 | 3 | 351.44 | 1054.32
6 | (i) Stay set 20 mm | 7130860033 | No | 6 | 803.97 | 4823.82 | 4 | 803.97 | 3215.88
| (ii) Stay Clamp for PCC Pole | 7130810193 | No | 6 | 291.13 | 1746.78
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 4 | 322.98 | 1291.92
| (iv) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 51 | 69.7564 | 3557.5769 | 34 | 69.7564 | 2371.7179
7 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 93.9 | 563.4 | 6 | 93.9 | 563.4
8 | Concreting of H-Beam supports @ 0.6 Cmt per pole ; @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole (1:3:6) | 7130200202 | Cmt | 1.9 | 2510.8 | 4770.52 | 2.5 | 2510.8 | 6277 | only material cost (excluding labour & G.S.T.)
9 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 2 | 114.85 | 229.7 | 2 | 114.85 | 229.7
10 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 146.77 | 73.385 | 2 | 146.77 | 293.54
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 327.94 | 163.97 | 2 | 327.94 | 655.88
12 | Barbed wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001
13 | Danger Board | 7130880041 | No | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
14 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 69.38 | 34.69 | 0.5 | 69.38 | 34.69
| 16x65 mm | 7130620614 | Kg | 0.5 | 68.22 | 34.11 | 0.5 | 68.22 | 34.11
| 16x90 mm | 7130620619 | Kg |  | 68.22 |  | 2.5 | 68.22 | 170.55
| 16x140 mm | 7130620625 | Kg | 2 | 67.06 | 134.12 |  | 67.06
| 16x200 mm | 7130620631 | Kg | 4 | 67.06 | 268.24 | 3.5 | 67.06 | 234.71
15 | GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 2 | 849.08 | 1698.16 | 2 | 849.08 | 1698.16
16 | G.I.Bend of 40 mm dia. | 7130640171 | Each | 1 | 104.16 | 104.16 | 1 | 104.16 | 104.16 | NEW BIN CODE ALLOTED
17 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3 | 4545.92 | 13637.76 | 3 | 4545.92 | 13637.76
18 | 33 kV CTPT unit of appropriate capacity |  | No
19 | Copper control cable 10 Core 2.5 Sqmm. (armoured) | 7130310660 | Mtr | 10 | 205.7332 | 2057.3324 | 10 | 205.7332 | 2057.3324
20 | H.T. Static Trivector Meter 3 Ø 4 Wire 0.5 S with DLMS Protocol category A | 7131310033 | No | 1 | 3500.23 | 3500.23 | 1 | 3500.23 | 3500.23
21 | Universal Meter Box for HT meters. | 7132406425 | Each | 1 | 2614.17 | 2614.17 | 1 | 2614.17 | 2614.17
22 | Test terminal Box (TTB) | 7131310037 | Each | 1 | 894.97 | 894.97 | 1 | 894.97 | 894.97
23 | SUB TOTAL-1 |  |  |  |  | 67765.4744 |  |  | 102694.1431
24 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 6098.8927 |  | 0.09 | 9242.4729
25 | Labour charges for concreting |  | Cmt | 1.9 | 578.8434 | 1099.8025 | 2.5 | 578.8434 | 1447.1085
26 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 2 | 369.7721 | 739.5441
27 | Labour charges as per Schedule No.- AL-2 |  |  |  |  | 10556.67 |  |  | 11076.4
28 | Transport charges upto 50 Kms average lead from Area Store to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 5267.4711 |  |  | 5267.4711
29 | SUB TOTAL-2 |  |  |  |  | 91527.8548 |  |  | 129727.5956
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 8470.6843 |  | 0.125 | 12836.7679
31 | Cost per DP for non-guaranteed works |  |  |  |  | 99998.5391 |  |  | 142564.3635
32 | Cost per DP for non-guaranteed works (Round off) |  |  |  |  | 99999 |  |  | 142564
Note:- 1. This Schedule is to be supplemented with Schedule A-1 & A-3.
2. All the rates are with considering price variation clause.

## A-9
COST SCHEDULE A-9
2018-19
SCHEDULE FOR LAST SPAN CABLING OF 33 kV LINE USING COVERED CONDUCTOR OF 70 & 99 SQ.MM SIZE
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 70 sq.mm Covered Conductor | 99 sq.mm Covered Conductor
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 46.4039 | 482.3 | 22380.5913 | 22380.5913
2 | 33 kV Covered conductor 70 sq.mm (207 Amp) (with 3% sag) | 7130310045 | Mtr. | 694.74 | 50 | 34737
3 | 33 kV Covered conductor 99 sq.mm (258 Amp) (with 3% sag) | 7130310046 | Mtr. | 790.12 | 50 |  | 39506
4 | 33 kV Polymer Disc Insulator | 7130820013 | Set | 236.53 | 3 | 709.59 | 709.59 | BIN CODE Changed. Old Bin 7130820011
5 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 114.85 | 1 | 114.85 | 114.85
6 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | Set | 3257.64 | 2 | 6515.28 | 6515.28
7 | Stay Set 20 mm | 7130860033 | No | 803.97 | 2 | 1607.94 | 1607.94
8 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 69.7564 | 17 | 1185.859 | 1185.859
9 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay (1:3:6) | 7130200202 | Cmt | 2510.8 | 1.25 | 3138.5 | 3138.5 | only material cost (excluding labour & G.S.T.)
10 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 1 | 146.77 | 146.77
11 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 1 | 327.94 | 327.94
12 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 76.075 | 2 | 152.1501 | 152.1501
13 | Danger Board | 7130880041 | No | 89.74 | 1 | 89.74 | 89.74
14 | Stay Clamp for "H" Beam | 7130810692 | Pair | 322.98 | 4 | 1291.92 | 1291.92
15 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 69.38 | 5 | 346.9 | 346.9
16 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 68.22 | 1 | 68.22 | 68.22
17 | Dead end Assembly (Suitable for all size cable) | 7130320044 | No. | 866.03 | 2 | 1732.06 | 1732.06
18 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 849.08 | 3 | 2547.24 | 2547.24
19 | Cable tie for AB Cable | 7130320045 | No | 25.72 | 25 | 643 | 643
20 | SUB TOTAL-1 |  |  |  |  | 77735.5504 | 82504.5504
21 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 6996.1995 | 7425.4095
22 | Labour Charges |  |  | 46344.6309 | 1 | 46344.6309 | 46344.6309
23 | Transport Charges |  |  | 14407.7881 | 1 | 14407.7881 | 14407.7881
24 | Labour charges for concreting |  | Cmt | 578.8434 | 1.25 | 723.5543 | 723.5543
25 | Service in lieu of Earthing Coal & Sand etc |  | No | 2628.1669 | 2 | 5256.3339 | 5256.3339
26 | SUB TOTAL-2 |  |  |  |  | 151464.057 | 156662.267
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 9716.9438 | 10313.0688
28 | GRAND TOTAL |  |  |  |  | 161181.0008 | 166975.3358
29 | GRAND TOTAL (Round Off) |  |  |  |  | 161181 | 166975
Note on D13: 89326879: Earlier unit was - No.

## A-10
COST SCHEDULE A-10
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER RAILWAY TRACK / ROAD FOR 60 MTR. LONG CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE USING OPEN TRENCH METHOD.
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD; 6 Mtr long | 7132461004 | Mtr | 1146.75 | 120 | 137610 | 137610
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 417 | 18 | 7506 | 7506
3 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 1967.9693 | 180 | 354234.465
4 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2150.6242 | 190 |  | 408618.6018
5 | End terminating jointing kit upto 240 sqmm XLPE cable | 7130352037 | Set | 23009.06 | 4 | 92036.24
6 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 34129.38 | 4 |  | 136517.52
7 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1079.16 | 24 | 25899.84 | 25899.84
8 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
9 | M.S.Flat (50x6) mm | 7130600173 | kg | 45.4764 | 100 | 4547.644 | 4547.644
10 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 4 | 2224 | 2224
11 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 80 | 2640 | 2640
12 | Sand | 7132498006 | Cmt | 903 | 1.2 | 1083.6 | 1083.6
13 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 4545.92 | 6 | 27275.52 | 27275.52
14 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 50.1858 | 18 | 903.3442 | 903.3442
15 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 266.98 | 6 | 1601.88 | 1601.88
16 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 849.08 | 10 | 8490.8 | 8490.8
17 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway / Road constructing authorities including liaisoning work etc. |  | LS | LS | LS | 25000 | 25000
18 | SUB TOTAL-1 |  |  |  |  | 697053.3332 | 795918.75
19 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 62734.8 | 71632.6875
20 | Service in lieu of Earthing Coal & Sand etc |  | No | 2628.1669 | 10 | 26281.6694 | 26281.6694
21 | Labour Charges for excavation of cable trench using open trench method as per Schedule - AL-6 |  | Mtr |  | 60 | 166337 | 170972
22 | Transportation Charges |  |  |  |  | 79242.8498 | 79242.8498
23 | SUB TOTAL-2 |  |  |  |  | 1031649.6524 | 1144047.9567
24 | Overhead Charges @ 12.5% [ Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 87131.6667 | 99489.8438
25 | Charges payable to Railway including supervision charges etc. | 15% |  |  |  | 154747.4479 | 171607.1935
26 | Cost per 60 Mtr for non guaranteed works |  |  |  |  | 1273528.7669 | 1415144.994
27 | Cost per 60 Mtr for non guaranteed works (Rounded off ) |  |  |  |  | 1273529 | 1415145
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
The rates mentioned at S.No.1, 2, 3 & 4 are applicable for 60 Mtr Corridor of Railway crossing. Estimate may be prepared based on actual length of corridor.
** | The charges to be paid for according railway permisssion shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note on B14: 89326879: Earlier name was -- End terminating jointing kit for 240 sqmm XLPE cable
*
**

## A-11
COST SCHEDULE A-11
SCHEDULE FOR LAYING OF 1 kM 33 kV CABLE DIRECT IN GROUND SINGLE CABLE LINE USING OPEN TRENCH METHOD
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 1967.9693 | 1040 | 2046688.02
2 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2150.6242 | 1040 |  | 2236649.1888
3 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 120- 240 sq mm Underground XLPE cable |  | Set | 57101.14 | 2 | 114202.28
4 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 300- 400 sq mm Underground XLPE cable |  | No | 63943.26 | 2 |  | 127886.52
5 | End terminating jointing kit upto 240 sqmm XLPE cable | 7130352037 | Set | 23009.06 | 2 | 46018.12
6 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 34129.38 | 2 |  | 68258.76
7 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 1079.16 | 10 | 10791.6 | 10791.6
8 | G.I. Wire 8 SWG (for earthing connect to LA & cable) | 7130870043 | Kg | 63 | 5 | 314.9998 | 314.9998
9 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 20 | 11120 | 11120
10 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 4000 | 132000 | 132000
11 | River Sand (For 10 cm. base & 10 cm. filling of trench above cable & then cable covering tiles over complete length of trench) | 7132498006 | Cmt | 903 | 150 | 135450 | 135450
12 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 4545.92 | 6 | 27275.52 | 27275.52
13 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 50.1858 | 18 | 903.3442 | 903.3442
14 | Aluminium T-clamp suitable for Dog / Raccoon conductor for connecting L.A. | 7130830585 | No. | 266.98 | 6 | 1601.88 | 1601.88
15 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. | 7130642039 | No | 849.08 | 2 | 1698.16 | 1698.16
16 | M.S. Nuts & Bolts | Fill the appropriate Bin Code | Kg | 70.53 | 3 | 211.59 | 211.59
17 | Bhatta brick |  | No | 5.9 | 4400 | 25960 | 25960
18 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Road constructing authorities including liaisoning work etc. [ To be provisioned as per actual requirement ] |  | LS | LS | LS | 25000 | 25000
19 | SUB TOTAL-1 |  |  |  |  | 2579235.514 | 2805121.5628
20 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 232131.1963 | 252460.9407
21 | Service in lieu of Earthing Coal & Sand etc |  | No | 2628.1663 | 10 | 26281.6626 | 26281.6626
22 | Labour Charges - |  |  |  |  | 791943.5928 | 791943.5928
i | Cable trench excavation [(1.0 Mx0.75 Mx1.5 M) LxWxD] |  | Cmt | 239.23 | 1125 | 269133.75 | 269133.75
ii | Spreading of sand for base pad of cable (10 cm thick & 10 cm. above cable) |  | Mtr | 13.4095 | 1000 | 13409.5 | 13409.5
iii | Laying of XLPE Cable in open trench & rising on pole through GI pipe & back filling of cable trench with excavated soil |  | Mtr | 463.51 | 1040 | 482050.4 | 482050.4
iv | Laying of GI pipe |  | Mtr | 66.4123 | 10 | 664.1228 | 664.1228
v | Fixing of rising pipe with clamps |  | Mtr | 370.81 | 10 | 3708.1 | 3708.1
vi | Fixing of 33 kV lightning arrestor including earthing, jumpering and fixing of aluminium clamp |  | Set | 580.03 | 2 | 1160.06 | 1160.06
vii | Providing earthing (earthing pit digging and laying of earthing pipe complete) |  | Set | 1010.62 | 2 | 2021.24 | 2021.24
viii | Covering of cable with tiles |  | Mtr | 3.69 | 1000 | 3690 | 3690
ix | Making of Straight jointing of XLPE Cable |  | Set | 4362.99 | 2 | 8725.98 | 8725.98
x | Making of End jointing of XLPE Cable |  | Set | 3690.22 | 2 | 7380.44 | 7380.44
23 | Transportation Charges |  |  |  |  | 79242.8498 | 79242.8498
24 | SUB TOTAL-2 |  |  |  |  | 3708834.8155 | 3955050.6087
25 | Overhead Charges @ 12.5% [ Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 322404.4393 | 350640.1954
26 | Charges payable to Nagar Nigam / Nagar Palika / Nagar Panchayat / Gram Panchayat including supervision charges etc.
27 | Cost per Km for non guaranteed works |  |  |  |  | 4031239.2548 | 4305690.8041
28 | Cost per Km for non guaranteed works (Rounded off ) |  |  |  |  | 4031239 | 4305691
(a) | Cable and accessories size can be replaced as per actual requirement
(b) | When multiple cables have to be laid in the common trench, the following excavation is to be followed-- (i) 1.0 Mtr width x 1.5 Mtr depth for laying of 02 cables; (ii) 1.25 Mtr width x 1.5 Mtr depth for laying of 03 cables; (iii) 1.5 Mtr width x 1.5 Mtr depth for laying of 04 cables and so on.
(c) | Between two cables, fly ash brick is to be provided as separator
(d) | All other items are to be changed as per size of trench and number of cables in a trench.
ACTIVITY OF Col. 21 (xi) INCLUDED in (vi)
xi | Jumpering of Lightning arrestor and fixing of aluminium clamps |  | Set | 291.28 | 2 | 582.56 | 582.56
Note on E32: 89326879: As per AL-6
Note on E33: 89326879: As per AL-6
Note on E34: 89326879: As per AL-6
Note on E35: 89326879: As per AL-6
Note on E36: 89326879: As per AL-6
Note on E37: 89326879: As per AL-6
Note on E38: 89326879: As per AL-6
Note on E39: 89326879: As per AL-6

## B-1
COST SCHEDULE B -1
SCHEDULE FOR 33/11 kV, 3.15 MVA, 1.6 MVA SUB-STATION WITH TWO BAYS FOR OUTGOING FEEDERS AND 5 MVA SUB-STATION WITH THREE BAYS FOR OUTGOING FEEDERS AT NEW SITE
2018-19
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Proposed 33/11 kV S/s expandable to 2x1.6 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x3.15 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x5 MVA with control room
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 |  | LAND AND CIVIL WORKS (Rate as per SoR PWD)
| i | Construction of 1.5 Mtr high barbed wire fencing in angle iron post as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Mtr | 406 | 400 | 162400 | 400 | 162400 | 400 | 162400
| ii | Drilling of 150 mm dia bore well (upto 100 Mtr depth) with 1.5 HP Submersible motor pump and water supply line for switch yard including all taxes, T&P, materials, labours, transportation etc complete. |  | Job | 170146 | 1 | 170146 | 1 | 170146 | 1 | 170146
| iii | Construction of A1 type Control Room with toilet as per Drg. No. 04-01/AR/24-R2 date 13.06.2007 including all taxes royalty, T&P, materials, labours, transportation etc. complete. |  | Job | 906710 | 1 | 906710 | 1 | 906710 | 1 | 906710
| iv (a) | Construction of 2.4 Mtr high Chain link wire mesh fencing on Hard Soil or Hard Moorum as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | M | 2494 | 125 | 311750 | 125 | 311750 | 125 | 311750
| iv (b) | Construction of 2.4 Mtr high Chain link wire mesh fencing on Black Cotton Soil as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | M | 2860 | 125 | 357500 | 125 | 357500 | 125 | 357500 | NEW ROW ADDED
| v | Construction of 4.50 m x 2.15 m size yard / area gate as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Each | 35276 | 2 | 70552 | 2 | 70552 | 2 | 70552
| vi | Supply and filling of good quality hard moorum including stacking at site and spreading in layers of 150 mm thickness including watering and ramming including all leads & lifts, labour, T&P, transportation, loading unloading, royalty, taxes etc. complete (Moorum measured in stacks will be reduced by 16% for voids). |  | Cmt | 371 | 300 | 111300 | 300 | 111300 | 300 | 111300
| vii | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete and including spreading in 100 mm thick layers complete (Metal measured in stacks will be reduced by 8% for voids). |  | Cu. M | 1140 | 180 | 205200 | 180 | 205200 | 180 | 205200
| viii (a) | Construction of 4.0 Mtr wide Cement Concrete Road on hard soil or hard moorum as per given drawing including cost of mixture machine, vibrator, curing all materials, T&P, labour, transportation, loading, unloading, royalty taxes etc. complete. |  | Mtr | 4328 | 120 | 519360 | 120 | 519360 | 120 | 519360
| viii (b) | Construction of 4.0 Mtr wide Cement Concrete Road on black cotton soil as per given drawing including cost of mixture machine, vibrator, curing all materials, T&P, labour, transportation, loading, unloading, royalty taxes etc. complete. |  | Mtr | 4845 | 120 | 581400 | 120 | 581400 | 120 |  | NEW ROW ADDED
| ix | Construction of 7.50 M long 600 mm internal dia. NP-3 Hume pipe culvert as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty taxes etc. complete. |  | Each | 33635 | 1 | 33635 | 1 | 33635 | 1 | 33635
| x | Construction of 1.0 M high (from G.L.) brick masonary retaining wall as per given drawing including all labour, material, T&P, curing, transportation, loading, unloading, royalty taxes etc. complete. |  | RM | 3952 | 130 | 513760 | 130 | 513760 | 130 | 513760 | Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
|  | Sub total-1 | 7: 3004813; 9: 3004813; 11: 3004813
2 |  | EQUIPMENTS
| i | 33/11 kV transformer 1.60 MVA | 7132220091 | No | 780829.7 | 1 | 780829.7 | -- | -- | -- | --
|  | 33/11 kV transformer 3.15 MVA | 7132220095 | No | 2241066.5 | -- |  | 1 | 2241066.5 | -- | --
|  | 33/11 kV transformer 5.00 MVA | 7132220097 | No | 3165338.45 | -- |  | -- |  | 1 | 3165338.45
| ii | 33 kV VCB (With CT's & panel) | 4: No; 5: 333874.46; 6: --; 8: 1
|  | (i) 33 kV VCB (Without CT's & Panel) | 7131943380 | No | 235869.4 | -- |  | 1 | 235869.4 | 1 | 235869.4
|  | (ii) 33 kV Control Panel | 7131960524 | No | 38863.78 | -- |  | 1 | 38863.78 | 1 | 38863.78
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 19713.76 | -- |  | 3 | 59141.28 | 3 | 59141.28
| iii | 11 kV VCB for X'mer protection (With CTs & panel) | 4: No; 5: 197002.16; 6: 1; 8: 1; 10: 1
|  | (i) 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 117747.13 | 1 | 117747.13 | 1 | 117747.13 | 1 | 117747.13
|  | (ii) 11 kV Control Panel for Transformer Protection | 7131960522 | Each | 38863.78 | 1 | 38863.78 | 1 | 38863.78 | 1 | 38863.78
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | No | 13463.75 | 3 | 40391.25 | 3 | 40391.25 | 3 | 40391.25
| iv | 11 kV VCB for feeder protection with CTs & panel. | 4: No; 5: 364875.86; 6: 2; 8: 2; 10: 3 | 143697.19
|  | (i) 11 kV VCB with Relay & Control Panel | 7131960497 | No | 143697.19 | 2 | 287394.38 | 2 | 287394.38 | 3 | 431091.57 | 7131941762+7131960008=7131960497
|  | (ii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 12913.58 | 6 | 77481.48 | 6 | 77481.48 | 9 | 116222.22
| v | 33 kV Isolator (600 A.) Set without earth switch | 7131930752 | No | 39152.26 | 2 | 78304.52 | 2 | 78304.52 | 2 | 78304.52
| vi | 11 kV Isolator (600 A.) (including 2 Nos. for capacitor bank) Set | 7131930663 | No | 22623.4 | 6 | 135740.4 | 6 | 135740.4 | 8 | 180987.2
| vii | 33 kV DO Fuse unit | 7131930415 | Each | 2886.87 | 3 | 8660.61 | 3 | 8660.61 | 9 | 25981.83
| viii | 11 kV DO Fuse unit | 7131930412 | Each | 1177.88 | 3 | 3533.64 | 3 | 3533.64 | 6 | 7067.28
| ix | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 4545.92 | 3 | 13637.76 | 3 | 13637.76 | 3 | 13637.76
| x | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 504.66 | 12 | 6055.92 | 12 | 6055.92 | 15 | 7569.9
| xi | 33 kV AB Switch | 7131930321 | Each | 18863.48 | 1 | 18863.48 | 1 | 18863.48 | 1 | 18863.48
| xii | 11 kV AB Switch | 7131930221 | Each | 8496 | 3 | 25488 | 3 | 25488 | 4 | 33984
| xiii | Single phase 33 kV PT | 7132230057 | Each | 16586.32 | 3 | 49758.96 | 3 | 49758.96 | 3 | 49758.96
| xiv | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 80471.17 | 1 | 80471.17 | 1 | 80471.17 | 1 | 80471.17
| xv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 36485.4 | 2 | 72970.8 | 2 | 72970.8 | 3 | 109456.2
| xvi | Single phase 11 kV PT's | 7132230056 | Each | 10336.32 | 3 | 31008.96 | 3 | 31008.96 | 3 | 31008.96
| xvii | LT Meter (CT Operated) 100/5 A with CT's | 4: No; 5: 2674.82; 6: 1; 8: 1; 10: 1
|  | (i) LT Meter (CT Operated) 100/5 A | 7131310997 | No | 1639.61 | 1 | 1639.61 | 1 | 1639.61 | 1 | 1639.61
|  | (ii) LT CT 100/5 A | 7132230016 | No | 345.07 | 3 | 1035.21 | 3 | 1035.21 | 3 | 1035.21
| xviii | H.T. STATIC TRIVECTOR METERS | 4: No; 5: 10500.69; 6: 3; 8: 3; 10: 4
|  | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | 7131310033 | No | 3500.23 | 3 | 10500.69 | 3 | 10500.69 | 4 | 14000.92
| xix | Lead Acid Battery with automatic charger | 4: No; 5: 62792.19; 6: 1; 8: 1; 10: 1
|  | (i) Lead Acid Battery | 7132404366 | No | 51840 | 1 | 51840 | 1 | 51840 | 1 | 51840
| 1 | (ii) Battery Charger | 7132468558 | No | 10952.19 | 1 | 10952.19 | 1 | 10952.19 | 1 | 10952.19
| xx | 33/0.4 kV station transformer (50 kVA) | 7132210215 | Each | 132374.78 | 0 | 0 | 0 | 0 | 2 | 264749.56
| xxi | Energy efficient 11/0.4 kV station transformer (100 kVA) [LEVEL-2] * | 7132210020 | Each | 117398.25 | 1 | 117398.25 | 1 | 117398.25
| xxii | LT Distribution box for 63 kVA X'mer | 7131950065 | Each | 15292.16 | 0 | 0 | 0 | 0 | 2 | 30584.32
| xxiii | LT Distribution box for 100 kVA X'mer | 7131950105 | Each | 19116 | 1 | 19116 | 1 | 19116
| xxiv | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 6 Nos = 2448.6 Kgs | 7130601958 | Kg | 46.4039 | 2448.6 | 113624.5406 | 2448.6 | 113624.5406 | 2448.6 | 113624.5406
| xxv | Control cable
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr. | 119.1884 | 360 | 42907.8168 | 360 | 42907.8168 | 480 | 57210.4224
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr. | 62.7585 | 360 | 22593.0744 | 360 | 22593.0744 | 510 | 32006.8554
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr. | 36.2593 | 180 | 6526.6704 | 240 | 8702.2272 | 300 | 10877.784
| xxvi | Tee Clamp for Dog Conductor | 7130830585 | No | 266.98 | 96 | 25630.08 | 96 | 25630.08 | 108 | 28833.84
| xxvii | Danger Board for 33 kV & 11 kV equipment / supply pole | 7130880041 | No | 89.74 | 10 | 897.4 | 10 | 897.4 | 10 | 897.4
| xxviii | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 50.6744 | 300 | 15202.32 | 300 | 15202.32 | 300 | 15202.32
| xxix | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3036.33 | 5 | 15181.65 | 5 | 15181.65 | 6 | 18217.98
|  | Sub-total - 2 | 7: 2322247.4422; 9: 4118534.259; 11: 5532293.0724
3 |  | STRUCTURE AND BUS BAR ARRANGEMENTS: -
| i | 8 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x8 mtr =296.8 kg/pole x 10 Nos = 2968 Kgs. | 7130601958 | Kg | 46.4039 | 2968 | 137726.7158 | 2968 | 137726.7158 | 3561.6 | 165272.059
| ii | 7 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x7mtr = 259.7 Kg/pole x 4 Nos = 1038.8 Kgs. | 7130601958 | Kg | 46.4039 | 1038.8 | 48204.3505 | 1038.8 | 48204.3505 | 1038.8 | 48204.3505
| iii | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 8 Nos = 3264.8 Kgs | 7130601958 | Kg | 46.4039 | 3264.8 | 151499.3874 | 3264.8 | 151499.3874 | 4081 | 189374.2343
| iv | MS DC Cross arm (100 x 50 x 6 mm Channel) 5.2 Mtr long Set | 7130810684 | No | 8537.3 | 22 | 187820.6 | 22 | 187820.6 | 28 | 239044.4
| v | MS DC Cross arm (100 x 50 x 6 mm Channel) 3.8 Mtr long Set | 7130810006 | Set | 6872.65 | 2 | 13745.3 | 2 | 13745.3 | 9 | 61853.85
| vi | MS DC Cross arm (100 x 50 x 6 mm Channel) 2.7 Mtr long Set | 7130810608 | Set | 5428.06 | 9 | 48852.54 | 9 | 48852.54 | 11 | 59708.66
| vii | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1676.77 | 1 | 1676.77 | 1 | 1676.77 | 2 | 3353.54
| viii | R.S. Joist (175x85 mm) | 7130600675 | Kg | 44.9155 | 468 | 21020.4634 | 468 | 21020.4634 | 546 | 24523.8739
| ix | ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr | 66.185 | 500 | 33092.52 | 500 | 33092.52 | 600 | 39711.024
| x | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 351.44 | 6 | 2108.64 | 6 | 2108.64 | 9 | 3162.96
| xi | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 142.14 | 9 | 1279.26 | 12 | 1705.68 | 12 | 1705.68
| xii | Polymer Disc Insulator for 33 kV Side | 7130820013 | Each | 236.53 | 81 | 19158.93 | 81 | 19158.93 | 81 | 19158.93 | BIN CODE Changed. Old Bin 7130820011
| xiii | 33 kV Strain Hardware fitting | 7130820248 | Each | 248.51 | 81 | 20129.31 | 81 | 20129.31 | 102 | 25348.02
| xiv | Polymer Disc insulator for 11 kV side (double disc) | 7130820010 | Each | 128.45 | 108 | 13872.6 | 108 | 13872.6 | 150 | 19267.5
| xv | 33 kV Strain Plate 8 mm thick | 7130810624 | Each | 93.9 | 198 | 18592.2 | 198 | 18592.2 | 246 | 23099.4
| xvi | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 40 | 5870.8 | 40 | 5870.8 | 45 | 6604.65
| xvii | Aluminium Paint | 7130210809 | Ltr | 327.94 | 40 | 13117.6 | 40 | 13117.6 | 45 | 14757.3
|  | Sub-total - 3 | 7: 737767.9872; 9: 738194.4072; 11: 944150.4318
4 |  | OTHER MISCELLANEOUS ITEMS: -
| i | Concreting of structures & foundation (1:3:6) | 7130200202 | Cmt | 2510.8 | 51.6 | 129557.28 | 60.6 | 152154.48 | 67.2 | 168725.76 | only material cost (excluding labour & G.S.T.)
| ii | PVC insulated Single Core 70 Sqmm Armoured cable. | 7130311010 | Mtr. | 57.599 | 10 | 575.99 | 10 | 575.99 | 10 | 575.99 | Old Bin Code- 7130311054
| iii | 16 Sqmm 4-core Cable for Switch yard lighting, tripping arrangement & system control (armoured) | 7130311084 | Mtr. | 58.8139 | 300 | 17644.161 | 300 | 17644.161 | 300 | 17644.161
| iv | 18 W LED Street Light complete set |  | Set | 2264.64 | 4 | 9058.56 | 4 | 9058.56 | 4 | 9058.56 | Old item was - Mercury vapour lamp for Gate lighting 2 Nos. Old Bin Code no. 7131230128; Unit - No.
| v | 70 W LED Street Light complete set |  | Set | 4138.4 | 6 | 24830.4 | 6 | 24830.4 | 6 | 24830.4 | Old item was - 250 Watt metal halide fitting / HPSV fitting for Yard lighting Old Bin Code no. 7131280017; Unit - No.
| vi | AC Distribution board for AC/DC Supply | 7131920028 | No | 10907.7 | 1 | 10907.7 | 1 | 10907.7 | 1 | 10907.7
| vii | Fixing of 33/11 kV S/S (Name Plate) Board made up of 2 mm thick MS Sheet of size 5'x8' as per approved drawing. | 7132406800 |  | 9412.76 | 1 | 9412.76 | 1 | 9412.76 | 1 | 9412.76 | NEW BIN CODE ALLOTED
| viii | Earthing of Sub-station including Distribution Transformer earthing. | bar: 4; 6; 8; 10
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4315.55 | 21 | 90626.55 | 21 | 90626.55 | 21 | 90626.55
|  | (ii) GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 849.08 | 40 | 33963.2 | 40 | 33963.2 | 40 | 33963.2
|  | (iii) MS flat 50x6 mm size (2.5 kg per meter) | 7130600173 | Kg | 45.4764 | 1000 | 45476.44 | 1000 | 45476.44 | 1000 | 45476.44
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 63 | 31 | 1952.9988 | 31 | 1952.9988 | 31 | 1952.9988
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 95.97 | 25 | 2399.25 | 25 | 2399.25 | 25 | 2399.25
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 95.97 | 10 | 959.7 | 10 | 959.7 | 10 | 959.7
|  | (vii) GI Spring washers | 7130622922 | Kg | 149.07 | 5 | 745.35 | 5 | 745.35 | 5 | 745.35
|  | MS Nuts & Bolts | 4: Kg; 6: 186; 8: 270; 10: 270
|  | (i) MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 69.38 | 10 | 693.8 | 15 | 1040.7 | 15 | 1040.7
|  | (ii) MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 68.22 | 5 | 341.1 | 10 | 682.2 | 10 | 682.2
|  | (iii) MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 68.22 | 15 | 1023.3 | 25 | 1705.5 | 25 | 1705.5
|  | (iv) MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 67.06 | 66 | 4425.96 | 85 | 5700.1 | 85 | 5700.1
|  | (v) MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 67.06 | 80 | 5364.8 | 110 | 7376.6 | 110 | 7376.6
|  | (vi) MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 67.06 | 10 | 670.6 | 25 | 1676.5 | 25 | 1676.5
| ix | Furniture
|  | (i) Table 4'x2.5' | 7132476002 | No | 4886.32 | 1 | 4886.32 | 1 | 4886.32 | 1 | 4886.32
|  | (ii) Chair | 7132409830 | No | 2649.94 | 2 | 5299.88 | 2 | 5299.88 | 2 | 5299.88 | Old Bin Code is 7132409061
|  | (iii) Small Steel Almirah 50'' | 7132401672 | No | 5408.9 | 1 | 5408.9 | 1 | 5408.9 | 1 | 5408.9
| x | Fire fighting equipments | bar: 4
|  | (i) Fire fighting equipments (dry chemical powder type 5 Kg capacity) | 7132490006 | No | 5191.41 | 2 | 10382.82 | 2 | 10382.82 | 2 | 10382.82
|  | (ii) Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | 7132421002 | No | 5805.2 | 2 | 11610.4 | 2 | 11610.4 | 2 | 11610.4
| xi | Electrically insulated 11 kV mats infront of electrical control panel | 7132448003 | No | 4622.46 | 3 | 13867.38 | 3 | 13867.38 | 3 | 13867.38
|  | Sub-total - 4 | 7: 442085.5998; 9: 470344.8398; 11: 486916.1198
5 |  | Total including Civil works | 7: 6506914.0291; 9: 8331886.5059; 11: 9968172.6239
6 |  | Total excluding Civil works | 7: 3502101.0291; 9: 5327073.5059; 11: 6963359.6239
7 |  | Incidental Charges @ 9 % on "6" above | 5: 0.09; 7: 315189.0926; 9: 479436.6155; 11: 626702.3661
| (i) | Services on S/s earthing |  | No | 26292.6517 | 1 | 26292.6517 | 1 | 26292.6517 | 1 | 26292.6517
| (ii) | Services on Cable trench (separate trench for power cable & control cable). |  | RM | 2151.893 | 70 | 150632.51 | 70 | 150632.51 | 80 | 172151.44
| (iii) | Services on Painting of structures |  | No | 16922.9018 | 1 | 16922.9018 | 1 | 16922.9018 | 1 | 16922.9018
| (iv) | Services on Labelling of equipments |  | No | 14102.4181 | 1 | 14102.4181 | 1 | 14102.4181 | 1 | 14102.4181
8 |  | Labour charges as per sch. (BL-1+BL-3) | 7: 212677.93; 9: 226221; 11: 258055.14
9 |  | Labour charges for concreting |  | Cmt | 578.8434 | 51.6 | 29868.3194 | 60.6 | 35077.91 | 67.2 | 38898.2765
10 |  | Transport charges | 7: 37656.203; 9: 37656.203; 11: 41840.221
11 |  | Total cost of Sub-station (Including Civil works) | 7: 7310256.0558; 9: 9318228.7161; 11: 11163138.0391
12 |  | Total Cost (Rs In lakhs) | 7: 73.1026; 9: 93.1823; 11: 111.6314
13 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] | 5: 0.125; 7: 437762.6286; 9: 665884.1882; 11: 870419.953
14 |  | Grand Total cost of S/s. | 7: 7748018.6844; 9: 9984112.9043; 11: 12033557.9921
15 |  | Grand Total (Rounded off) | 7: 7748019; 9: 9984113; 11: 12033558
16 |  | Grand Total cost (Rs in LAKHS) | 7: 77.4802; 9: 99.8411; 11: 120.3356
Note:
| (1) | All the rates are with considering price variation clause.
| (2) | In case of non-availability of H-Beam for structure double welded RS Joist may be used (1) 8 meter long double welded RS Joist and cost of it shall be taken in place of cost of item No.3 (i) unit rate as Rs 10640.00 & quantity should be 10 Nos for 3.15 & 1.6 MVA and 12 Nos for 5 MVA (2) 7 meter long double welded RS Joist and cost of it shall be taken as in place of cost of item No.3 (ii) unit rate as Rs 9372.00 & quantity should be 04 Nos each for 3.15 & 1.6 MVA and 5 MVA
| (3) | The cost of land is not taken in to account since normally CSPDCL acquires Govt. land at negligible cost. How ever needs to be procure other than Govt. land then should be added actual cost.
| * | ISI Marked Energy Efficiency level-2 transformer
Note on C12: 89326879: Earlier name was - Area fencing with Barbed wire & RCC post
Note on C13: 89326879: Earlier name was -- Drilling of bore well (70 Mtr.-100 Mtr deep) with Submersible pump, overhead tank with staging if required, pipeline to earthing pit
Note on C14: 89326879: Earlier name was - Construction of control room with toilet (size 9.8 mtr x 5.5 mtr control room).
Note on C15: 89326879: Earlier name was -- Chain link mesh yard fencing with M.S.Angle post of size 65x65x6 mm, 2.85 Mtr. above GL / Yard level.
Note on C17: 89326879: Earlier name was - Iron Gate [3.26 x 1.8 m (Weight approx. 300 Kg) in RCC Column of size 40x40 cm]
Note on C18: 89326879: Earlier name was - Yard levelling & Moorum filling 40x30 x 0.30 m area
Note on C19: 89326879: Earlier name was - Yard Metalling with 40 mm crusher broken metal
Note on C20: 89326879: Earlier name was - Cement Concrete Road (4 Mtr wide)
Note on C22: 89326879: Earlier name was - Hume pipe culvert (600 mm dia)
Note on C23: 89326879: Earlier name was - Brick masonary retaining wall 1 Mtr. High.
Note on C32: 89326879: Earlier name was - 33 kV CT's 200-100/5 Amps
Note on C72: 89326879: Earlier name was - Marshelling Box
Note on C95: 89326879: Earlier name was - 70 Sqmm, 3.5 Core PVC armoured cable
Note on C97: 89326879: ITEM REPLACED
Note on C98: 89326879: ITEM REPLACED
Note on D95: 89326879: Bin Code changed
Note on E12: 89326879: Earliler unit was - RM
Note on E13: 89326879: Earlier unit was- Each
Note on E15: 89326879: Earlier unit was - RM
Note on E22: 89326879: Earlier unit was - Each
Note on E79: 89326879: Earlier unit was - No.
Note on E80: 89326879: Earlier unit was - No.
Note on E81: 89326879: Earlier unit was -- 'Set'
Note on E129: 89326879: Earlier unit taken as Mtr
Note on H24: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
Note on J24: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
Note on L24: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.

## B-2
COST SCHEDULE B-2
2018-19
( 33 kV SUB-STATION )
POWER TRANSFORMERS
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | 1600 kVA | 3150 kVA | 5000 kVA
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Cost of Transformer as per Schedule of rates
| Power Transformer 1600 kVA | 7132220091 | No | 780829.7 | 1 | 780829.7
| Power Transformer 3150 kVA | 7132220095 | No | 2241066.5 | 1 |  | 2241066.5
| Power Transformer 5000 kVA | 7132220097 | No | 3165338.45 | 1 |  |  | 3165338.45
2 | SUB TOTAL-1 |  |  |  |  | 780829.7 | 2241066.5 | 3165338.45
3 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 70274.673 | 201695.985 | 284880.4605
4 | Services for Painting |  |  |  |  | 5552.1331 | 8883.413 | 8883.413
5 | Labour charges as per Schedule BL-3 |  |  |  |  | 58958.93 | 70082 | 81577.14
6 | Transport charges upto 50 Km average lead from Area Store to construction camp including site transport (Transport Sch T-2) |  |  |  |  | 3895.9523 | 11229.9166 | 17519.132
7 | SUB TOTAL-2 |  |  |  |  | 919511.3885 | 2532957.8146 | 3558198.5955
8 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 97603.7125 | 280133.3125 | 395667.3063
9 | Total cost |  |  |  |  | 1017115.101 | 2813091.1271 | 3953865.9017
10 | Total Cost (Rounded off) |  |  |  |  | 1017115 | 2813091 | 3953866
Note: | All the rates are with considering price variation clause.

## B-3
COST SCHEDULE B-3
|  |  | ( 33 kV SUB-STATIONS ) |  |  |  |  | 2018-19
SCHEDULE FOR INSTALLATION OF ADDITIONAL TRANSFORMER FOR PARALLEL OPERATION WITH TWO ADDITIONAL BAY ON 11 kV SIDE
S. No. | S.No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | Sub-station capacity |  |  | Reason
[7 empty] | 1.6 MVA | 3.15 MVA | 5.0 MVA
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 |  | EQUIPMENTS
| i | Power Transformer 33/11 kV
|  | Power Transformer 1.6 MVA | 7132220091 | No | 780829.7 | 1 | 780829.7
|  | Power Transformer 3.15 MVA | 7132220095 | No | 2241066.5 | 1 |  | 2241066.5
|  | Power Transformer 5 MVA | 7132220097 | No | 3165338.45 | 1 |  |  | 3165338.45
| ii | 33 kV VCB with CT's and panels. |  | No | 333874.46
|  | (i) 33 kV VCB ( without CT's and panels) | 7131943380 | No | 235869.4 | 1 |  | 235869.4 | 235869.4
|  | (ii) 33 kV Control Panel | 7131960524 | No | 38863.78 | 1 |  | 38863.78 | 38863.78
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 19713.76 | 3 |  | 59141.28 | 59141.28
| iii | 11 kV VCB for X'mer protection with CT's and panels. |  | No | 197002.16 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | Each | 117747.13 | 1 | 117747.13 | 117747.13 | 117747.13
|  | (ii) 11 kV Control Panel for X-mer Protection | 7131960522 | Each | 38863.78 | 1 | 38863.78 | 38863.78 | 38863.78
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | Each | 13463.75 | 3 | 40391.25 | 40391.25 | 40391.25
| iv | 11 kV VCB for feeder protection with CT's and panels. |  | No | 364875.86 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | No | 117747.13 | 2 | 235494.26 | 235494.26 | 235494.26
|  | (ii) 11 kV Control Panel for feeder protection | 7131960008 | Each | 25950.06 | 2 | 51900.12 | 51900.12 | 51900.12
|  | (iii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 12913.58 | 6 | 77481.48 | 77481.48 | 77481.48
| v | 33 kV DO Fuse Unit | 7131930415 | Each | 2886.87 | 3 | 8660.61
| vi | 33 kV isolator, 600 A. Without earth switch | 7131930752 | No | 39152.26 | 3 | 117456.78 | 117456.78 | 117456.78
| vii | 11 kV isolator, 600 A | 7131930663 | No | 22623.4 | 5 | 113117 | 113117 | 113117
| viii | 33 kV Polymer Lightning Arrestor | 7130840021 | Each | 4545.92 | 3 | 13637.76 | 13637.76 | 13637.76
| ix | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 504.66 | 9 | 4541.94 | 4541.94 | 4541.94
| x | H.T. STATIC TRIVECTOR METERS |  | No | 10500.69
|  | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | 7131310033 | No | 3500.23 | 3 | 10500.69 | 10500.69 | 10500.69
| xi | 33 kV Single Phase PT | 7132230057 | Each | 16586.32 | 3 | 49758.96 | 49758.96 | 49758.96
| xii | 11 kV Single Phase PT | 7132230056 | Each | 10336.32 | 3 | 31008.96 | 31008.96 | 31008.96
| xiii | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 80471.17 | 1 | 80471.17 | 80471.17 | 80471.17
| xiv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 36485.4 | 2 | 72970.8 | 72970.8 | 72970.8
| xv | 33 kV AB switch | 7131930321 | Each | 18863.48 | 0 | 0 | 0 | 0
| xvi | 11 kV AB switch | 7131930221 | Each | 8496 | 2 | 16992 | 16992 | 16992
| xvii | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3036.33 | 5 | 15181.65 | 15181.65 | 15181.65
2 |  | STRUCTURE AND BUS BAR ARRANGEMENT
| (i) | DO fuse supporting structure set on 7 Mtr long H- Beam 37.1 kg/mtr 33 kV & 11 kV side (2 No. each side) i.e. 37.1 kg x 7 = 259.7 kg/pole x 4 Nos = 1038.8 Kgs | 7130601958 | Kg | 46.4039 | 1038.8 | 48204.3505 | 48204.3505 | 48204.3505
| (ii) | 33 kV additional bay ( 02 No H-Beam 152x152 mm 08 mtr long) with 6 Nos, 5.2 Mtr channel |  | Set | 123389.0863 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.20 Kgs | 7130601958 | Kg | 46.4039 | 1187.2 | 55090.6863 | 55090.6863 | 55090.6863
|  | (ii) D.C.Cross arm Channel 5.2 mtr 100x50 mm | 7130810684 | No | 8537.3 | 8 | 68298.4 | 68298.4 | 68298.4
| (iii) | 11 kV, 2 Addl. bus bar structure 08 mtr long H- Beam 37.1 Kg/mtr with 4 Nos, 5.2 Mtr long DC cross arm (100 x 50 mm) |  | Set | 384318.177 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.2 Kgs. | 7130601958 | Kg | 46.4039 | 1187.2 | 55090.6863 | 55090.6863 | 55090.6863
|  | (ii) H-Beam 152x152 mm 11 mtr long 37.1 kg/mtr i.e.= 408.1 kg/pole x 4 No = 1632.40 Kgs | 7130601958 | Kg | 46.4039 | 1632.4 | 75749.6937 | 75749.6937 | 75749.6937
|  | (iii) R.S. Joist (175x85 mm) [ 8x2 Mtr ] | 7130600675 | Kg | 44.9155 | 273 | 12261.937 | 12261.937 | 12261.937
|  | (iv) D.C.Cross arm Channel 5.2 mtr 100x50 mm (set) | 7130810684 | No | 8537.3 | 24 | 204895.2 | 204895.2 | 204895.2
|  | (v) D.C.Cross arm 5 ft. Centre 100x50 mm Channel | 7130810608 | Set | 5428.06 | 5 | 27140.3 | 27140.3 | 27140.3
|  | (vi) D.C.Cross arm 8 ft. Centre 100x50 mm Channel | 7130810517 | Set | 4590.18 | 2 | 9180.36 | 9180.36 | 9180.36
| (iv) | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 50.6744 | 300 | 15202.32 | 15202.32 | 15202.32
| (v) | ACSR Dog conductor | 7130830063 | Mtr | 66.185 | 300 | 19855.512 | 19855.512 | 19855.512
| (vi) | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 351.44 | 3 | 1054.32 | 1054.32 | 1054.32
| (vii) | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 142.14 | 6 | 852.84 | 852.84 | 852.84
| (viii) | Strain hardware with strain set suitable for Dog conductor: -
|  | (a) 33 kV side with 3 disc insulator per phase. |  | Set | 34922.88 | 18
|  | (i) 33 kV Polymer Disc insulator . | 7130820013 | No | 236.53 | 72 | 17030.16 | 17030.16 | 17030.16 | BIN CODE Changed. Old Bin 7130820011
|  | (ii) 33 kV Strain Hardware | 7130820248 | Each | 248.51 | 72 | 17892.72 | 17892.72 | 17892.72
|  | (b) 11 kV side with 2 disc insulator per phase. |  | Set | 9737.64
|  | (i) 11 kV Polymer Disc insulator | 7130820010 | No | 128.45 | 12 | 1541.4 | 1541.4 | 1541.4
|  | (ii) 11 kV Hardware | 7130820241 | No | 119.62 | 12 | 1435.44 | 1435.44 | 1435.44
|  | (iii) Strain plate 8 mm thick | 7130810624 | No | 93.9 | 72 | 6760.8 | 6760.8 | 6760.8
| (ix) | T-clamp for jumper connection with AB Switches & DO fuses / Isolator. | 7130830585 | No | 266.98 | 96 | 25630.08 | 25630.08 | 25630.08
| (x) | Stay Clamp for "H" Beam | 7130810692 | Pair | 322.98 | 42 | 13565.16 | 13565.16 | 13565.16
| (xi) | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 6 | 880.62 | 880.62 | 880.62 | NEW ROW ADDED
| (xii) | Aluminium Paint | 7130210809 | Ltr | 327.94 | 6 | 1967.64 | 1967.64 | 1967.64 | NEW ROW ADDED
3 |  | OTHER MISCELLANEOUS ITEMS
| i | Concreting of structure @ 0.45 Cmt. per bus structure (1:3:6) = 7.2 Cmt for 16 Nos structure. | 7130200202 | Kg | 2510.8 | 8.6 | 21592.88 | 21592.88 | 21592.88 | only material cost (excluding labour & G.S.T.)
| ii | Concreting of Transformer foundation (1:3:6) = 15 cmt | 7130200202 | Kg | 2510.8 | 15 | 37662 | 37662 | 37662 | only material cost (excluding labour & G.S.T.)
| iii | Concreting of 11 kV VCB foundation (1:3:6) = 18 cmt. | 7130200202 | Kg | 2510.8 | 18 | 45194.4 | 45194.4 | 45194.4 | only material cost (excluding labour & G.S.T.)
| iv | Concreting of 33 kV VCB foundation (1:3:6) = 7 cmt. | 7130200202 | Kg | 2510.8 | 7 | 17575.6 | 17575.6 | 17575.6 | only material cost (excluding labour & G.S.T.)
| v | Control cable for Xmer & VCB
|  | a) 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 119.1884 | 180 | 21453.9084 | 21453.9084 | 21453.9084
|  | b) 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 62.7585 | 720 | 45186.1488 | 45186.1488 | 45186.1488
|  | c) 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 36.2593 | 180 | 6526.6704 | 6526.6704 | 6526.6704
| vi | Earthing for addl X'mer & VCB
Document – As per W/o of G.S. Flat mesh earthing of 33/11 kV S/s as per No. CE/RR/TR/4328/9029 Raipur, Dt. 05/03/2007 (Rate taken from Sch.- III)
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4315.55 | 9 | 38839.95 | 38839.95 | 38839.95
|  | (ii) GI Pipe of 40 mm dia 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 849.08 | 24 | 20377.92 | 20377.92 | 20377.92
|  | (iii) MS flat 50x6 mm size | 7130600173 | Kg | 45.4764 | 400 | 18190.576 | 18190.576 | 18190.576
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 63 | 31 | 1952.9988 | 1952.9988 | 1952.9988
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 95.97 | 25 | 2399.25 | 2399.25 | 2399.25
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 95.97 | 10 | 959.7 | 959.7 | 959.7
|  | (vii) GI Spring washers | 7130622922 | Kg | 149.07 | 5 | 745.35 | 745.35 | 745.35
| vii | M.S. Nut- Bolts |  | Kg |  | 213
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 69.38 | 10 | 693.8 | 693.8 | 693.8
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 68.22 | 8 | 545.76 | 545.76 | 545.76
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 68.22 | 25 | 1705.5 | 1705.5 | 1705.5
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 67.06 | 70 | 4694.2 | 4694.2 | 4694.2
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 67.06 | 80 | 5364.8 | 5364.8 | 5364.8
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 67.06 | 20 | 1341.2 | 1341.2 | 1341.2
4 |  | SUB TOTAL - A (1+2+3) |  |  |  |  | 2849589.2782 | 4635039.9282 | 5559311.8782
5 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 256463.035 | 417153.5935 | 500338.069
|  | (i) Services on Earthing |  | No. | 11658 | 1 | 11658 | 11658 | 11658 | No. of earthing = 6; services on 6 earthing =6x1943=11658/-
|  | (ii) Services on Painting |  | No. | 16922.9018 | 1 | 16922.9018 | 16922.9018 | 16922.9018
|  | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete and including spreading in 100 mm thick layers complete (Metal measured in stacks will be reduced by 8% for voids). |  | Cmt | 1140 | 45 | 51300 | 51300 | 51300 | Earlier name was - Yard Metalling with 40 mm crusher broken metal
|  | Services on Labelling of equipments |  | No | 14102.418 | 1 | 14102.418 | 14102.418 | 14102.418
|  | Services on X'mer foundation [2.5(L)*2(W)*3(H)] |  | Cmt | 4266.6225 | 15 | 63999.3375 | 63999.3375 | 63999.3375
|  | Services on foundation of 11 kV VCB [2(L)*2(W)*1.5(H)] |  | Cmt | 4266.6225 | 18 | 76799.205 | 76799.205 | 76799.205
|  | Services on foundation of 33 kV VCB [2(L)*2(W)*1.75(H)] |  | Cmt | 4266.6225 | 7 | 29866.3575 | 29866.3575 | 29866.3575
|  | Construction of brick masonry cable trench with cover |  | RM | 2151.893 | 45 | 96835.185 | 96835.185 | 96835.185
6 |  | Labour charges: - |  |  |  |  | 229796.7392 | 240919.8092 | 252414.9492
| i | X'mer erection (Labour sch BL-3) |  |  |  |  | 58958.93 | 70082 | 81577.14
| ii | Other items as per schedule [Labour Schedule BL-2+(4*BL-4)] |  |  |  |  | 142706.02 | 142706.02 | 142706.02
| iii | Labour charges for concreting |  | Cmt | 578.8434 | 48.6 | 28131.7892 | 28131.7892 | 28131.7892
7 |  | Transport charges upto 50 Km lead from area stores to construction site for addl. lead refer Schedule T-2
| i | For Transformer only |  |  |  |  | 3780.8891 | 10845.615 | 15436.9493
| ii | For other material (Excluding Power Transformer) |  |  |  |  | 8841.2585 | 11045.8194 | 12549.9757
8 |  | SUB TOTAL-B |  |  |  |  | 3709954.6048 | 5676488.1702 | 6701535.2263
9 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 356198.6598 | 579379.991 | 694913.9848
10 |  | Grand Total cost of S/s. |  |  |  |  | 4066153.2646 | 6255868.1613 | 7396449.2111
11 |  | Grand Total cost of S/s. (Rounded off) |  |  |  |  | 4066153 | 6255868 | 7396449
Note: |  | (1) All the rates are with considering price variation clause.
(2) In case of non-availability of H-Beam for structure double welded RS Joist may be used and cost should be taken on actual material used
Note on C16: 89326879: Earlier name was - 33 kV CT's 200-100/5A
Note on C38: 89326879: Earlier name was - Marshelling Box
Note on C96: 89326879: Earlier name was - Yard Metalling with 40 mm crusher broken metal
Note on E49: 89326879: Earlier unit was - No.
Note on E101: 89326879: Earlier unit taken as Mtr
*

## B-4
COST SCHEDULE B-4
(33/11 kV SUB-STATIONS)
11 kV OUT DOOR YARD EXTENSION FOR ADDL. BAY WITH CIRCUIT BREAKER
2018-19
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | 1.6 MVA & Above
[6 empty] | Qnty | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | H-Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 No = 593.6 Kgs | 7130601958 | Kg | 46.4039 | 594 | 27563.9047
2 |  | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1 x 11 mtr = 408.1 kg/pole x 2 Nos = 816.2 Kgs. | 7130601965 | Kg | 46.4039 | 816.2 | 37874.8469
3 |  | MS DC Cross arm (100x50 mm), 5.2 Mtr long for bus bar | 7130810684 | Set | 8537.3 | 6 | 51223.8
4 |  | MS DC Cross arm (100x50 mm), 8' centre for bus bar | 7130810517 | Set | 4590.18 | 2 | 9180.36
5 |  | Strain set with hardware suitable for 100 Sqmm ACSR conductor for 11 kV bus. |  | Set |  | 21
| (i) | 11 kV Polymer Disc insulator for double disc | 7130820010 | No | 128.45 | 42 | 5394.9
| (ii) | Hardware suitable for 100 Sqmm ACSR Dog conductor for 11 kV bus. | 7130820248 | No | 248.51 | 21 | 5218.71
6 |  | 11 kV Polymeric Pin insulator with Pin | 7130820008 | Each | 142.14 | 3 | 426.42
7 |  | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 504.66 | 3 | 1513.98
8 |  | 11 kV Isolator (600 A.) | 7131930663 | Set | 22623.4 | 2 | 45246.8
9 |  | 11 kV AB Switch | 7131930221 | Each | 8496 | 1 | 8496
10 |  | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2510.8 | 1.8 | 4519.44 | only material cost (excluding labour & G.S.T.)
11 |  | ACSR 100 Sqmm Al. Eq. Dog Conductor | 7130830063 | Mtr | 66.185 | 50 | 3309.252
12 |  | Terminal clamp for jumpering of 100 Sqmm Al. Eq ACSR Conductor / Isolator | 7130830585 | No | 266.98 | 24 | 6407.52
13 |  | 11 kV feeder control VCB with CT's (One 11 kV VCB controlling two feeders) with control panel. |  | No | 187124.77 | 1
| (i) | 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 117747.13 | 1 | 117747.13
| (ii) | 11 kV feeder Control Panel | 7131960008 | No | 25950.06 | 1 | 25950.06
| (iii) | 11 kV CT's 300-150/5 Amps | 7132230188 | No | 13463.75 | 3 | 40391.25
| (iv) | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3036.33 | 1 | 3036.33
14 |  | Concreting of foundation of VCB (1:3:6) | 7130200202 | Cmt | 2510.8 | 6 | 15064.8 | only material cost (excluding labour & G.S.T.)
15 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 119.1884 | 60 | 7151.3028
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 62.7585 | 120 | 7531.0248
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 36.2593 | 60 | 2175.5568
16 |  | H.T. STATIC TRIVECTOR METER for feeder metering. |  | No | 3500.23 | 1
|  | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | 7131310033 | No | 3500.23 | 1 | 3500.23
17 |  | 11 kV CT/PT unit 200-100/5 Amp. | 7132230412 | Each | 36485.4 | 1 | 36485.4
18 |  | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 2 | 293.54 | NEW ROW ADDED
19 |  | Aluminium Paint | 7130210809 | Ltr | 327.94 | 2 | 655.88 | NEW ROW ADDED
20 |  | M.S. Nuts & Bolts |  | Kg |  | 30
| a | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 69.38 | 3 | 208.14
| b | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 68.22 | 2 | 136.44
| c | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 68.22 | 2 | 136.44
| d | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 67.06 | 6 | 402.36
| e | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 67.06 | 15 | 1005.9
| f | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 67.06 | 2 | 134.12
21 |  | SUB TOTAL-1 |  |  |  |  | 468381.838
22 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 42154.3654
23 | a | Services on Painting of structure |  | No | 3948.6771 | 1 | 3948.6771
| b | Construction of brick masonry cable trench with cover |  | RM | 2151.893 | 5 | 10759.465
24 |  | Labour charges |  |  |  |  | 32606.8285
| i | as per Schedule No. BL-4 |  |  |  |  | 28091.85
| ii | for concreting of structure |  | Cmt | 578.8434 | 1.8 | 1041.9181
| iii | for foundation of VCB |  | Cmt | 578.8434 | 6 | 3473.0604
25 |  | Transport charges upto 50 Km lead from area stores to construction site for addl. lead refer Schedule T-2. |  |  |  |  | 4399.9221
26 |  | SUB TOTAL-2 |  |  |  |  | 562251.0961
27 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 58547.7297
28 |  | Total cost: - |  |  |  |  | 620798.8259
29 |  | Total cost (Rounded off): - |  |  |  |  | 620799
Note :- |  | All the rates are with considering price variation clause.
Note on C29: 89326879: Earlier name was - Marshelling Box
Note on E50: 89326879: Earlier unit taken as Mtr

## B-5
COST SCHEDULE B-5
| (33/11 kV SUB-STATIONS) |  |  |  | 2018-19
33 kV OUT DOOR YARD EXTENSION FOR ADDITIONAL BAY.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 Nos = 593.6 Kgs | 7130601958 | Kg | 46.4039 | 593.6 | 27545.3432
2 | MS DC cross arm (100x50 mm), 5.2 Mtr. long for bus bar | 7130810684 | Set | 8537.3 | 6 | 51223.8
3 | Strain set with hardware suitable for 80 Sqmm ACSR conductor for 33 kV bus (3 disc insulator per disc) |  | Set | 14371.5 | 15
| (i) 33 kV Polymer Disc Insulator | 7130820013 | No | 236.53 | 45 | 10643.85 | BIN CODE Changed. Old Bin 7130820011
| (ii) 33 kV Hardware | 7130820248 | Each | 248.51 | 15 | 3727.65
4 | 33 kV Isolator (600 Amps.) without earth switch | 7131930752 | No | 39152.26 | 2 | 78304.52 | BIN CODE Changed. Old Bin 7131930109
5 | Terminal clamp for isolators | 7130830585 | No | 266.98 | 12 | 3203.76
6 | T-clamps for bus jumper | 7130830585 | No | 266.98 | 6 | 1601.88
7 | ACSR 100 Sqmm Al. Eq. Conductor | 7130830063 | Mtr | 66.185 | 50 | 3309.252
8 | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2510.8 | 0.9 | 2259.72 | only material cost (excluding labour & G.S.T.)
9 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | Each | 351.44 | 6 | 2108.64
10 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 2 | 293.54 | NEW ROW ADDED
11 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 2 | 655.88 | NEW ROW ADDED
12 | M.S. Nuts & Bolts |  | Kg |  | 40
| MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 69.38 | 2 | 138.76
| MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 68.22 | 3 | 204.66
| MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 68.22 | 5 | 341.1
| MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 67.06 | 15 | 1005.9
| MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 67.06 | 10 | 670.6
| MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 67.06 | 5 | 335.3
13 | SUB TOTAL-1 |  |  |  |  | 187574.1552
14 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 16881.674
15 | Services on Painting on structure |  | No | 3948.6771 | 1 | 3948.6771
16 | Labour charges as per Schedule No BL-5 |  |  |  |  | 21793.56
17 | Labour charges for concreting |  | Cmt | 578.8434 | 0.9 | 520.9591
18 | Transport charges upto 50 Km lead from Area stores to construction site for addl. lead refer Schedule T-2. |  |  |  |  | 4399.9221
19 | SUB TOTAL-2 |  |  |  |  | 235118.9474
20 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 23446.7694
21 | Total cost: - |  |  |  |  | 258565.7168
22 | Total cost (Rounded off): - |  |  |  |  | 258566
Note: -For the provision of 33 kV VCB installation, the cost Schedule No.- B-6 may be referred to. All the rates are with considering price variation clause
Note on B13: 89326879: Earlier name was - 33 kV Isolator (600 A.) with earth switch

## B-6
COST SCHEDULE B-6
2018-19
INSTALLATION OF 33 kV VCB
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | 33 kV VCB with control panel & CT |  | No | 350836.16 | 1
| (i) | 33 kV VCB (without CT's & Panel) | 7131943380 | No | 235869.4 | 1 | 235869.4
| (ii) | 33 kV Control Panel | 7131960524 | No | 38863.78 | 1 | 38863.78
| (iii) | 33 kV CT's 300-150/5 Amps | 7132230263 | No | 25367.66 | 3 | 76102.98
| (iv) | Marshelling Box (with 10 No. connectors) | 7130352046 | No | 3036.33 | 1 | 3036.33
2 |  | Concreting of foundation of 33 kV breaker (1:3:6) | 7130200202 | Cmt | 2510.8 | 7 | 17575.6 | only material cost (excluding labour & G.S.T.)
3 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 119.1884 | 60 | 7151.3028
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 62.7585 | 120 | 7531.0248
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 36.2593 | 60 | 2175.5568
4 |  | Terminal clamps | 7130830585 | No | 266.98 | 6 | 1601.88
5 |  | Tee clamp for jumper | 7130830585 | No | 266.98 | 6 | 1601.88
6 |  | SUB TOTAL-1 |  |  |  |  | 391509.7344
7 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 35235.8761
8 |  | Labour charges for concreting |  | Cmt | 578.8434 | 7 | 4051.9038
9 |  | Labour charges as per Schedule No BL-6 |  |  |  |  | 8245
10 |  | Transportation charges |  |  |  |  | 7531.2345
11 |  | SUB TOTAL-2 |  |  |  |  | 446573.7488
12 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 48938.7168
13 |  | Grand Total |  |  |  |  | 495512.4656
14 |  | Grand Total (Rounded off): - |  |  |  |  | 495512
Note on C11: 89326879: Earlier name was - Marshelling Box

## B-8
COST SCHEDULE B-8
AUGMENTATION OF 33/11 kV SUB-STATION CAPACITY BY REPLACEMENT OF POWER TRANSFORMER
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | 1.6 to 3.15 MVA |  | 3.15 to 5.0 MVA without 33 kV VCB |  | 3.15 to 5.0 MVA with 33 kV VCB
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 33/11 kV 3.15 MVA X-mer | 7132220095 | No | 2241066.5 | 1 | 2241066.5 | -- | -- | -- | --
2 | 33/11 kV 5.0 MVA X-mer | 7132220097 | No | 3165338.45 | -- | -- | 1 | 3165338.45 | 1 | 3165338.45
3 | 33 kV VCB (With CT's and control panel) |  | No |  | 1 |  | -- | -- | 1
| (i) 33 kV VCB (without CT's and panels) | 7131943380 | No | 235869.4 | 1 | 235869.4 |  |  | 1 | 235869.4
| (ii) 33 kV Control Panel | 7131960524 | No | 38863.78 | 1 | 38863.78 |  |  | 1 | 38863.78
| (iii) 33 kV CT's (300-150/5) Amps | 7132230263 | No | 25367.66 | 3 | 76102.98 |  |  | 3 | 76102.98
4 | Concreting of foundation for 33 kV VCB (1:3:6) | 7130200202 | Cmt | 2510.8 | -- | -- | -- | -- | 7 | 17575.6 | only material cost (excluding labour & G.S.T.)
5 | Control cabling
a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 119.1884 | 60 | 7151.3028 | 60 | 7151.3028 | 60 | 7151.3028
b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 62.7585 | 120 | 7531.0248 | 120 | 7531.0248 | 120 | 7531.0248
c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 36.2593 | 60 | 2175.5568 | 60 | 2175.5568 | 60 | 2175.5568
6 | Terminal clamp for transformer | 7130830586 | No | 213.35 |  |  |  |  | 7 | 1493.45
7 | T-clamps for jumper | 7130830586 | No | 213.35 | -- | -- | -- | -- | 3 | 640.05
8 | SUB TOTAL-1 |  |  |  |  | 2608760.5444 |  | 3182196.3344 |  | 3552741.5944
9 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 234788.449 |  | 286397.6701 |  | 319746.7435
10 | Labour charges as per Schedule No BL-8 |  |  |  |  | 78327 |  | 78327 |  | 78327
11 | Labour charges for concreting |  | Cmt | 578.8434 | -- | -- | -- | -- | 7 | 4051.9038
12 | Transport charges for transformer upto 50 Kms lead |  |  |  |  | 12803.9422 |  | 22989.1099 |  | 22989.1099
13 | Transport charges for VCB |  |  |  |  | 7531.2345 |  | 0 |  | 7531.2345
14 | SUB TOTAL-2 |  |  |  |  | 2942211.1701 |  | 3569910.1144 |  | 3985387.5861
15 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 326095.0681 |  | 397774.5418 |  | 444092.6993
16 | (-) Cost of Old Transformer assuming 25 years of life & 5 years in service. |  |  |  |  | 584300.84 |  | 1491844.86 |  | 1491844.86
17 | Net cost of Augmentation |  |  |  |  | 2684005.3981 |  | 2475839.7962 |  | 2937635.4254
18 | Net cost of Augmentation (Rounded off) |  |  |  |  | 2684005 |  | 2475840 |  | 2937635
Note:- All the rates are with considering price variation clause.

## B-9
COST SCHEDULE B-9
INSTALLATION OF 1.6 MVA 33/11 kV SUB-STATION ON LINE
2018-19
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | CIVIL WORKS (Rate as per SoR PWD)
| 1 | Land |  | Sq Mtr | LS
| 2 | Construction of 1.5 Mtr high barbed wire fencing in angle iron post as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Mtr | 406 | 32 | 12992
| 3 | Construction of 4.50 m x 2.15 m size yard / area gate as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Each | 35276 | 1 | 35276
|  | Total of 01 : - |  |  |  |  | 48268
2 |  | EQUIPMENTS AND BUS BAR ARRANGEMENT
| 1 | Power Transformer 1.6 MVA | 7132220091 | No | 780829.7 | 1 | 780829.7
| 2 | PCC supports 280 Kg; 9.0 Mtr. long | 7130800033 | No | 4402.65 | 2 | 8805.3
| 3 | 33 kV "V" cross arm | 7130810595 | No | 2354.14 | 2 | 4708.28
|  | (i) Cross arm clamp | 7130810361 | Pair | 309.8 | 2 | 619.6
| 4 | 33 kV Top clamp | 7130810676 | No | 391.69 | 5 | 1958.45
| 5 | 33 kV A.B. Switch | 7131930321 | Set | 18863.48 | 1 | 18863.48
| 6 | 33 kV D.O. Fuse Unit | 7131930415 | Each | 2886.87 | 3 | 8660.61
| 7 | 33 kV Polymer Lightning Arrestor | 7130840021 | Each | 4545.92 | 3 | 13637.76
| 8 | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 351.44 | 9 | 3162.96
| 9 | MS Channel 100x50 mm, 5.2 Mtr. Long for D.O., A.B. switch and LA mounting. | 7130810684 | Set | 8537.3 | 2 | 17074.6
| 10 | PCC supports 140 Kg; 8.0 Mtr. for 11 kV Bus | 7130800012 | No | 2255.2 | 8 | 18041.6
| 11 | MS Channel 5.2 Mtr. long | 7130810684 | No | 8537.3 | 16 | 136596.8
| 12 | 11 kV AB Switch complete | 7131930221 | Each | 8496 | 3 | 25488
| 13 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 504.66 | 3 | 1513.98
| 14 | 11 kV Strain set with hardware |  | Set |  | 21
|  | 11 kV Polymer Disc insulator | 7130820010 | No | 128.45 | 21 | 2697.45
|  | 11 kV Hardware | 7130820241 | No | 119.62 | 21 | 2512.02
| 15 | ACSR Conductor 80 Sqmm Al. Eq. Raccoon Conductor | 7130830060 | Mtr. | 50.1858 | 20 | 1003.7158
| 16 | T-clamps for Raccoon Conductor | 7130830586 | No | 213.35 | 27 | 5760.45
| 17 | Bimetallic Clamps for Transformer & auto recloser | 7130830052 | No | 650.6 | 12 | 7807.2
| 18 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 5 | 733.85 | NEW ROW ADDED
| 19 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 5 | 1639.7 | NEW ROW ADDED
| 20 | M.S. Nut- Bolts |  | Kg |  | 125
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 69.38 | 2 | 138.76
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 68.22 | 2 | 136.44
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 68.22 | 25 | 1705.5
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 67.06 | 40 | 2682.4
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 67.06 | 50 | 3353
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 67.06 | 6 | 402.36
| 21 | M.S. Flat 50x6 mm | 7130600173 | Kg | 45.4764 | 100 | 4547.644
| 22 | Earthing of Sub-station |  |  | 14560.346
|  | (i) G.I. Pipe of 40 mm dia. 3.04 Mtr. long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | 7130642039 | No | 849.08 | 12 | 10188.96
|  | (ii) MS flat 50x6 mm size | 7130600173 | Kg | 45.4764 | 60 | 2728.5864
|  | (iii) G.I. Wire 8 SWG | 7130870043 | Kg | 63 | 10 | 629.9996
|  | (iv) G.I. Nuts and bolts 16x40 mm | 7130620133 | Kg | 95.97 | 5 | 479.85
|  | (v) G.I. Nuts and bolts 16x65 mm | 7130620140 | Kg | 95.97 | 4 | 383.88
|  | (vi) G.I. Spring washers | 7130622922 | Kg | 149.07 | 1 | 149.07
|  | Total of 02 : - |  |  |  |  | 1089641.9558
3 |  | Incidental Charges @ 9% : - |  |  | 0.09 |  | 98067.776
4 |  | Services On Earthing of sub-station. |  | No | 3043.5582 | 1 | 3043.5582
5 |  | Labour charges as per Schedule No BL-9 |  |  |  |  | 96697.16
6 |  | Transportation charges |  |  |  |  | 28815.5864
7 |  | SUB TOTAL-2 |  |  |  |  | 1316266.0364
8 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 136205.2445
9 |  | Total cost including Civil Works. |  |  |  |  | 1500739.2809
10 |  | Total Cost (Round off) : - |  |  |  |  | 1500739
Note:- All the rates are with considering price variation clause.
Note on C10: 89326879: Earlier name was - Fencing for Sub-station with barbed wire.
Note on C11: 89326879: Earlier name was - Iron gate on RCC column.
Note on E10: 89326879: Earlier unit was - RM
Note on E17: 89326879: Earlier unit was - No.

## C-1
COST SCHEDULE C-1
1 KM OF 11 kV LINE ON PCC POLE 140 KG 8.0 METER LONG WITH MAXIMUM OF 65 Mtrs SPAN USING RABBIT AND WEASEL CONDUCTOR
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Using RABBIT Conductor |  |  | Using WEASEL Conductor
|  |  |  | Qnty | Rate | Amount | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 140 Kg, 8.0 Mtr long PCC Poles | 7130800012 | No | 16 | 2255.2 | 36083.2 | 16 | 2255.2 | 36083.2
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 16 | 1057.95 | 16927.2 | 16 | 1057.95 | 16927.2
3 | Cross Arm Clamp | 7130810361 | Pair | 16 | 309.8 | 4956.8 | 16 | 309.8 | 4956.8
4 | 11 kV Top clamp angle type with cleat | 7130810679 | No | 16 | 296.79 | 4748.64 | 16 | 296.79 | 4748.64
5 | Earthing Set (Coil earth as per Drawing No :-G/007 | 7130870013 | No | 16 | 114.85 | 1837.6 | 16 | 114.85 | 1837.6
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 48 | 142.14 | 6822.72 | 48 | 142.14 | 6822.72
7 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 33.9486 | 105240.598
8 | ACSR conductor Weasel with 3% sag | 7130830055 | Mtr |  |  |  | 3100 | 20.6046 | 63874.353
9 | Jointing sleeves suitable for 80 Sq mm. Al. Eq. ACSR Raccoon Conductor | 7130830050 | No | 6 | 36.14 | 216.84 | 6 | 36.14 | 216.84
10 | (i) Stay set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 155.99 | 623.96 | 4 | 155.99 | 623.96
11 | Red Oxide Paint | 7130211158 | Ltr | 4 | 146.77 | 587.08 | 4 | 146.77 | 587.08
12 | Aluminium Paint | 7130210809 | Ltr | 4 | 327.94 | 1311.76 | 4 | 327.94 | 1311.76
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 32 | 76.075 | 2434.401 | 32 | 76.075 | 2434.401
14 | Danger Board | 7130880041 | Each | 16 | 89.74 | 1435.84 | 16 | 89.74 | 1435.84
15 | Binding wire and tape | 7130830006 | Kg | 3 | 155.45 | 466.35 | 3 | 155.45 | 466.35
16 | MS Nuts and Bolts |  | Kg | 18 |  |  | 18
| 16x90 mm | 7130620619 | Kg | 2 | 68.22 | 136.44 | 2 | 68.22 | 136.44
| 16x160 mm | 7130620627 | Kg | 16 | 67.06 | 1072.96 | 16 | 67.06 | 1072.96
17 | Guarding :- |  |  |  | 7179.3546 |  |  | 7179.3546
| (i) 11 kV Guarding Channel 100x50 mm set | 7130810511 | No | 1 | 2508.6 | 2508.6 | 1 | 2508.6 | 2508.6
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 63 | 2204.9986 | 35 | 63 | 2204.9986
| (iii) Stay Clamp | 7130810026 | Pair | 2 | 155.99 | 311.98 | 2 | 155.99 | 311.98
| (iv) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 70.4396 | 774.836 | 11 | 70.4396 | 774.836
| (v) Stay set 16 mm | 7130860032 | No | 2 | 441.23 | 882.46 | 2 | 441.23 | 882.46
| (vi) I- Bolt Big size | 7130620013 | No | 4 | 124.12 | 496.48 | 4 | 124.12 | 496.48
18 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. /pole and for stay set @ 02 Nos. per stay set. |  |  | 22 |  |  | 22
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 28 | 158 | 4424 | 28 | 158 | 4424 | NEW BIN CODE ALLOTED | RATE EXCLUDING G.S.T.
19 | SUB TOTAL-1 |  |  |  |  | 199820.3357 |  |  | 158454.0907
20 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 17983.8302 |  | 0.09 | 14260.8682
21 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 12 | 295.8177 | 3549.8118 | 12 | 295.8177 | 3549.8118
22 | Labour charges as per Sch No.- CL-1 |  |  |  |  | 39215.66 |  |  | 34897.9
23 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 9453.3841 |  |  | 9453.3841
24 | SUB TOTAL-2 |  |  |  |  | 270023.0218 |  |  | 220616.0547
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 24977.542 |  | 0.125 | 19806.7613
26 | Cost per Km for non-guaranteed works |  |  |  |  | 295000.5638 |  |  | 240422.8161
27 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 295001 |  |  | 240423
Note: - Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on D11: 89326879: Earlier unit was - No.
Note on D20: 89326879: Earlier unit was - No.
Note on D32: 89326879: earlier unit was - No.

## C-2
COST SCHEDULE C-2
11 kV DP STRUCTURE ON PCC POLE 140 KG 8 METER LONG (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg, 8.0 Mtr long PCC Poles | 7130800012 | No | 2 | 2255.2 | 4510.4
2 | DC Cross arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | Set | 1 | 3977.41 | 3977.41
3 | 11 kV Polymer Disc Insulator | 7130820010 | No. | 6 | 128.45 | 770.7
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 119.62 | 717.72
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 142.14 | 426.42
6 | Horizontal & Cross Bracing 4' Center with set of 4 back Clamps |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 41.7888 | 2173.0155
| (ii) Back Clamp for Pole | 7130810692 | No | 4 | 322.98 | 1291.92
7 | (i) Stay set 16 mm | 7130860032 | No | 6 | 441.23 | 2647.38
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per Stay | 7130860077 | Kg | 33 | 70.4396 | 2324.5081
| (iii) Stay Clamp | 7130810026 | Pair | 6 | 155.99 | 935.94
8 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay (1:3:6) | 7130200202 | Cmt | 1.8 | 2510.8 | 4519.44 | only material cost (excluding labour & G.S.T.)
9 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 114.85 | 229.7
10 | Red Oxide paint | 7130211158 | Ltr | 0.5 | 146.77 | 73.385
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 327.94 | 163.97
12 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 76.075 | 304.3001
13 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74
14 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | kg | 0.5 | 69.38 | 34.69
| 16x200 mm | 7130620631 | kg | 5.5 | 67.06 | 368.83
15 | SUB TOTAL-1 |  |  |  |  | 25559.4688
16 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 2300.3522
17 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 2 | 295.8177 | 591.6353
18 | Labour charges as per Sch. No - CL-2 |  |  |  |  | 8013.36
19 | Labour charges for concreting |  | Cmt | 1.8 | 578.8434 | 1041.9181
20 | Transport charges upto 50 Kms. average lead from Area stores to construction camp incl. site transport (Transport Sch T-1) |  |  |  |  | 3587.5921
21 | SUB TOTAL-2 |  |  |  |  | 41094.3265
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 3194.9336
23 | Cost per DP for non-guaranteed works |  |  |  |  | 44289.2601
24 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 44289
Note: | All the rates are with considering price variation clause.
Note on D19: 89326879: Earlier unit was - No.

## C-3
COST SCHEDULE C-3
2018-19
1 KM OF 11 kV LINE ON H-BEAM / PCC POLE SUPPORT WITH MAXIMUM OF 80 Mtrs SPAN USING RABBIT CONDUCTOR
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 12 Nos = 4897.2 Kgs | 7130601965 | Kg | 4897.2 | 46.4039 | 227249.0811
2 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No |  |  |  | 12 | 7605.2 | 91262.4
3 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 12 | 1057.95 | 12695.4 | 12 | 1057.95 | 12695.4
4 | Back Clamp for Cross Arm
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 12 | 322.98 | 3875.76
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 12 | 291.13 | 3493.56
5 | 11 kV Top clamp angle type with cleat | 7130810679 | No | 12 | 296.79 | 3561.48 | 12 | 296.79 | 3561.48
6 | Earthing Set (Coil earth as per Drawing No :- G/007 | 7130870013 | No | 12 | 114.85 | 1378.2 | 12 | 114.85 | 1378.2
7 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 36 | 142.14 | 5117.04 | 36 | 142.14 | 5117.04
8 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 33.9486 | 105240.598 | 3100 | 33.9486 | 105240.598
9 | Jointing sleeves suitable for 50 Sqmm Al Eq. ACSR Conductor | 7130830854 | No | 6 | 29.14 | 174.84 | 6 | 29.14 | 174.84
10 | (I) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (II) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 34 | 70.4396 | 2394.9478 | 34 | 70.4396 | 2394.9478
(III) Stay Clamp
| (i) Stay Clamp For "H" Beam | 7130810692 | No | 4 | 322.98 | 1291.92
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 4 | 291.13 | 1164.52
11 | Concreting of supports @ 0.6 Cmt. Per Pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC & @ 0.2 Cmt. Per Stay and @ 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt. | 9 | 2510.8 | 22597.2 | 7.8 | 2510.8 | 19584.24 | only material cost (excluding labour & G.S.T.)
12 | Red Oxide Paint | 7130211158 | Ltr | 3 | 146.77 | 440.31 | 1.7 | 146.77 | 249.509
13 | Aluminium Paint | 7130210809 | Ltr | 3 | 327.94 | 983.82 | 1.8 | 327.94 | 590.292
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 24 | 76.075 | 1825.8007 | 24 | 76.075 | 1825.8007
15 | Danger Board | 7130880041 | Each | 12 | 89.74 | 1076.88 | 12 | 89.74 | 1076.88
16 | Binding wire and tape | 7130830006 | Kg | 3 | 155.45 | 466.35 | 3.5 | 155.45 | 544.075
17 | MS Nuts and Bolts |  | Kg | 13 |  |  | 18
| 16x40 mm | 7130620609 | Kg | 0.5 | 69.38 | 34.69
| 16x65 mm | 7130620614 | Kg | 6 | 68.22 | 409.32
| 16x90 mm | 7130620619 | Kg |  |  |  | 3.5 | 68.22 | 238.77
| 16x140 mm | 7130620625 | Kg | 6.5 | 67.06 | 435.89
| 16x160 mm | 7130620627 | Kg |  |  |  | 14.5 | 67.06 | 972.37
18 | Guarding |  | LS
| (i) 11 kV Guarding Channel 100x50 mm | 7130810511 | No | 1 | 2508.6 | 2508.6 | 1 | 2508.6 | 2508.6
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 63 | 2204.9986 | 35 | 63 | 2204.9986
| (iii) Stay Clamp | 7130810026 | Pair | 2 | 155.99 | 311.98 | 2 | 155.99 | 311.98
| (iv) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 17 | 70.4396 | 1197.4739 | 17 | 70.4396 | 1197.4739
| (v) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 2 | 441.23 | 882.46 | 2 | 441.23 | 882.46
| (vi) I- Bolt Big Size | 7130620013 | No. | 4 | 124.12 | 496.48 | 4 | 124.12 | 496.48
19 | SUB TOTAL-1 |  |  |  |  | 400616.4401 |  |  | 260931.835
20 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 36055.4796 |  | 0.09 | 23483.8651
21 | Labour charges as per Sch No - CL-4 |  |  |  |  | 55260.79 |  |  | 56764.49
22 | Labour charges for concreting |  | Cmt | 9 | 578.8434 | 5209.5906 | 7.8 | 578.8434 | 4514.9785
23 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 9453.3841 |  |  | 9453.3841
24 | SUB TOTAL-2 |  |  |  |  | 506595.6844 |  |  | 355148.5527
25 | Overhead Charges @ 12.5 % [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 50077.055 |  | 0.125 | 32616.4794
26 | Cost per Km for non-guaranteed works |  |  |  |  | 556672.7394 |  |  | 387765.0321
27 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 556673 |  |  | 387765
Note: - Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
All the rates are with considering price variation clause.
Note on D39: 89326879: Earlier unit was - No.

## C-3 (A)
COST SCHEDULE C-3 (A)
2018-19
ADDITIONAL (MID SPAN) POLES FOR 11 kV LINE
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-BEAM 152X152 MM 37.10 Kg/MTR 11.0 MTR LONG
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole | 7130601965 | Kg | 408.1 | 46.4039 | 18937.4234
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 1 | 1057.95 | 1057.95
3 | Back Clamp for Cross Arm
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 1 | 322.98 | 322.98
4 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 1 | 296.79 | 296.79
5 | Earthing Set (Coil earth as per Drawing No:-G/007 | 7130870013 | No | 1 | 114.85 | 114.85
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 142.14 | 426.42
7 | Concreting of supports H-Beam @ 0.6 Cmt. Per Pole & @ 0.2 Cmt. Per Stay and 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt. | 0.65 | 2510.8 | 1632.02 | only material cost (excluding labour & G.S.T.)
8 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 76.075 | 152.1501
9 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74
10 | MS Nuts and Bolts
| 16x40 mm | 7130620609 | Kg | 0.25 | 69.38 | 17.345
| 16x65 mm | 7130620614 | Kg | 0.6 | 68.22 | 40.932
| 16x140 mm | 7130620625 | Kg | 0.55 | 67.06 | 36.883
11 | SUB TOTAL-1 |  |  |  |  | 23125.4835
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 2081.2935
13 | Labour charges as per Sch No. CL-4 (revised based on one pole) |  |  |  |  | 2690.7878
14 | Labour charges for concreting |  | Cmt | 0.65 | 578.8434 | 376.2482
15 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) - Taken 5% of |  |  |  |  | 472.6723
16 | SUB TOTAL-2 |  |  |  |  | 28746.4853
17 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 2890.6854
18 | Cost per pole for non-guaranteed works |  |  |  |  | 31637.1707
19 | Cost per Pole (Rounded off) |  |  |  |  | 31637

## C-3 (B)
COST SCHEDULE C-3 (B)
COST PER KM OF 11 kV LINE ON AERIAL BUNCHED CABLE (ABC) OF 35 & 70 SQ.MM. ON 11 MTR. LONG H - BEAM / 9.0 MTR LONG PCC POLE OF SPAN 35 MTRS.
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | "H" Beam 152x152mm 37.1 Kg/Mtr 11.0 Mtr long |  |  |  | 200 Kg; 9.0 Mtr long PCC Pole
[5 empty] | Using 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 29 Nos = 11835 Kgs | 7130601965 | Kg | 46.4039 | 11835 | 549189.9198 | 11835 | 549189.9198
2 | 200 Kg 9.0 Meter long PCC Pole | 7130800001 | No. | 3046.2 |  |  |  |  | 29 | 88339.8 | 29 | 88339.8
3 | 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm (incl. 6% sag) | 7130310057 | Km | 314067.63 | 1.06 | 332911.6878 |  |  | 1.06 | 332911.6878
4 | 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm (incl. 6% sag) | 7130310058 | Km | 444325.88 |  |  | 1.06 | 470985.4328 |  |  | 1.06 | 470985.4328
5 | 11 kV Termination kit 35-70 sqmm | 7130320048 | Set | 2464.11 | 9 | 22176.99 | 9 | 22176.99 | 9 | 22176.99 | 9 | 22176.99
6 | 11 kV AB Cable straight through jointing kit suitable for 35-70 sqmm | 7130310061 | Set | 3890.71 | 6 | 23344.26 | 6 | 23344.26 | 6 | 23344.26 | 6 | 23344.26
7 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 2334.43 | 16 | 37350.88 | 16 | 37350.88 | 16 | 37350.88 | 16 | 37350.88
8 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 2075.04 | 21 | 43575.84 | 21 | 43575.84 | 21 | 43575.84 | 21 | 43575.84
9 | Eye Hook | 7130893004 | No. | 176.78 | 40 | 7071.2 | 40 | 7071.2 | 40 | 7071.2 | 40 | 7071.2
10 | Stay set 16 mm | 7130860032 | No. | 441.23 | 12 | 5294.76 | 12 | 5294.76 | 12 | 5294.76 | 12 | 5294.76
11 | Stay wire 7/10 SWG 10 kg/stay | 7130860077 | Kg | 70.4396 | 120 | 8452.7568 | 120 | 8452.7568 | 120 | 8452.7568 | 120 | 8452.7568
12 | Earth spike | 7130870010 | No. | 764.89 | 29 | 22181.81 | 29 | 22181.81 | 29 | 22181.81 | 29 | 22181.81
13 | G.I. Wire 6 SWG | 7130870045 | Kg | 63 | 24 | 1511.999 | 24 | 1511.999 | 24 | 1511.999 | 24 | 1511.999
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 76.075 | 58 | 4412.3517 | 58 | 4412.3517 | 58 | 4412.3517 | 58 | 4412.3517
15 | Pole Clamp | 7130810077 | No. | 433.92 | 37 | 16055.04 | 37 | 16055.04 | 37 | 16055.04 | 37 | 16055.04
16 | Danger Board | 7130880041 | Each | 89.74 | 29 | 2602.46 | 29 | 2602.46 | 29 | 2602.46 | 29 | 2602.46
17 | Pad Connector | 7130880006 | No. | 139.39 | 3 | 418.17 | 3 | 418.17 | 3 | 418.17 | 3 | 418.17
18 | Concreting of Pole @ 0.65 Cmt per pole and 0.2 Cmt per stay | 7130200202 | Cmt. | 2510.8 | 21.25 | 53354.5 | 21.25 | 53354.5 | 2.4 | 6025.92 | 2.4 | 6025.92 | only material cost (excluding labour & G.S.T.)
19 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 8 | 1174.16 | 8 | 1174.16
20 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 8 | 2623.52 | 8 | 2623.52
21 | M.S.Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30 |  | 30
| 16x40 mm | 7130620609 | Kg | 69.38 | 12 | 832.56 | 12 | 832.56 | 12 | 832.56 | 12 | 832.56
| 16x65 mm | 7130620614 | Kg | 68.22 | 12 | 818.64 | 12 | 818.64 | 12 | 818.64 | 12 | 818.64
| 16x140 mm | 7130620625 | Kg | 67.06 | 6 | 402.36 | 6 | 402.36 | 6 | 402.36 | 6 | 402.36
22 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130820029 | No. | 32.16 | 530 | 17044.8 | 530 | 17044.8 | 530 | 17044.8 | 530 | 17044.8
23 | SUB TOTAL-1 |  |  |  |  | 1152800.6652 |  | 1290874.4102 |  | 640824.2854 |  | 778898.0304
24 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 103752.0599 | 0.09 | 116178.6969 | 0.09 | 57674.1857 | 0.09 | 70100.8227
25 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No. | 295.8177 |  |  |  |  | 29 | 8578.7119 | 29 | 8578.7119
26 | Labour charges as per Sch No. CL-3(B) |  |  |  |  | 167275.32 |  | 167275.32 |  | 150425.17 |  | 150425.17
27 | Labour charges for concreting |  | Cmt | 578.8434 | 21.25 | 12300.4222 | 21.25 | 12300.4222 | 2.4 | 1389.2242 | 2.4 | 1389.2242
28 | Transportation charges |  |  |  |  | 23633.1036 |  | 23633.1036 |  | 23633.1036 |  | 23633.1036
29 | SUB TOTAL-2 |  |  |  |  | 1459761.5709 |  | 1610261.9529 |  | 882524.6808 |  | 1033025.0628
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 144100.0831 |  | 161359.3013 |  | 80103.0357 |  | 97362.2538
31 | Total Cost per Km including labour charges |  |  |  |  | 1603861.654 |  | 1771621.2542 |  | 962627.7164 |  | 1130387.3166
32 | Total Cost (Round off) |  |  |  |  | 1603862 |  | 1771621 |  | 962628 |  | 1130387

## C-3 (C)
COST SCHEDULE C-3 (C)
SCHEDULE FOR AUGMENTATION OF 1 kM OF 11 kV LINE FROM WEASEL TO RACCOON CONDUCTOR
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty | Rate | Amount
1 | Raccoon Conductor | 7130830060 | Km | 3.03 | 50185.79 | 152062.9437
2 | 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2508.6 | 2508.6
3 | G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 63 | 2204.9986
4 | Stay Clamp | 7130810026 | Pair | 2 | 155.99 | 311.98
5 | Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 70.4396 | 774.836
6 | Stay set 16 mm | 7130860032 | No | 2 | 441.23 | 882.46
7 | I-Bolt Big size | 7130620013 | No | 4 | 124.12 | 496.48
8 | Material Cost |  |  |  |  | 159242.2983
9 | Dismantling Charges |  | Ckt Km | 1 | 5630.6257 | 5630.6257
10 | Stringing Charges as per Labour Rate Schedule AL-1 |  | Ckt Km | 1 | 11261.2514 | 11261.2514
11 | SUB TOTAL-1 |  |  |  |  | 176134.1754
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 15852.0758
13 | Transportation charges |  |  |  |  | 3601.947
14 | SUB TOTAL-2 |  |  |  |  | 195588.1983
15 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 22016.7719
16 | Cost per Km |  |  |  |  | 217604.9702
17 | Total Cost (Round off) |  |  |  |  | 217605
Note on D10: 89326879: Earlier unit was - No.

## C-3 (D)
COST SCHEDULE C-3 (D)
SCHEDULE FOR AUGMENTATION OF 1 kM OF 11 kV LINE FROM WEASEL TO RABBIT CONDUCTOR
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty | Rate | Amount
1 | Rabbit Conductor | 7130830057 | Km | 3.03 | 33948.58 | 102864.1974
2 | 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2508.6 | 2508.6
3 | G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 63 | 2204.9986
4 | Stay Clamp | 7130810026 | Pair | 2 | 155.99 | 311.98
5 | Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 70.4396 | 774.836
6 | Stay set 16 mm | 7130860032 | No | 2 | 441.23 | 882.46
7 | I-Bolt Big size | 7130620013 | No. | 4 | 124.12 | 496.48
8 | Material Cost |  |  |  |  | 110043.552
9 | Dismantling Charges |  | Ckt Km | 1 | 5210.8684 | 5210.8684
10 | Stringing Charges as per Labour Rate Schedule CL-1 |  | Ckt Km | 1 | 10421.7368 | 10421.7368
11 | SUB TOTAL-1 |  |  |  |  | 125676.1572
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 11310.8542
13 | Transportation charges |  |  |  |  | 3601.947
14 | SUB TOTAL-2 |  |  |  |  | 140588.9584
15 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 15709.5197
16 | Cost per Km |  |  |  |  | 156298.4781
17 | Total Cost (Round off) |  |  |  |  | 156298
Note on D10: 89326879: Earlier unit was - No.

## C-3 (E)
COST SCHEDULE C-3 (E)
2018-19
COST PER KM OF 11 kV OVERHEAD XLPE CABLE LINE ON H - BEAM POLE WITH AVERAGE SPAN 30 MTRS.
Assumed as if cable length is 500 Mtr. in one stroke.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 33 Nos = 13467.3 Kgs | 7130601965 | Kg | 13467.3 | 46.4039 | 624934.9731
2 | 11 kV XLPE 3 Core Cable 120 sqmm (incl. sag 6%) | 7130310078 | Mtr. | 1060 | 792.3696 | 839911.776
3 | 11 kV Heat Shrinkable Type Straight Through jointing kit for 150 sqmm XLPE Cable | 7130352040 | Set | 42 | 18210.23 | 764829.66
4 | 11 kV Straight thru' joint kit suitable for 120 sqmm Cable | 7130310062 | Set | 4 | 4094.35 | 16377.4
5 | Earth spike | 7130870010 | No. | 6 | 764.89 | 4589.34
6 | D.C.Cross Arm 5.2 Mtr. Channel | 7130810684 | Set | 2 | 8537.3 | 17074.6
7 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 2 | 2334.43 | 4668.86
8 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 31 | 2075.04 | 64326.24
9 | Eye Hook | 7130893004 | No. | 33 | 176.78 | 5833.74
10 | Stay set without stay wire 20 mm | 7130860033 | No. | 12 | 803.97 | 9647.64
11 | Stay wire 7/8 SWG 10 kg/stay | 7130860076 | Kg | 120 | 69.7564 | 8370.7692
12 | Stay clamp for H-Beam | 7130810692 | No. | 24 | 322.98 | 7751.52
13 | Clamp for H-Beam | 7130810692 | No. | 33 | 322.98 | 10658.34
14 | M.S.Angle 65x65x6 mm | 7130600032 | Kg | 330 | 41.7888 | 13790.2908
15 | Red Oxide Paint | 7130211158 | Ltr | 3 | 146.77 | 440.31
16 | Aluminium Paint | 7130210809 | Ltr | 3 | 327.94 | 983.82
17 | Earthing Coil | 7130870013 | No. | 33 | 114.85 | 3790.05
18 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 66 | 76.075 | 5020.952
19 | Danger Board | 7130880041 | No. | 33 | 89.74 | 2961.42
20 | Concreting of Pole @ 0.65 Cmt per pole and 0.3 Cmt per stay | 7130200202 | Cmt | 25.05 | 2510.8 | 62895.54 | only material cost (excluding labour & G.S.T.)
21 | M.S.Nuts and Bolts |  | Kg | 40
| 16x65 mm | 7130620614 | Kg | 26 | 68.22 | 1773.72
| 16x200 mm | 7130620631 | Kg | 14 | 67.06 | 938.84
22 | SUB TOTAL-1 |  |  |  |  | 2471569.8011
23 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 222441.2821
24 | Labour charges 7% of material cost |  |  |  |  | 320723.1723
25 | Labour charges for concreting |  | Cmt | 25.05 | 578.8434 | 14500.0272
26 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) | 3% of material cost |  |  |  | 106829.5851
27 | Service in lieu of Earthing Coal & Salt etc |  | No. | 33 | 2628.1669 | 86729.5091
28 | SUB TOTAL-2 |  |  |  |  | 3222793.3768
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 308946.2251
30 | Total Cost per Km including labour charges |  |  |  |  | 3531739.602
31 | Total Cost (Round off) |  |  |  |  | 3531740
Note on B10: 89326879: Earlier name was - 11 kV End Termination kit for XLPE Cable 150 sqmm

## C-4
COST SCHEDULE C-4
11 kV DP STRUCTURE ON H-BEAM / PCC POLE SUPPORT (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 46.4039 | 37874.8469
2 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No |  |  |  | 2 | 7605.2 | 15210.4
3 | DC Cross Arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | No | 1 | 3977.41 | 3977.41 | 1 | 3977.41 | 3977.41
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 6 | 128.45 | 770.7 | 6 | 128.45 | 770.7
5 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 119.62 | 717.72 | 6 | 119.62 | 717.72
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 3 | 142.14 | 426.42 | 3 | 142.14 | 426.42
7 | Horizontal & Cross Bracing 4' center with set of 4 back clamp |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 41.7888 | 2173.0155 | 52 | 41.7888 | 2173.0155
Back Clamp for Pole
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 322.98 | 1291.92
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 4 | 291.13 | 1164.52
8 | (I) Stay set 16 mm | 7130860032 | No | 6 | 441.23 | 2647.38 | 6 | 441.23 | 2647.38
| (II) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 51 | 70.4396 | 3592.4216 | 51 | 70.4396 | 3592.4216
(III) Stay Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 6 | 322.98 | 1937.88
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 6 | 291.13 | 1746.78
9 | Concreting of pole @ 0.6 Cmt Per Pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC & @ 0.2 Cmt per stay and @ 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt | 2.5 | 2510.8 | 6277 | 2.3 | 2510.8 | 5774.84 | only material cost (excluding labour & G.S.T.)
10 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 114.85 | 229.7 | 2 | 114.85 | 229.7
11 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 146.77 | 73.385 | 0.5 | 146.77 | 73.385
12 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 327.94 | 163.97 | 0.5 | 327.94 | 163.97
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001
14 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
15 | MS Nuts and Bolts |  | Kg | 6 |  |  | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 69.38 | 34.69 | 0.5 | 69.38 | 34.69
| 16x200 mm | 7130620631 | Kg | 5.5 | 67.06 | 368.83 | 5.5 | 67.06 | 368.83
16 | SUB TOTAL-1 |  |  |  |  | 62951.3291 |  |  | 39466.2223
17 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 5665.6196 |  | 0.09 | 3551.96
18 | Labour charges for concreting |  | Cmt | 2.5 | 578.8434 | 1447.1085 | 2.3 | 578.8434 | 1331.3398
19 | Labour charges as per Sch No.- CL-5 |  |  |  |  | 10042.69 |  |  | 10281.71
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 3587.5921 |  |  | 3587.5921
21 | SUB TOTAL-2 |  |  |  |  | 83694.3394 |  |  | 58218.8242
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 7868.9161 |  | 0.125 | 4933.2778
23 | Cost per DP for non-guaranteed works |  |  |  |  | 91563.2555 |  |  | 63152.102
24 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 91563 |  |  | 63152
Note: | All the rates are with considering price variation clause.

## C-5
COST SCHEDULE C-5
1 kM OF 11 kV LINE ON 175x85 MM R.S. JOIST WITH MAXIMUM OF 65 Mtrs. SPAN USING RABBIT AND WEASEL CONDUCTOR
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Using RABBIT Conductor |  |  | Using WEASEL Conductor
|  |  |  | Qnty | Rate | Amount | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | R.S. Joist (175X85) mm 11 Mtr. Long i.e. 19.495 kg/mtr x 11 Mtr = 214.44 kg x 12 No = 2573.28 Kgs | 7130600675 | Kg | 2573 | 44.9155 | 115567.633 | 2573 | 44.9155 | 115567.633
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 12 | 1057.95 | 12695.4 | 12 | 1057.95 | 12695.4
3 | Back Clamp for Cross Arm | 7130810361 | Pair | 12 | 309.8 | 3717.6 | 12 | 309.8 | 3717.6
4 | 11 kV Top clamp Angle type with cleat | 7130810679 | No | 12 | 296.79 | 3561.48 | 12 | 296.79 | 3561.48
5 | Earthing Set (Coil earth as per Drawing No:-G/007) | 7130870013 | No | 12 | 114.85 | 1378.2 | 12 | 114.85 | 1378.2
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 36 | 142.14 | 5117.04 | 36 | 142.14 | 5117.04
7 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 33.9486 | 105240.598
8 | ACSR conductor Weasel with 3% sag | 7130830055 | Mtr |  |  |  | 3100 | 20.6046 | 63874.353
9 | Jointing sleeves suitable for 80 Sq.mm. Al Eq. ACSR Conductor | 7130830050 | No | 6 | 36.14 | 216.84 | 6 | 36.14 | 216.84
10 | (i) Stay set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 34 | 70.4396 | 2394.9478 | 34 | 70.4396 | 2394.9478
| (iii) Stay Clamp for R.S. Joist | 7130810216 | Pair | 4 | 309.8 | 1239.2 | 4 | 309.8 | 1239.2
11 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay & pole base padding @ 0.05 cmt/pole (1:3:6) | 7130200202 | Cmt | 5.4 | 2510.8 | 13558.32 | 5.4 | 2510.8 | 13558.32 | only material cost (excluding labour & G.S.T.)
12 | Red Oxide Paint | 7130211158 | Ltr | 2.5 | 146.77 | 366.925 | 2.5 | 146.77 | 366.925
13 | Aluminium Paint | 7130210809 | Ltr | 2.5 | 327.94 | 819.85 | 2.5 | 327.94 | 819.85
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 24 | 76.075 | 1825.8007 | 24 | 76.075 | 1825.8007
15 | Danger Board | 7130880041 | Each | 12 | 89.74 | 1076.88 | 12 | 89.74 | 1076.88
16 | Binding wire and tape | 7130830006 | Kg | 3 | 155.45 | 466.35 | 3 | 155.45 | 466.35
17 | MS Nuts and Bolts |  | Kg | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 5 | 69.38 | 346.9 | 5 | 69.38 | 346.9
| 16x65 mm | 7130620614 | Kg | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88
| 16x90 mm | 7130620619 | Kg | 5 | 68.22 | 341.1 | 5 | 68.22 | 341.1
18 | Guarding :-
| (i) 11 kV Guarding Channel 100x50 mm | 7130810511 | No | 1 | 2508.6 | 2508.6 | 1 | 2508.6 | 2508.6
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 63 | 2204.9986 | 35 | 63 | 2204.9986
| (iii) Stay Clamp | 7130810026 | Pair | 2 | 155.99 | 311.98 | 2 | 155.99 | 311.98
| (iv) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 17 | 70.4396 | 1197.4739 | 17 | 70.4396 | 1197.4739
| (v) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 2 | 441.23 | 882.46 | 2 | 441.23 | 882.46
| (vi) I- Bolt Big size | 7130620013 | No | 4 | 124.12 | 496.48 | 4 | 124.12 | 496.48
19 | SUB TOTAL-1 |  |  |  |  | 279570.8569 |  |  | 238204.6119
20 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 25161.3771 |  | 0.09 | 21438.4151
21 | Labour charges for concreting |  | Cmt | 5.4 | 578.8434 | 3125.7544 | 5.4 | 578.8434 | 3125.7544
22 | Labour charges as per Sch. No. CL-6 |  |  |  |  | 55260.78 |  |  | 54394.54
23 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) |  |  |  |  | 9453.3841 |  |  | 9453.3841
24 | SUB TOTAL-2 |  |  |  |  | 372572.1525 |  |  | 326616.7054
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 34946.3571 |  | 0.125 | 29775.5765
26 | Cost per Km for non-guaranteed works |  |  |  |  | 407518.5096 |  |  | 356392.2819
27 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 407519 |  |  | 356392
Note: - (1) Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
(2) All the rates are with considering price variation clause.
Note on D12: 89326879: Earlier unit was- No.
Note on D21: 89326879: Earlier unit was - No.
Note on D35: 89326879: Earlier unit was - No.

## C-6
2018-19
COST SCHEDULE C-6
11 kV DP STRUCTURE ON 175X85 MM R.S. JOIST (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
Sl. No. | PARTICULARS | New SAP Bin Code | Unit | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | R.S. Joist (175x85 mm) 11 Mtr Long i.e. 214.44 Kg/pole @ 19.495 Kg/Mtr. i.e.214.44x2 No pole=428.89 Kgs | 7130600675 | Kg | 428.89 | 44.9155 | 19263.8174
2 | DC Cross arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | Set | 1 | 3977.41 | 3977.41
3 | 11 kV Polymer Disc Insulator | 7130820010 | No. | 6 | 128.45 | 770.7
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 119.62 | 717.72
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 142.14 | 426.42
6 | Horizontal & Cross Bracing 4' Center with set of 4 back clamp |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 41.7888 | 2173.0155
| (ii) Back Clamp for Pole | 7130810216 | Pair | 4 | 309.8 | 1239.2
7 | (i) Stay set 16 mm | 7130860032 | No | 6 | 441.23 | 2647.38
| (ii) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 51 | 70.4396 | 3592.4216
| (iii) Stay Clamp for R.S. Joist | 7130810216 | Pair | 6 | 309.8 | 1858.8
8 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay & pole base padding @ 0.05 Cmt/pole (1:3:6) | 7130200202 | Cmt | 1.9 | 2510.8 | 4770.52 | only material cost (excluding labour & G.S.T.)
9 | Earthing Set (Coil earth as per Drawing No - G/007) | 7130870013 | No | 1 | 114.85 | 114.85
10 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 146.77 | 73.385
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 327.94 | 163.97
12 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 76.075 | 304.3001
13 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74
14 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 69.38 | 34.69
| 16x65 mm | 7130620614 | Kg | 2.5 | 68.22 | 170.55
| 16x200 mm | 7130620631 | Kg | 3 | 67.06 | 201.18
15 | SUB TOTAL-1 |  |  |  |  | 42590.0697
16 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 3833.1063
17 | Labour charges for concreting |  | Cmt | 1.9 | 578.8434 | 1099.8025
18 | Labour charges as per Sch. No. CL-7 |  |  |  |  | 10042.69
19 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 3587.5921
20 | SUB TOTAL-2 |  |  |  |  | 61153.2605
21 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 5323.7587
22 | Cost per DP for non-guaranteed works |  |  |  |  | 66477.0192
23 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 66477
Note: | All the rates are with considering price variation clause.
Note on D15: 89326879: Earlier unit was - No.
Note on D18: 89326879: Earlier unit was - No.

## C-7(A-1)
COST SCHEDULE C-7 (A-1)
2018-19
11/0.4 kV OUT DOOR SUB-STATION (USING PCC POLE FOR 25/63 kVA TRANSFORMER & DOUBLE WELDED R.S. JOIST 175x85 mm FOR 100/200 kVA TRANSFORMER AND SINGLE CORE PVC INSULATED CABLE)
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 49457.85 | 49457.85
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 89213.04 | 89213.04
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 117398.25 | 117398.25
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 220752.68 | 220752.68
2 | (i) 140 Kg 8.0 Mtr long PCC Pole | 7130800012 | No | 3 | 2255.2 | 6765.6 | 3 | 2255.2 | 6765.6 | -- | -- | -- | -- | -- | --
| (ii) 175x85 mm 11.0 Mtr long R.S. Joist @19.495 Kg/mtr x 9 mtr = 175.45 kg/pole x 2 No = 428.9 Kgs, For 4 No pole = 857.8 Kg | 7130600675 | Kg | [6 empty] | 857.78 | 44.9155 | 38527.6347 | 857.78 | 44.9155 | 38527.6347
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35
| 11 kV H.W. | 7130820241 | No. | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77
7 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | M.S. Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 155.99 | 623.96 | 4 | 155.99 | 623.96 | 4 | 155.99 | 623.96
10 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 1.85 | 2510.8 | 4644.98 | 1.85 | 2510.8 | 4644.98 | 1.85 | 2510.8 | 4644.98 | 1.85 | 2510.8 | 4644.98 | only material cost (excluding labour & G.S.T.)
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
13 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 76.075 | 456.4502 | 6 | 76.075 | 456.4502 | 8 | 76.075 | 608.6002 | 8 | 76.075 | 608.6002
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 146.77 | 146.77 | 1 | 146.77 | 146.77 | 3 | 146.77 | 440.31 | 3 | 146.77 | 440.31
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94 | 1 | 327.94 | 327.94 | 3 | 327.94 | 983.82 | 3 | 327.94 | 983.82
18 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38
| 16x65 mm | 7130620614 | Kg | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88
| 16x140 mm | 7130620625 | Kg | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24
| 16x200 mm | 7130620631 | Kg | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1814.36 | 1814.36 | -- |  |  | -- |  |  | --
21 | PVC insulated Single Core Armoured cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 18.1746 | 2180.9568 | -- | [5 empty] | -- |  |  | Old Bin Code - 7130311084
ii | 70 Sqmm | 7130311010 | Mtr | -- | -- | -- | 120 | 57.599 | 6911.88 | 120 | 57.599 | 6911.88 | -- | -- | -- | Old Bin Code - 7130311054
iii | 150 Sqmm | 7130311011 | Mtr | -- | -- | -- | -- | -- | -- | 40 | 110.4928 | 4419.7116 | 120 | 110.4928 | 13259.1348 | Old Bin Code - 7130311057
iv | 300 Sqmm | 7130311012 | Mtr | -- | -- | -- | -- | -- | -- | -- | -- | -- | 40 | 215.644 | 8625.7612 | Old Bin Code - 7130311061
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15292.16 | 15292.16 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19116 | 19116
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 38230.4 | 38230.4
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 |  |  |  |  | 93409.3715 |  |  | 151373.2847 |  |  | 229161.6511 |  |  | 361559.8255
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 8406.8434 |  | 0.09 | 13623.5956 |  | 0.09 | 20624.5486 |  | 0.09 | 32540.3843
26 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 295.8177 | 887.453 | 3 | 295.8177 | 887.453 | 0 | 0 | 0 | 0 | 0 | 0 |  | 192.6179
27 | Labour charges for concreting |  | Cmt | 1.85 | 578.8434 | 1070.8603 | 1.85 | 578.8434 | 1070.8603 | 1.85 | 578.8434 | 1070.8603 | 1.85 | 578.8434 | 1070.8603
28 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338
29 | Labour charges as per Sch CL-3 |  |  |  |  | 11448.9 |  |  | 12026.4 |  |  | 12026.4 |  |  | 14922.9
30 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 5437.7635 |  |  | 6019.9669 |  |  | 6019.9669 |  |  | 6019.9669
31 | SUB TOTAL-2 |  |  |  |  | 128545.7255 |  |  | 192886.0943 |  |  | 276787.9607 |  |  | 423998.4708
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 11676.1714 |  | 0.125 | 18921.6606 |  | 0.125 | 28645.2064 |  | 0.125 | 45194.9782
33 | Cost per S/s for non-guaranteed works |  |  |  |  | 140221.8969 |  |  | 211807.7549 |  |  | 305433.1671 |  |  | 469193.449
34 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 140222 |  |  | 211808 |  |  | 305433 |  |  | 469193
Note (A) :- (1) All the rates are with considering price variation clause.
(2) Single RS Joist 175x85 mm may be used in place of PCC pole for 25/63 kVA Transformer
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer
Note on B42: 89326879: Earlier name was - PVC insulated 4 Core cable
Note on B43: 89326879: Earlier name was - 16 Sqmm (Armoured)
Note on B44: 89326879: Earlier name was - 70 Sqmm (Armoured)
Note on C43: 89326879: Bin Code changed
Note on C44: 89326879: Bin Code changed
Note on C45: 89326879: Bin Code changed
Note on C46: 89326879: Bin Code changed
Note on D24: 89326879: Earlier unit was - No.
Note on E43: 89326879: Earlier Qty. was - 30
Note on H44: 89326879: Earlier Qty. was - 30
Note on K44: 89326879: Earlier Qty. was - 30
Note on K45: 89326879: Earlier Qty. was - 10
Note on N45: 89326879: Earlier Qty. was - 30
Note on N46: 89326879: Earlier Qty. was - 10

## C-7(A-2)
COST SCHEDULE C-7 (A-2)
2018-19
11/0.4 kV OUT DOOR SUB-STATION (USING PCC POLE FOR 25/63 kVA TRANSFORMER & DOUBLE WELDED RS JOIST 175x85 mm FOR 100/200 kVA TRANSFORMER AND SINGLE CORE CABLE)
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 49457.85 | 49457.85
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 89213.04 | 89213.04
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 117398.25 | 117398.25
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 220752.68 | 220752.68
2 | (i) 140 Kg 8.0 Mtr. long PCC Pole | 7130800012 | No | 3 | 2255.2 | 6765.6 | 3 | 2255.2 | 6765.6 | -- | -- | -- | -- | -- | --
| (ii) 175x85 mm 11.0 Mtr long R.S. Joist @ 19.495 Kg/mtr x 9 mtr = 175.45 kg/pole x 2 No = 428.9 Kgs, For 4 No pole = 857.8 Kg | 7130600675 | Kg | [6 empty] | 857.78 | 44.9155 | 38527.6347 | 857.78 | 44.9155 | 38527.6347
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35
5 | 11 kV H.W | 7130820241 | No | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84
7 | 11 kV DO fuse & LA mounting DC cross arm (75x40 mm) | 7130810509 | No | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77
8 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
9 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752
10 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 155.99 | 623.96 | 4 | 155.99 | 623.96 | 4 | 155.99 | 623.96
11 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 1.85 | 2510.8 | 4644.98 | 1.85 | 2510.8 | 4644.98 | 1.85 | 2510.8 | 4644.98 | 1.85 | 2510.8 | 4644.98 | only material cost (excluding labour & G.S.T.)
12 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178
13 | Transformer mounting Cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
14 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
15 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994
16 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 76.075 | 456.4502 | 6 | 76.075 | 456.4502 | 8 | 76.075 | 608.6002 | 8 | 76.075 | 608.6002
17 | Red Oxide Paint | 7130211158 | Ltr | 1 | 146.77 | 146.77 | 1 | 146.77 | 146.77 | 3 | 146.77 | 440.31 | 3 | 146.77 | 440.31
18 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94 | 1 | 327.94 | 327.94 | 3 | 327.94 | 983.82 | 3 | 327.94 | 983.82
19 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98
20 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38
| 16x65 mm | 7130620614 | Kg | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88
| 16x140 mm | 7130620625 | Kg | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24
| 16x200 mm | 7130620631 | Kg | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3
21 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1814.36 | 1814.36 | -- |  |  | -- |  |  | --
22 | Single Core cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 18.1746 | 2180.9568 | -- | [5 empty] | --
ii | 35 Sqmm | 7130310021 | Mtr |  |  |  | 80 | 28.1566 | 2252.5272
iii | 50 Sqmm | 7130311009 | Mtr |  |  |  | 40 | 42.7072 | 1708.2888 | 120 | 42.7072 | 5124.8664
iv | 70 Sqmm | 7130311010 | Mtr | -- | [5 empty] | 40 | 57.599 | 2303.96 | 120 | 57.599 | 6911.88
v | 150 Sqmm | 7130311011 | Mtr | -- | [8 empty] | 40 | 110.4928 | 4419.7116
23 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15292.16 | 15292.16 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19116 | 19116
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 38230.4 | 38230.4
24 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
25 | SUB TOTAL-1 |  |  |  |  | 93409.3715 |  |  | 148422.2207 |  |  | 225258.8859 |  |  | 351006.5211
26 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 8406.8434 |  | 0.09 | 13357.9999 |  | 0.09 | 20273.2997 |  | 0.09 | 31590.5869
27 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 295.8177 | 887.453 | 3 | 295.8177 | 887.453 | 0 | 0 | 0 | 0 | 0 | 0
28 | Labour charges for concreting |  | Cmt | 1.85 | 578.8434 | 1070.8603 | 1.85 | 578.8434 | 1070.8603 | 1.85 | 578.8434 | 1070.8603 | 1.85 | 578.8434 | 1070.8603
29 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338
30 | Labour charges as per Sch. CL-3 |  |  |  |  | 11448.9 |  |  | 12026.4 |  |  | 12026.4 |  |  | 14922.9
31 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 5437.7635 |  |  | 6019.9669 |  |  | 6019.9669 |  |  | 6019.9669
32 | SUB TOTAL-2 |  |  |  |  | 128545.7255 |  |  | 189669.4345 |  |  | 272533.9466 |  |  | 412495.369
33 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 11676.1714 |  | 0.125 | 18552.7776 |  | 0.125 | 28157.3607 |  | 0.125 | 43875.8151
34 | Cost per S/s for non-guaranteed works |  |  |  |  | 140221.8969 |  |  | 208222.2121 |  |  | 300691.3074 |  |  | 456371.1842
35 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 140222 |  |  | 208222 |  |  | 300691 |  |  | 456371
Note (A) :- (1) All the rates are with considering price variation clause.
(2) Single RS Joist175x85 mm may be used in place of PCC pole for 25/63 kVA Transformer
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer
Note on D24: 89326879: Earlier unit was - No.

## C-7(B-1)
COST SCHEDULE C-7 (B-1)
11/0.4 kV OUT DOOR SUB-STATION (USING H-BEAM POLE FOR 25 / 63 / 100 / 200 kVA TRANSFORMER AND SINGLE CORE PVC CABLE)
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 49457.85 | 49457.85
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 89213.04 | 89213.04
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 117398.25 | 117398.25
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 220752.68 | 220752.68
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35
| 11 kV H.W | 7130820241 | No. | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721
| (iii) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92
10 | Concreting of supports @ 0.6 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | only material cost (excluding labour & G.S.T.)
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
13 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
14 | Earthing set (Pipe earth as per drg. no.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 146.77 | 146.77 | 1 | 146.77 | 146.77 | 3 | 146.77 | 440.31 | 3 | 146.77 | 440.31
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94 | 1 | 327.94 | 327.94 | 3 | 327.94 | 983.82 | 3 | 327.94 | 983.82
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | kg | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38
| 16x65 mm | 7130620614 | kg | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88
| 16x140 mm | 7130620625 | kg | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24
| 16x200 mm | 7130620631 | kg | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1814.36 | 1814.36 | -- |  |  | -- |  |  | --
21 | PVC insulated Single Core Armoured cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 18.1746 | 2180.9568 | -- | [5 empty] | -- |  |  | Old Bin Code- 7130311084
ii | 70 Sqmm | 7130311010 | Mtr | -- |  |  | 120 | 57.599 | 6911.88 | 120 | 57.599 | 6911.88 | -- |  |  | Old Bin Code- 7130311054
iii | 150 Sqmm | 7130311011 | Mtr | -- | [5 empty] | 40 | 110.4928 | 4419.7116 | 120 | 110.4928 | 13259.1348 | Old Bin Code- 7130311057
iv | 300 Sqmm | 7130311012 | Mtr | [9 empty] | 40 | 215.644 | 8625.7612 | Old Bin Code- 7130311061
22 | LT Distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15292.16 | 15292.16 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19116 | 19116
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 38230.4 | 38230.4
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 |  |  |  |  | 125662.1283 |  |  | 183626.0415 |  |  | 229500.2231 |  |  | 362522.3575
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 11309.5915 |  | 0.09 | 16526.3437 |  | 0.09 | 20655.0201 |  | 0.09 | 32627.0122
26 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338
27 | Labour charges as per Sch. CL-3 |  |  |  |  | 11448.9 |  |  | 12026.4 |  |  | 12026.4 |  |  | 14922.9
28 | Labour charges for concreting |  | Cmt | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711
29 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 5437.7635 |  |  | 6019.9669 |  |  | 6019.9669 |  |  | 6019.9669
30 | SUB TOTAL-2 |  |  |  |  | 162958.4883 |  |  | 227298.8571 |  |  | 277301.715 |  |  | 425192.3415
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 15707.766 |  | 0.125 | 22953.2552 |  | 0.125 | 28687.5279 |  | 0.125 | 45315.2947
32 | Cost per S/s for non-guaranteed works |  |  |  |  | 178666.2543 |  |  | 250252.1123 |  |  | 305989.2429 |  |  | 470507.6362
33 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 178666 |  |  | 250252 |  |  | 305989 |  |  | 470508
Note (A) :- (1) All the rates are with considering price variation clause.
(2) As per requirement 315 kVA Transformer may be used against 200 kVA schedule
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer
Note on B42: 89326879: Earlier name was - PVC insulated 4 Core cable
Note on B43: 89326879: Earlier name was - 16 Sqmm (Armoured)
Note on B44: 89326879: Earlier name was - 70 Sqmm (Armoured)
Note on C43: 89326879: Bin Code changed
Note on C44: 89326879: Bin Code changed
Note on C45: 89326879: Bin Code changed
Note on C46: 89326879: Bin Code changed
Note on E43: 89326879: Earlier Qty. was - 30
Note on H44: 89326879: Earlier Qty. was - 30
Note on K44: 89326879: Earlier Qty. was - 30
Note on K45: 89326879: Earlier Qty. was - 10
Note on N45: 89326879: Earlier Qty. was - 30
Note on N46: 89326879: Earlier Qty. was - 10

## C-7 (B-1) A
COST SCHEDULE C-7 (B-1) A
RELOCATION OF 25 / 63 / 100 kVA 11/0.4 kV X-MER S/S USING H- BEAM POLE AND 3.5 CORE PVC CABLE [BASED ON COST SCHEDULE C-7 (B-1) EXCEPT TRANSFORMER COST ]
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | H-BEAM 152x152 mm; 37.1 Kg /Mtr; 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469
2 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
3 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35
4 | 11 kV H.W | 7130820241 | No. | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84
6 | 11 kV D.O. fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | kg | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721
| (iii) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92
10 | Concreting of supports @ 0.6 Cmt / pole & @ 0.2 Cmt / Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | only material cost (excluding labour & G.S.T.)
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
13 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001
16 | Red Oxide paint | 7130211158 | Ltr | 1 | 146.77 | 146.77 | 1 | 146.77 | 146.77 | 3 | 146.77 | 440.31 | 3 | 146.77 | 440.31
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94 | 1 | 327.94 | 327.94 | 3 | 327.94 | 983.82 | 3 | 327.94 | 983.82
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | kg | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38
| 16x65 mm | 7130620614 | kg | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88
| 16x140 mm | 7130620625 | kg | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24
| 16x200 mm | 7130620631 | kg | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1814.36 | 1814.36 | -- |  |  | -- |  |  | --
21 | PVC insulated Single Core Armoured cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 18.1746 | 2180.9568 | -- | [8 empty] | Old Bin Code- 7130311084
ii | 70 Sqmm | 7130311010 | Mtr | -- |  |  | 120 | 57.599 | 6911.88 | 120 | 57.599 | 6911.88 |  |  |  | Old Bin Code- 7130311054
iii | 150 Sqmm | 7130311011 | Mtr | -- | [5 empty] | 40 | 110.4928 | 4419.7116 | 120 | 110.4928 | 13259.1348 | Old Bin Code- 7130311057
iv | 300 Sqmm | 7130311012 | Mtr | [9 empty] | 40 | 215.644 | 8625.7612 | Old Bin Code- 7130311061
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15292.16 | 15292.16 | -- |  |  | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19116 | 19116
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 38230.4 | 38230.4
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 |  |  |  |  | 76204.2783 |  |  | 94413.0015 |  |  | 112101.9731 |  |  | 141769.6775
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 6858.385 |  | 0.09 | 8497.1701 |  | 0.09 | 10089.1776 |  | 0.09 | 12759.271
26 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338
27 | Labour charges as per Sch. CL-3 |  |  |  |  | 11448.9 |  |  | 12026.4 |  |  | 12026.4 |  |  | 14922.9
28 | Labour charges for concreting |  | Cmt | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711
29 | Transport charges upto 50 Kms average lead from Area stores to construction camp incl. site transport (Transport Sch T-1) |  |  |  |  | 5437.7635 |  |  | 6019.9669 |  |  | 6019.9669 |  |  | 6019.9669
30 | SUB TOTAL-2 |  |  |  |  | 109049.4318 |  |  | 130056.6435 |  |  | 149337.6225 |  |  | 184571.9203
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 9525.5348 |  | 0.125 | 11801.6252 |  | 0.125 | 14012.7466 |  | 0.125 | 17721.2097
32 | Cost per S/s for non-guaranteed works |  |  |  |  | 118574.9665 |  |  | 141858.2687 |  |  | 163350.3692 |  |  | 202293.13
33 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 118575 |  |  | 141858 |  |  | 163350 |  |  | 202293
Note on B38: 89326879: Earlier name was - PVC insulated 4 Core cable
Note on B39: 89326879: Earlier name was - 16 Sqmm (Armoured)
Note on B40: 89326879: Earlier name was - 70 Sqmm (Armoured)
Note on C39: 89326879: Bin Code changed
Note on C40: 89326879: Bin Code changed
Note on C41: 89326879: Bin Code changed
Note on C42: 89326879: Bin Code changed
Note on E39: 89326879: Earlier Qty. was - 30
Note on H40: 89326879: Earlier Qty. was - 30
Note on K40: 89326879: Earlier Qty. was - 30
Note on K41: 89326879: Earlier Qty. was - 10
Note on N41: 89326879: Earlier Qty. was - 30
Note on N42: 89326879: Earlier Qty. was - 10

## C-7 (B-1) B
COST SCHEDULE -- C-7 (B-1) B
|  |  | RENOVATION OF EXISTING DISTRIBUTION TRANSFORMERS | [13 empty] | 2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER |  |  | 315 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
1 | LT Distribution Box
| 25 kVA |  | No | 0 | 0 | 0
| 63 kVA | 7131950065 | No |  |  |  | 1 | 15292.16 | 15292.16
| 100 kVA | 7131950105 | No | [6 empty] | 1 | 19116 | 19116
| 200 kVA | 7131950200 | No | [9 empty] | 1 | 38230.4 | 38230.4
| 315 kVA | 7131950207 | No | [12 empty] | 1 | 32804 | 32804
2 | PVC insulated Single Core Armoured cable
| 25 kVA (70 sq mm) | 7130311010 | Mtr | 120 | 57.599 | 6911.88 | [12 empty] | Old Bin Code- 7130311054
| 63 kVA (70 sq mm) | 7130311010 | Mtr |  |  |  | 120 | 57.599 | 6911.88 | [9 empty] | Old Bin Code- 7130311054
| 100 kVA (70 sq mm) | 7130311010 | Mtr | [6 empty] | 120 | 57.599 | 6911.88 | [6 empty] | Old Bin Code- 7130311054
| 100 kVA (150 sq mm) | 7130311011 | Mtr | [6 empty] | 40 | 110.4928 | 4419.7116 | [6 empty] | Old Bin Code- 7130311057
| 200 kVA (150 sq mm) | 7130311011 | Mtr | [9 empty] | 120 | 110.4928 | 13259.1348 |  |  |  | Old Bin Code- 7130311057
| 200 kVA (300 sq mm) | 7130311012 | Mtr | [9 empty] | 40 | 215.644 | 8625.7612 |  |  |  | Old Bin Code- 7130311061
| 315 kVA (150 sq mm) | 7130311011 | Mtr | [12 empty] | 120 | 110.4928 | 13259.1348 | Old Bin Code- 7130311057
| 315 kVA (300 sq mm) | 7130311012 | Mtr | [12 empty] | 40 | 215.644 | 8625.7612 | Old Bin Code- 7130311061
3 | Earthing set (Pipe earth as per drg no. G/008) (Material + services)
| (i) GI Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994
4 | SUB TOTAL-1 |  |  |  |  | 9793.8594 |  |  | 25086.0194 |  |  | 33329.571 |  |  | 62997.2754 |  |  | 57570.8754
5 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 881.4473 |  | 0.09 | 2257.7417 |  | 0.09 | 2999.6614 |  | 0.09 | 5669.7548 |  | 0.09 | 5181.3788
6 | Service in lieu of earthing coal & sand |  | Nos | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338
7 | Labour charges as per Sch. CL-7 (B-1)B |  |  |  |  | 4749.9327 |  |  | 5603.95 |  |  | 7235.38 |  |  | 8628.05 |  |  | 8628.05
8 | Transportation charges |  | LS |  |  | 5437.7635 |  |  | 6019.9669 |  |  | 6019.9669 |  |  | 6019.9669 |  |  | 6019.9669
9 | SUB TOTAL-2 |  |  |  |  | 28747.5367 |  |  | 46852.2119 |  |  | 57469.1131 |  |  | 91199.5809 |  |  | 85284.8049
10 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 1224.2324 |  | 0.125 | 3135.7524 |  | 0.125 | 4166.1964 |  | 0.125 | 7874.6594 |  | 0.125 | 7196.3594
11 | Grand Total |  |  |  |  | 29971.7691 |  |  | 49987.9643 |  |  | 61635.3095 |  |  | 99074.2403 |  |  | 92481.1643
12 | Grand Total (Round off) |  |  |  |  | 29972 |  |  | 49988 |  |  | 61635 |  |  | 99074 |  |  | 92481
Note on B14: 89326879: Earlier name was - PVC insulated 4 Core cable
Note on B15: 89326879: Earlier name was - 25 kVA (70 sq mm) [Armoured]
Note on B16: 89326879: Earlier name was - 63 kVA (70 sq mm) [Armoured]
Note on B17: 89326879: Earlier name was - 100 kVA (70 sq mm) [Armoured]
Note on C15: 89326879: Bin Code changed
Note on C16: 89326879: Bin Code changed
Note on C17: 89326879: Bin Code changed
Note on C18: 89326879: Bin Code changed
Note on C19: 89326879: Bin Code changed
Note on C20: 89326879: Bin Code changed
Note on C21: 89326879: Bin Code changed
Note on C22: 89326879: Bin Code changed
Note on E15: 89326879: Earlier Qty. was - 30
Note on H16: 89326879: Earlier Qty. was - 30
Note on K17: 89326879: Earlier Qty. was - 30
Note on K18: 89326879: Earlier Qty. was - 10
Note on N19: 89326879: Earlier Qty. was - 30
Note on N20: 89326879: Earlier Qty. was - 10
Note on Q21: 89326879: Earlier Qty. was - 30
Note on Q22: 89326879: Earlier Qty. was - 10

## C-7(B-2)
COST SCHEDULE C-7 (B-2)
11/0.4 kV OUT DOOR SUB-STATION (USING H-BEAM POLE FOR 25 / 63 / 100 / 200 kVA TRANSFORMER AND SINGLE CORE CABLE)
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 49457.85 | 49457.85
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 89213.04 | 89213.04
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 117398.25 | 117398.25
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 220752.68 | 220752.68
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469 | 816.2 | 46.4039 | 37874.8469
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35 | 3 | 128.45 | 385.35
| 11 kV H.W | 7130820241 | No. | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86 | 3 | 119.62 | 358.86
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84 | 6 | 142.14 | 852.84
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77 | 1 | 1676.77 | 1676.77
7 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | kg | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752 | 20 | 41.7888 | 835.7752
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92 | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721 | 22 | 70.4396 | 1549.6721
| (iii) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92 | 4 | 322.98 | 1291.92
10 | Concreting of supports @ 0.6 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | 2.1 | 2510.8 | 5272.68 | only material cost (excluding labour & G.S.T.)
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178 | 34 | 41.7888 | 1420.8178
12 | Transformer mounting Cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18 | 1 | 4590.18 | 4590.18
13 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74 | 1 | 89.74 | 89.74
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98 | 9 | 215.22 | 1936.98
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994 | 15 | 63 | 944.9994
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001 | 4 | 76.075 | 304.3001
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 146.77 | 146.77 | 1 | 146.77 | 146.77 | 3 | 146.77 | 440.31 | 3 | 146.77 | 440.31
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94 | 1 | 327.94 | 327.94 | 3 | 327.94 | 983.82 | 3 | 327.94 | 983.82
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98 | 3 | 504.66 | 1513.98
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38 | 1 | 69.38 | 69.38
| 16x65 mm | 7130620614 | Kg | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88 | 4 | 68.22 | 272.88
| 16x140 mm | 7130620625 | Kg | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24 | 4 | 67.06 | 268.24
| 16x200 mm | 7130620631 | Kg | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3 | 5 | 67.06 | 335.3
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1814.36 | 1814.36 | -- |  |  | -- |  |  | --
21 | Single Core cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 18.1746 | 2180.9568 | -- | [5 empty] | --
ii | 35 Sqmm | 7130310021 | Mtr | -- |  |  | 80 | 28.1566 | 2252.5272
iii | 50 Sqmm | 7130311009 | Mtr | -- |  |  | 40 | 42.7072 | 1708.2888 | 120 | 42.7072 | 5124.8664
iv | 70 Sqmm | 7130311010 | Mtr | [6 empty] | 40 | 57.599 | 2303.96 | 120 | 57.599 | 6911.88
v | 150 Sqmm | 7130311011 | Mtr | [9 empty] | 40 | 110.4928 | 4419.7116
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15292.16 | 15292.16 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19116 | 19116
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 38230.4 | 38230.4
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 |  |  |  |  | 125662.1283 |  |  | 180674.9775 |  |  | 225597.4579 |  |  | 351969.0531
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 11309.5915 |  | 0.09 | 16260.748 |  | 0.09 | 20303.7712 |  | 0.09 | 31677.2148
26 | Service in lieu of Earthing Coal & Sand etc. |  | No | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338 | 1 | 7884.5338 | 7884.5338
27 | Labour Charges as per Sch CL-3 |  |  |  |  | 11448.9 |  |  | 12026.4 |  |  | 12026.4 |  |  | 14922.9
28 | Labour charges for concreting |  | Cmt | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711 | 2.1 | 578.8434 | 1215.5711
29 | Transport charges upto 50 Kms averg. lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 5437.7635 |  |  | 6019.9669 |  |  | 6019.9669 |  |  | 6019.9669
30 | SUB TOTAL-2 |  |  |  |  | 162958.4883 |  |  | 224082.1973 |  |  | 273047.701 |  |  | 413689.2397
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 15707.766 |  | 0.125 | 22584.3722 |  | 0.125 | 28199.6822 |  | 0.125 | 43996.1316
32 | Cost per S/s for non-guaranteed works |  |  |  |  | 178666.2543 |  |  | 246666.5695 |  |  | 301247.3832 |  |  | 457685.3714
33 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 178666 |  |  | 246667 |  |  | 301247 |  |  | 457685
Note (A) :- (1) All the rates are with considering price variation clause.
(2) As per requirement 315 kVA Transformer may be used against 200 kVA schedule
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer

## C-8
COST SCHEDULE C-8
1 Km OF 11 kV LINE ON 365 kG 11 Mtr. LONG PCC POLE USING RACCOON / DOG CONDUCTOR MAXIMUM SPAN 80 METER.
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | PCC Pole using Raccoon Conductor |  | PCC Pole using Dog Conductor
[5 empty] | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | 7605.2 | 12 | 91262.4 | 12 | 91262.4
2 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1057.95 | 12 | 12695.4 | 12 | 12695.4
3 | Stay Clamp for PCC Pole | 7130810193 | No | 291.13 | 12 | 3493.56 | 12 | 3493.56
4 | 11 kV Top clamp | 7130810679 | No | 296.79 | 12 | 3561.48 | 12 | 3561.48
5 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 114.85 | 12 | 1378.2 | 12 | 1378.2
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 142.14 | 36 | 5117.04 | 36 | 5117.04
7 | ACSR Raccoon Conductor with 3% sag | 7130830060 | Mtr | 50.1858 | 3100 | 155575.949
8 | ACSR Dog Conductor with 3% sag | 7130830063 | Mtr | 66.185 |  |  | 3100 | 205173.624
9 | Jointing Sleeves suitable for Raccoon / Dog ACSR Conductor | 7130830051 | No | 141.07 | 6 | 846.42 | 6 | 846.42
10 | (I) Stay set 20 mm | 7130860033 | No | 803.97 | 4 | 3215.88 | 4 | 3215.88
| (II) Stay Wire 7/8 SWG @ 8.5 Kg per stay | 7130860076 | Kg | 69.7564 | 34 | 2371.7179 | 34 | 2371.7179
(III) Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 291.13 | 4 | 1164.52 | 4 | 1164.52
11 | Concreting of support @ 0.5 Cmt/pole, @ 0.3 Cmt/stay & base padding @ 0.05 Cmt /pole (1:3:6) | 7130200202 | Cmt | 2510.8 | 7.8 | 19584.24 | 7.8 | 19584.24 | only material cost (excluding labour & G.S.T.)
12 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 2 | 293.54 | 2 | 293.54
13 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 2 | 655.88 | 2 | 655.88
14 | Barbed Wire [ @ 2 Kg/Pole ] | 7130610206 | Kg | 76.075 | 24 | 1825.8007 | 24 | 1825.8007
15 | Danger Board | 7130880041 | Each | 89.74 | 12 | 1076.88 | 12 | 1076.88
16 | Binding wire and tape | 7130830006 | Kg | 155.45 | 6 | 932.7 | 6 | 932.7
17 | MS Nuts and Bolts |  | Kg |  | 24 |  | 24
| 16x40 mm | 7130620609 | Kg | 69.38 | 1 | 69.38 | 1 | 69.38
| 16x65 mm | 7130620614 | Kg | 68.22 | 12 | 818.64 | 12 | 818.64
| 16x140 mm | 7130620625 | Kg | 67.06 | 11 | 737.66 | 11 | 737.66
18 | SUB TOTAL-1 |  |  |  |  | 306677.2877 |  | 356274.9627
19 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 27600.9559 |  | 32064.7466
20 | Labour charges for concreting |  | Cmt | 578.8434 | 7.8 | 4514.9785 | 7.8 | 4514.9785
21 | Labour charges as per Sch No.- CL-4 |  |  |  |  | 57630.73 |  | 59363.23
22 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  | 9453.3841 |  | 9453.3841 |  | 9453.3841
23 | SUB TOTAL-2 |  |  |  |  | 405877.3361 |  | 461671.3019
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 38334.661 |  | 44534.3703
25 | Cost per Km for non-guaranteed works |  |  |  |  | 444211.9971 |  | 506205.6722
26 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 444212 |  | 506206
Note: All the rates are with considering price variation clause.

## C-9
COST SCHEDULE C-9
1 KM OF 11 kV LINE ON H-BEAM 152x152 MM 37.1 Kg /MTR. 13.0 MTR. USING RACCOON / DOG CONDUCTOR MAXIMUM SPAN 80 MTR.
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | H-Beam using Raccoon conductor |  | H-Beam using Dog conductor
[5 empty] | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole x 12 Nos = 5788 Kgs | 7130601958 | Kg | 46.4039 | 5788 | 268585.6574 | 5788 | 268585.6574
2 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1057.95 | 12 | 12695.4 | 12 | 12695.4
3 | Back Clamp for Cross Arm | 7130810361 | Pair | 309.8 | 12 | 3717.6 | 12 | 3717.6
4 | 11 kV Top clamp | 7130810679 | No | 296.79 | 12 | 3561.48 | 12 | 3561.48
5 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 114.85 | 12 | 1378.2 | 12 | 1378.2
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 142.14 | 36 | 5117.04 | 36 | 5117.04
7 | ACSR Raccoon conductor with 3% sag | 7130830060 | Mtr | 50.1858 | 3100 | 155575.949
8 | ACSR Dog conductor with 3% sag | 7130830063 | Mtr | 66.185 |  |  | 3100 | 205173.624
9 | Jointing Sleeves suitable for Raccoon / Dog ACSR Conductor | 7130830051 | No | 141.07 | 6 | 846.42 | 6 | 846.42
10 | (i) Stay set 20 mm | 7130860033 | No | 803.97 | 4 | 3215.88 | 4 | 3215.88
| (ii) Stay Wire 7/8 SWG @ 8.5 Kg per stay | 7130860076 | Kg | 69.7564 | 34 | 2371.7179 | 34 | 2371.7179
(iii) Stay Clamp
| (I) Stay Clamp for "H" Beam | 7130810692 | No | 322.98 | 4 | 1291.92 | 4 | 1291.92
11 | Concreting of support @ 0.6 Cmt/pole, @ 0.2 Cmt/stay & base padding @ 0.05 Cmt /pole (1:3:6) | 7130200202 | Cmt | 2510.8 | 9 | 22597.2 | 9 | 22597.2 | only material cost (excluding labour & G.S.T.)
12 | Red Oxide paint | 7130211158 | Ltr | 146.77 | 2 | 293.54 | 2 | 293.54
13 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 2 | 655.88 | 2 | 655.88
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 76.075 | 24 | 1825.8007 | 24 | 1825.8007
15 | Danger Board | 7130880041 | Each | 89.74 | 12 | 1076.88 | 12 | 1076.88
16 | Binding wire and tape | 7130830006 | Kg | 155.45 | 6 | 932.7 | 6 | 932.7
17 | MS Nuts and Bolts |  | Kg |  | 24 |  | 24
| 16x40 mm | 7130620609 | Kg | 69.38 | 1 | 69.38 | 1 | 69.38
| 16x65 mm | 7130620614 | Kg | 68.22 | 12 | 818.64 | 12 | 818.64
| 16x140 mm | 7130620625 | Kg | 67.06 | 11 | 737.66 | 11 | 737.66
18 | SUB TOTAL-1 |  |  |  |  | 487364.9451 |  | 536962.6201
19 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 43862.8451 |  | 48326.6358
20 | Labour charges for concreting |  | Cmt | 578.8434 | 9 | 5209.5906 | 9 | 5209.5906
21 | Labour charges as per Sch No. CL-4 |  |  |  |  | 56127.04 |  | 57859.54
22 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  | 9451.7031 |  | 9451.7031 |  | 9451.7031
23 | SUB TOTAL-2 |  |  |  |  | 602016.1238 |  | 657810.0896
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 60920.6181 |  | 67120.3275
25 | Cost per Km for non-guaranteed works |  |  |  |  | 662936.7419 |  | 724930.4171
26 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 662937 |  | 724930
Note: All the rates are with considering price variation clause.
Note on D12: 89326879: Earlier unit was - No.

## C-9 (A)
COST SCHEDULE C-9 (A)
ADDITIONAL (MID SPAN) POLES FOR NEW 11 kV LINE WITH RACCOON CONDUCTOR
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | H BEAM 152X152 MM 37.10 KG / MTR 13.0 MTR LONG
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm; 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole | 7130601958 | kg | 482.3 | 46.4039 | 22380.5913
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 1 | 1057.95 | 1057.95
3 | Cross Arm Clamp
| (i) Stay Clamp For "H" Beam | 7130810692 | No | 1 | 322.98 | 322.98
4 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 1 | 296.79 | 296.79
5 | Earthing Set (Coil earth as per Drawing No:-G/007 | 7130870013 | No | 1 | 114.85 | 114.85
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 142.14 | 426.42
7 | Concreting of supports H-Beam @ 0.6 Cmt. Per Pole & @ 0.2 Cmt. Per Stay and 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt. | 0.65 | 2510.8 | 1632.02 | only material cost (excluding labour & G.S.T.)
8 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 76.075 | 152.1501
9 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74
10 | MS Nuts and Bolts
| 16x40 mm | 7130620609 | Kg | 0.25 | 69.38 | 17.345
| 16x65 mm | 7130620614 | Kg | 0.6 | 68.22 | 40.932
| 16x140 mm | 7130620625 | Kg | 0.55 | 67.06 | 36.883
11 | SUB TOTAL-1 |  |  |  |  | 26568.6514
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 2391.1786
13 | Labour charges for concreting |  | Cmt | 0.65 | 578.8434 | 376.2482
14 | Labour charges as per Sch No.- CL-4 (revised based on one pole) |  |  |  |  | 2690.7878
15 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) - Taken 5% of |  |  |  |  | 472.6723
16 | SUB TOTAL-2 |  |  |  |  | 32499.5383
17 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 3321.0814
18 | Cost per Pole for non-guaranteed works |  |  |  |  | 35820.6197
19 | Cost per Pole (Rounded off) |  |  |  |  | 35821

## C-10
COST SCHEDULE C-10
AUGMENTATION OF 11/0.4 kV SUB-STATION CAPACITY (ASSUMING 25 YEARS OF LIFE & 10 YEARS IN SERVICE)
2018-19
S. No. | PARTICULARS | Bin CodeNo. | New SAP Bin Code | Unit | Rate | 25 kVA to 63 kVA |  | 63 kVA to 100 kVA |  | 100 kVA to 200 kVA
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 11/0.4 kV 63 kVA X-mer (LEVEL-2) * |  | 7132210019 | Each | 89213.04 | 1 | 89213.04
2 | 11/0.4 kV 100 kVA X-mer (LEVEL-2) * |  | 7132210020 | Each | 117398.25 |  |  | 1 | 117398.25
3 | 11/0.4 kV 200 kVA X-mer (LEVEL-2) * |  | 7132210021 | Each | 220752.68 |  |  |  |  | 1 | 220752.68
4 | R.S. Joist (175X85) mm 11 Mtr. Long i.e. 19.495 kg/mtr x 11 mtr = 214.44 kg x 4 No = 857.8 Kgs |  | 7130600675 | Kg | 44.9155 |  |  | 857.8 | 38528.5331 | 857.8 | 38528.5331
5 | (i) Stay set 16 mm | 7130860032201 | 7130860032 | No | 441.23 |  |  | 4 | 1764.92 | 4 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077103 | 7130860077 | Kg | 70.4396 |  |  | 22 | 1549.6721 | 22 | 1549.6721
| (iii) Stay Clamp for R.S. Joist | 7130810026301 | 7130810216 | Pair | 309.8 |  |  | 4 | 1239.2 | 4 | 1239.2
6 | Concreting of support @ 0.3 Cmt/pole, @ 0.2 Cmt/stay & base padding @ 0.05 Cmt/pole (1:3:6) |  | 7130200202 | Cmt | 2510.8 |  |  | 1.5 | 3766.2 | 1.5 | 3766.2 | only material cost (excluding labour & G.S.T.)
7 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013401 | 7130870013 | No | 114.85 |  |  | 1 | 114.85 | 1 | 114.85
8 | Red Oxide Paint | 7130211158904 | 7130211158 | Ltr | 146.77 |  |  | 1 | 146.77 | 1 | 146.77
9 | Aluminium Paint | 7130210809004 | 7130210809 | Ltr | 327.94 |  |  | 1 | 327.94 | 1 | 327.94
10 | Barbed Wire [@ 2 Kg/Pole] | 7130407183901 | 7130610206 | Kg | 76.075 |  |  | 8 | 608.6002 | 8 | 608.6002
11 | MS Nuts & Bolts |  |  | Kg |  | 14 |  | 14 |  | 14
| 16x40 mm | 7130620609003 | 7130620609 | Kg | 69.38 | 1 | 69.38 | 1 | 69.38 | 1 | 69.38
| 16x65 mm | 7130620614003 | 7130620614 | Kg | 68.22 | 4 | 272.88 | 4 | 272.88 | 4 | 272.88
| 16x140 mm | 7130620625403 | 7130620625 | Kg | 67.06 | 4 | 268.24 | 4 | 268.24 | 4 | 268.24
| 16x200 mm | 7130620631603 | 7130620631 | Kg | 67.06 | 5 | 335.3 | 5 | 335.3 | 5 | 335.3
12 | 70 Sqmm Single core XLPE insulated unarmoured Al. Conductor cable |  | 7130310007 | Mtr | 50.411 | 120 | 6049.3164 | 120 | 6049.3164 | 120 | 6049.3164
13 | 150 Sqmm Single core XLPE insulated unarmoured Al. Conductor cable |  | 7130310041 | Mtr | 102.7156 |  |  |  |  | 40 | 4108.6232
14 | 11 kV A.B. Switch |  | 7131930221 | Each | 8496 |  |  |  |  | 1 | 8496
15 | LT Distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950063801 | 7131950065 | No | 15292.16 | 1 | 15292.16
ii | 100 kVA | 7131950105901 | 7131950105 | No | 19116 |  |  | 1 | 19116
iii | 200 kVA | 7131950200001 | 7131950200 | No | 38230.4 |  |  |  |  | 1 | 38230.4
16 | SUB TOTAL-1 | [5 empty] | 111500.3164 |  | 191556.0518 |  | 326629.505
17 | Incidental Charges @ 9% : - |  |  |  | 0.09 |  | 10035.0285 |  | 17240.0447 |  | 29396.6554
18 | Labour charges as per Sch. CL-10(B) | [5 empty] | 18753.15 |  | 21395.19 |  | 23710.63
19 | Labour charges for concreting |  |  | Cmt | 578.8434 |  |  | 1.5 | 868.2651 | 1.5 | 868.2651
20 | Transportation charges | [5 empty] | 5437.7635 |  | 6019.9873 |  | 6019.9873
21 | SUB TOTAL-2 | [5 empty] | 145726.2584 |  | 237079.5389 |  | 386625.0428
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 |  | 13937.5395 |  | 23944.5065 |  | 40828.6881
23 | SUB TOTAL-3 | [5 empty] | 159663.7979 |  | 261024.0453 |  | 427453.731
24 | Cost of X-mer (Cost of X-mer to be taken at the time of procurement i.e before 10 years)
| (i) 25 kVA |  |  | No |  | 1 | 45000
| (ii) 63 kVA |  |  | No |  |  |  | 1 | 70578
| (iii) 100 kVA |  |  | No | [5 empty] | 1 | 89572
25 | (-) 10% Irreducible cost | [5 empty] | 4500 |  | 7057.8 |  | 8957.2
26 | (-) 10 year life @ 4% per year | [5 empty] | 16200 |  | 25408.08 |  | 32245.92
27 | Depreciated cost of X-mer after addition to 10% irreducible cost | [5 empty] | 28800 |  | 45169.92 |  | 57326.08
28 | (-) Cost of old X-mer assuming 25 years of life & 10 years in service | [5 empty] | 28800 |  | 45169.92 |  | 57326.08
29 | Net cost of augmentation | [5 empty] | 130863.7979 |  | 215854.1253 |  | 370127.651
30 | Net cost of augmentation (R/Off) | [5 empty] | 130864 |  | 215854 |  | 370128
All the rates are with considering price variation clause.
* | ISI Marked Energy Efficiency level-2 transformer
Note on E16: 89326879: Earlier unit was - No.

## C-11
COST SCHEDULE C-11
11/0.4 kV OUT DOOR SUB-STATION (16 kVA TRANSFORMER)
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | 16 kVA, 11/.4 kV X' MER
|  |  |  | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient) 16 kVA (LEVEL-2) * Aluminium Wound | 7132210017 | No | 1 | 44158.56 | 44158.56
2 | 140 Kg 8.0 Mtr. long PCC Pole | 7130800012 | No | 3 | 2255.2 | 6765.6
3 | DC Cross arm of 100x50x6 mm 8' Center 2.7 Mtr. long | 7130810517 | No | 1 | 4590.18 | 4590.18
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 128.45 | 385.35
5 | 11 kV Strain H/W | 7130820241 | Set | 3 | 119.62 | 358.86
6 | 11 kV D.O. Fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1676.77 | 1676.77
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 41.7888 | 835.7752
9 | (i) Stay set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 155.99 | 623.96
10 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base pad @ 0.05 Cmt/pole (1:3:6) | 7130200202 | Cmt | 1.85 | 2510.8 | 4644.98 | only material cost (excluding labour & G.S.T.)
11 | Transformer belting with 50x50x6 mm angle with 2 Cross fixing channel. | 7130600023 | Kg | 34 | 41.7888 | 1420.8178
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4590.18 | 4590.18
13 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 76.075 | 456.4502
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 146.77 | 146.77
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 504.66 | 1513.98
19 | MS Nuts & Bolts |  | Kg | 14
| 16x40 mm | 7130620609 | Kg | 1 | 69.38 | 69.38
| 16x65 mm | 7130620614 | Kg | 4 | 68.22 | 272.88
| 16x140 mm | 7130620625 | Kg | 4 | 67.06 | 268.24
| 16x200 mm | 7130620631 | Kg | 5 | 67.06 | 335.3
20 | TPN switch fuse unit (32 Amps) | 7131920253 | No | 1 | 755.6 | 755.6
21 | 16 Sqmm single core PVC insulated Cable | 7130311008 | Mtr | 120 | 18.1746 | 2180.9568
22 | CT operated electronic static meter 100/5 Amp. | 7131310997 | No | 1 | 1639.61 | 1639.61
23 | LT CT 50/5 Amp. | 7132230016 | No | 4 | 345.07 | 1380.28
24 | Meter Box (GI plain sheet) for 3 Phase LT CT operated meter. | 7132406420 | No | 1 | 2580.37 | 2580.37
25 | Copper control cable 4 core 2.5 sq.mm Unarmoured | 7130310654 | Mtr | 12 | 62.7585 | 753.1025
26 | SUB TOTAL-1 |  |  |  |  | 92551.844
27 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 8329.666
28 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 295.8177 | 887.453
29 | Service in lieu of Earthing Coal & Sand etc. |  | No | 1 | 7884.5338 | 7884.5338
30 | Labour charges as per Sch. CL-3 |  |  |  |  | 11448.9
31 | Labour charges for concreting |  | Cmt | 1.85 | 578.8434 | 1070.8603
32 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) |  |  |  |  | 5437.7635
33 | SUB TOTAL-2 |  |  |  |  | 127611.0205
34 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 11568.9805
35 | Cost per S/s for non-guaranteed works |  |  |  |  | 139180.001
36 | Cost per S/s for non-guaranteed works (R/off) |  |  |  |  | 139180
Note: (1) All the rates are with considering price variation clause.
Note on D20: 89326879: Earlier unit was - No.

## C-12
COST SCHEDULE C-12
SCHEDULE FOR 11 kV UNDERGROUND CABLE CROSSING UNDER EXISTING RAILWAY TRACK / ROAD FOR 60 MTR. LONG RAIL / ROAD CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | Using HDD Technique (for Railway works) on 3x240 sq.mm AB XLPE Cable | Using HDD Technique (for Road crossing works) on 3x240 sq.mm AB XLPE Cable
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD; 6 Mtr long | 7132461004 | Mtr | 1146.75 | 120 | 137610 | 137610
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 417 | 18 | 7506 | 7506
3 | 11 kV XLPE 240 sqmm 3 core UG Cable | 7130310079 | Mtr | 960.0427 | 180 | 172807.6806 | 172807.6806
4 | End terminating jointing kit for 240 sqmm XLPE cable | 7130352041 | Set | 19916.04 | 4 | 79664.16 | 79664.16
5 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1079.16 | 24 | 25899.84 | 25899.84
6 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
7 | M.S.Flat (50x6) mm | 7130600173 | kg | 45.4764 | 100 | 4547.644 | 4547.644
8 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No. | 556 | 4 | 2224 | 2224
9 | Cable covering tiles 250x250x40 mm | 7130201343 | Each | 33 | 80 | 2640 | 2640
10 | Sand | 7132498006 | Cmt | 903 | 1.2 | 1083.6 | 1083.6
11 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 504.66 | 6 | 3027.96 | 3027.96
12 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 50.1858 | 18 | 903.3442 | 903.3442
13 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 266.98 | 6 | 1601.88 | 1601.88
14 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 849.08 | 10 | 8490.8 | 8490.8
15 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Railway authorities including liaisoning work etc. |  | LS | LS | LS | 25000
16 | SUB TOTAL-1 |  |  |  |  | 479006.9088 | 454006.9088
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 43110.6218 | 40860.6218
18 | Service in lieu of Earthing Coal & Sand etc |  | No | 2628.1669 | 10 | 26281.6694 | 26281.6694
19 | Labour Charges for laying of HDPE Pipe (using HDD Technique ** ) as per Revised Labour Schedule AL-5 |  |  |  |  | 340130 | 340130
20 | Labour Charges for excavation of cable trench beyond the length of HDPE Pipe upto DP Structure |  | Cmt | 254.0989 | 12 | 3049.1863 | 3049.1863 |  | (20 Mx1 Mx0.6 M)
21 | Transportation Charges |  |  |  |  | 79242.8549 | 79242.8549
22 | SUB TOTAL-2 |  |  |  |  | 970821.2412 | 943571.2412
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 59875.8636 | 56750.8636
24 | Charges payable to Railway including supervision charges etc. | 15% |  |  |  | 145623.1862 |  | Name Changed Earlier-Way leave charges payable to Railway including supervision
25 | Municipality Charges payable to Local bodies as per Demand note |  | LS
26 | Cost per 60 Mtr for non guaranteed works |  |  |  |  | 1176320.291 | 1000322.1048
27 | Cost per 60 Mtr for non guaranteed works (Rounded off ) |  |  |  |  | 1176320 | 1000322
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
** | Horizontal Directional Drilling (HDD) Technique
The rates mentioned at S.No.1, 2 & 3 are applicable for 60 Mtr Corridor of Railway crossing. Estimate may be prepared based on actual length of corridor.
*** | The charges to be paid for according railway permission shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note on D17: 89326879: Earlier unit was - No.
Note on E14: 89326879: Assuming 2 kg M-seal @ Rs 450/- per kg + PVC Plate 10 mm thick
***
Fill appropriate cost

## C-13
COST SCHEDULE C-13
SINGLE POLE MOUNTED LOW CAPACITY THREE PHASE 11/0.4 kV DISTRIBUTION TRANSFORMER SUB-STATION
2018-19
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | 16 kVA Three Phase
[5 empty] | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient) 16 kVA (LEVEL-2) * Aluminium Wound | 7132210017 | No. | 1 | 44158.56 | 44158.56
2 | 200 Kg 8.0 Meter long PCC Pole | 7130800033 | No. | 1 | 2552.95 | 2552.95
3 | 11 kV 'V' Cross arm with clamp (instead of DC Cross arm) | 7130810495 | No | 1 | 1057.95 | 1057.95
4 | 11 kV Top clamp with cleat | 7130810679 | No | 1 | 296.79 | 296.79
5 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 3 | 142.14 | 426.42
6 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 128.45 | 385.35
7 | 11 kV Strain Hardware | 7130820241 | No | 3 | 119.62 | 358.86
8 | 11 kV D.O. Fuse and L.A. mounting DC channel size 75x40x6 mm length 860 mm | 7130810509 | No | 1 | 1676.77 | 1676.77
9 | 11 kV D.O. Fuse unit for Three phase X-mer | 7131930412 | Each | 3 | 1177.88 | 3533.64
10 | MS angle for transformer clamping set size 50x50x6 mm | 7130600023 | Kg | 20 | 41.7888 | 835.7752
11 | (i) Stay set 16 mm | 7130860032 | No | 4 | 441.23 | 1764.92
| (ii) Stay wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 70.4396 | 1549.6721
| (iii) Stay clamp | 7130810026 | Pair | 4 | 155.99 | 623.96
12 | Concreting of supports @ 0.5 Cmt per pole and @ 0.2 Cmt per stay & base padding @ 0.05 Cmt/pole (1:3:6) | 7130200202 | Cmt | 1.35 | 2510.8 | 3389.58 | only material cost (excluding labour & G.S.T.)
13 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No. | 2 | 4590.18 | 9180.36
14 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 76.075 | 152.1501
16 | Earthing set (pipe earth as per drawing)
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 9 | 215.22 | 1936.98
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 15 | 63 | 944.9994
17 | Red Oxide Paint | 7130211158 | Ltr | 1 | 146.77 | 146.77
18 | Aluminium Paint | 7130210809 | Ltr | 1 | 327.94 | 327.94
19 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 504.66 | 1513.98
20 | M.S. Nuts and Bolts
| (i) 16x40 mm | 7130620609 | Kg | 1 | 69.38 | 69.38
| (ii) 16x65 mm | 7130620614 | Kg | 4 | 68.22 | 272.88
| (iii) 16x140 mm | 7130620625 | Kg | 4 | 67.06 | 268.24
| (iv) 16x200 mm | 7130620631 | Kg | 5 | 67.06 | 335.3
21 | TPN switch fuse unit (32 Amps) | 7131920253 | No | 1 | 755.6 | 755.6
22 | XLPE insulated 4 core 16 sq mm armoured cable for 3 phase X-mer | 7130311084 | Mtr. | 30 | 58.8139 | 1764.4161
23 | LT Feeder Piller box 1 phase 8 Way for distribution of service connection | 7130890004 | No. | 1 | 5151.35 | 5151.35
24 | SUB TOTAL-1 |  |  |  |  | 85521.2828
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 7696.9155
26 | Back filling of poles with boulders @ 0.3 Cmt per pole. |  | No. | 1 | 295.8177 | 295.8177
27 | Labour charges for concreting |  | Cmt | 1.35 | 578.8434 | 781.4386
28 | Labour charges as per Schedule No. CL-8 (G-1) |  |  |  |  | 7914.61
29 | Transport charges upto 50 Kms. Average lead from area store to const. camping site transport |  |  |  |  | 3138.0161
30 | SUB TOTAL-2 |  |  |  |  | 105348.0806
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 10690.1604
32 | Cost per Km. for Non-guaranteed works |  |  |  |  | 116038.241
33 | Cost per Km. for Non-guaranteed works (Rounded off) |  |  |  |  | 116038
* | ISI Marked Energy Efficiency level-2 transformer
Note on B23: 89326879: Earlier name was - Transformer mounting DC Cross arm size 65x65x6 channel length 800 mm
Note on D21: 89326879: Earlier unit was - No.

## C-14
COST SCHEDULE C-14
2018-19
PLINTH MOUNTED 11/0.4 kV OUTDOOR SUB-STATION
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | 63 kVA X-MER |  | 100 kVA X-MER |  | 200 kVA X-MER
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | RS Joist (175X85) mm 11 Mtr Long i.e. 19.495 Kg/mtr x 11 mtr. = 214.44 kg x 2 No = 428.89 Kgs | 7130600675 | Kg | 44.9155 | 429 | 19268.7581 | 429 | 19268.7581
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole x 2 Nos = 964.6 Kgs | 7130601958 | Kg | 46.4039 |  |  |  |  | 964.6 | 44761.1826
3 | Transformer 11/0.4 kV (Energy efficient)
| 63 kVA (LEVEL-2) * | 7132210019 | Each | 89213.04 | 1 | 89213.04
| 100 kVA (LEVEL-2) * | 7132210020 | Each | 117398.25 |  |  | 1 | 117398.25
| 200 kVA (LEVEL-2) * | 7132210021 | Each | 220752.68 |  |  |  |  | 1 | 220752.68
4 | DC Cross arm 100x50 mm 8' Centre | 7130810517 | No | 4590.18 | 1 | 4590.18 | 1 | 4590.18 | 1 | 4590.18
5 | 11 kV Polymer Disc Insulator | 7130820010 | No | 128.45 | 3 | 385.35 | 3 | 385.35 | 3 | 385.35
| 11 kV H.W. | 7130820241 | No | 119.62 | 3 | 358.86 | 3 | 358.86 | 3 | 358.86
6 | 11 kV DO fuse & LA mounting DC cross arm (75 x 40 mm) | 7130810509 | No | 1676.77 | 1 | 1676.77 | 1 | 1676.77 | 1 | 1676.77
7 | 11 kV DO Fuse Unit | 7131930412 | Each | 1177.88 | 3 | 3533.64 | 3 | 3533.64 | 3 | 3533.64
8 | M.S. Angle 50x50x6 mm | 7130600023 | Kg | 41.7888 | 20 | 835.7752 | 20 | 835.7752 | 20 | 835.7752
9 | (i) Stay set 16 mm | 7130860032 | No | 441.23 | 4 | 1764.92 | 4 | 1764.92 | 4 | 1764.92
| (ii) Stay wire 7/10 SWG (7.5 Kg each) | 7130860077 | Kg | 70.4396 | 30 | 2113.1892 | 30 | 2113.1892 | 30 | 2113.1892
| (iii) Stay clamp for R.S.Joist | 7130810216 | Pair | 309.8 | 4 | 1239.2 | 4 | 1239.2
| (iv) Stay clamp for H-Beam | 7130810692 | No | 322.98 |  |  |  |  | 4 | 1291.92
10 | Concreting of support [0.3 Cmt per RSJ, 0.5 Cmt per H-Beam, 0.2 Cmt per stay, 9 cub.m. (1.5x1.5x4 m) for X-mer plinth] (1:3:6) | 7130200202 | Kg. | 2510.8 | 10.4 | 26112.32 | 10.4 | 26112.32 | 10.8 | 27116.64 | only material cost (excluding labour & G.S.T.)
11 | Danger Board | 7130880041 | Each | 89.74 | 1 | 89.74 | 1 | 89.74 | 1 | 89.74
12 | Earthing set pipe carth
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 215.22 | 9 | 1936.98 | 9 | 1936.98 | 9 | 1936.98
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 63 | 15 | 944.9994 | 15 | 944.9994 | 15 | 944.9994
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 76.075 | 4 | 304.3001 | 4 | 304.3001 | 4 | 304.3001
14 | Red Oxide Paint | 7130211158 | Ltr | 146.77 | 2 | 293.54 | 2 | 293.54 | 2 | 293.54
15 | Aluminium Paint | 7130210809 | Ltr | 327.94 | 2 | 655.88 | 2 | 655.88 | 2 | 655.88
16 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 504.66 | 3 | 1513.98 | 3 | 1513.98 | 3 | 1513.98
17 | M.S. Nuts & Bolts |  |  |  | 14 |  | 14 |  | 17
| 16x40 mm | 7130620609 | Kg | 69.38 | 1 | 69.38 | 1 | 69.38 | 1 | 69.38
| 16x65 mm | 7130620614 | Kg | 68.22 | 4 | 272.88 | 4 | 272.88 | 4 | 272.88
| 16x140 mm | 7130620625 | Kg | 67.06 | 4 | 268.24 | 4 | 268.24 | 5 | 335.3
| 16x200 mm | 7130620631 | Kg | 67.06 | 5 | 335.3 | 5 | 335.3 | 7 | 469.42
18 | PVC insulated Single Core Armoured cable
| 70 Sqmm | 7130311010 | Mtr | 57.599 | 160 | 9215.84 | 120 | 6911.88 |  |  | Old Bin Code- 7130311054
| 150 sqmm | 7130311011 | Mtr | 110.4928 |  |  | 40 | 4419.7116 | 120 | 13259.1348 | Old Bin Code- 7130311057
| 300 sqmm | 7130311012 | Mtr | 215.644 |  |  |  |  | 40 | 8625.7612 | Old Bin Code- 7130311061
19 | LT Distribution Box for X-mer
| 63 kVA | 7131950065 | No. | 15292.16 | 1 | 15292.16
| 100 kVA | 7131950105 | No. | 19116 |  |  | 1 | 19116
| 200 kVA | 7131950200 | No. | 38230.4 |  |  |  |  | 1 | 38230.4
20 | Stay Clamp for (i) R.S.Joist 175x85 mm | 7130810216 | Pair | 309.8 | 14 | 4337.2 | 14 | 4337.2
| (ii) Stay clamp for H-Beam | 7130810692 | No. | 322.98 |  |  |  |  | 14 | 4521.72
21 | 11 kV AB Switch | 7131930221 | Each | 8496 |  |  | 1 | 8496 | 1 | 8496
22 | ACSR Conductor Rabbit | 7130830057 | Mtr | 33.9486 | 30 | 1018.4574 | 30 | 1018.4574 | 30 | 1018.4574
23 | SUB TOTAL-1 |  |  |  |  | 187640.8794 |  | 230261.681 |  | 390218.98
24 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 16887.6791 |  | 20723.5513 |  | 35119.7082
25 | Labour Charges as per Sch. CL-9. |  |  |  |  | 24780 |  | 27357.21 |  | 30025.25
26 | Labour charges for concreting |  | Cmt | 578.8434 | 10.4 | 6019.9714 | 10.4 | 6019.9714 | 10.8 | 6251.5087
27 | Transportation Charges |  |  |  |  | 7531.2447 |  | 7531.2447 |  | 8786.447
28 | SUB TOTAL-2 |  |  |  |  | 242859.7746 |  | 291893.6583 |  | 470401.8939
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 23455.1099 |  | 28782.7101 |  | 48777.3725
30 | Grand Total |  |  |  |  | 266314.8845 |  | 320676.3685 |  | 519179.2664
31 | Total (rounding off) |  |  |  |  | 266315 |  | 320676 |  | 519179
* | ISI Marked Energy Efficiency level-2 transformer
Note on B38: 89326879: Earlier name was - PVC insulated 3.5 Core Cable
Note on B39: 89326879: Earlier name was - 70 Sqmm (Armoured)
Note on C39: 89326879: Bin Code changed
Note on C40: 89326879: Bin Code changed
Note on C41: 89326879: Bin Code changed
Note on D22: 89326879: Earlier unit was - No.
Note on D46: 89326879: Earlier unit was - No.
Note on F39: 89326879: Earlier Qty. was - 40
Note on H39: 89326879: Earlier Qty. was - 30
Note on H40: 89326879: Earlier Qty. was - 10
Note on J40: 89326879: Earlier Qty. was - 30
Note on J41: 89326879: Earlier Qty. was - 10

## C-15
COST SCHEDULE C-15
SCHEDULE FOR LAYING OF 1 kM 11 kV CABLE DIRECT IN GROUND SINGLE CABLE LINE USING OPEN TRENCH METHOD
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x95 sq.mm AB XLPE Cable | 3x240 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 11 kV XLPE 95 sqmm 3 core UG Cable | 7130310077 | Mtr | 531.3632 | 1040 | 552617.7176
2 | 11 kV XLPE 240 sqmm 3 core UG Cable | 7130310079 | Mtr | 960.0427 | 1040 |  | 998444.3768
3 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 95 sq.mm., 11 kV Underground XLPE cable | 7130352039 | Set | 13753.61 | 2 | 27507.22
4 | Straight through heat shrinkable cable jointing kit with lugs for 3 Core 240 sq.mm., 11 kV Underground XLPE cable | 7130352041 | Set | 19916.04 | 2 |  | 39832.08
5 | End terminating jointing kit upto 95 sqmm XLPE cable | 7130352043 | Set | 7149.38 | 2 | 14298.76
6 | End terminating jointing kit for 240 sqmm XLPE cable | 7130352044 | Set | 8630.52 | 2 |  | 17261.04
7 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 1079.16 | 10 | 10791.6 | 10791.6
8 | G.I.Wire 8 SWG (for earthing connect to LA & cable) | 7130870043 | Kg | 62.999 | 5 | 314.995 | 314.995
9 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 20 | 11120 | 11120
10 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 4000 | 132000 | 132000
11 | River Sand (For 10 cm. base & 10 cm. filling of trench above cable & then cable covering tiles over complete length of trench) | 7132498006 | Cmt | 903 | 150 | 135450 | 135450
12 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 504.66 | 6 | 3027.96 | 3027.96
13 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 50.1858 | 18 | 903.3442 | 903.3442
14 | Aluminium T-clamp suitable for Dog / Raccoon conductor for connecting L.A. | 7130830585 | No. | 266.98 | 6 | 1601.88 | 1601.88
15 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. | 7130642039 | No | 849.08 | 2 | 1698.16 | 1698.16
16 | M.S. Nuts & Bolts | Fill the appropriate Bin Code | Kg | 70.53 | 3 | 211.59 | 211.59
17 | Bhatta brick |  | No | 5.9 | 4400 | 25960 | 25960
18 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Road constructing authorities including liaisoning work etc. [ To be provisioned as per actual requirement ] |  | LS | LS | LS | 25000 | 25000
19 | SUB TOTAL-1 |  |  |  |  | 942503.2268 | 1403617.026
20 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 84825.2904 | 126325.5323
21 | Service in lieu of Earthing Coal & Sand etc |  | No | 2628.1669 | 10 | 26281.6694 | 26281.6694
22 | Labour Charges - |  | Mtr |  |  | 337505.2832 | 337505.2832
i | Cable trench excavation [(1.0 Mx0.75 Mx1.2 M) LxWxD] |  | Cmt | 254.099 | 900 | 228689.1 | 228689.1
ii | Spreading of sand for base pad of cable (10 cm thick & 10 cm. above cable) |  | Mtr | 13.4095 | 1000 | 13409.5 | 13409.5
iii | Laying of XLPE Cable in open trench & rising on pole through GI pipe & back filling of cable trench with excavated soil |  | Mtr | 66.138 | 1040 | 68783.4784 | 68783.4784
iv | Laying of GI pipe |  | Mtr | 66.4123 | 10 | 664.1228 | 664.1228
v | Fixing of rising pipe with clamps |  | Mtr | 370.81 | 10 | 3708.1 | 3708.1
vi | Fixing of 11 kV lightning arrestor including earthing, jumpering and fixing of aluminium clamp |  | Set | 216.56 | 2 | 433.12 | 433.12
vii | Providing earthing (earthing pit digging and laying of earthing pipe complete) |  | Set | 1010.62 | 2 | 2021.24 | 2021.24
viii | Covering of cable with tiles |  | Mtr | 3.6902 | 1000 | 3690.2 | 3690.2
ix | Making of Straight jointing of XLPE Cable |  | No | 4362.998 | 2 | 8725.996 | 8725.996
x | Making of End jointing of XLPE Cable |  | No | 3690.213 | 2 | 7380.426 | 7380.426
23 | Transportation Charges |  |  |  |  | 79242.8498 | 79242.8498
24 | SUB TOTAL-2 |  |  |  |  | 1470358.3197 | 1972972.3608
25 | Overhead Charges @ 12.5% [ Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 117812.9034 | 175452.1283
26 | Charges payable to Nagar Nigam / Nagar Palika / Nagar Panchayat / Gram Panchayat including supervision charges etc.
27 | Cost per Km for non guaranteed works |  |  |  |  | 1588171.223 | 2148424.489
28 | Cost per Km for non guaranteed works (Rounded off ) |  |  |  |  | 1588171 | 2148424
(a) | Cable and accessories size can be replaced as per actual requirement
(b) | When multiple cables have to be laid in the common trench, the following excavation is to be followed-- (i) 0.75 Mtr width x 1.2 Mtr depth for laying of 02 cables; (ii) 1.0 Mtr width x 1.2 Mtr depth for laying of 03 cables; (iii) 1.25 Mtr width x 1.2 Mtr depth for laying of 04 cables and so on.
(c) | Between two cables, fly ash brick is to be provided as separator
(d) | All other items are to be changed as per size of trench and number of cables in a trench.
ACTIVITY OF Col. 21 (xi) INCLUDED in (vi)
xi | Jumpering of Lightning arrestor and fixing of aluminium clamps |  | Set | 291.28 | 2 | 582.56 | 582.56
Note on E32: 89326879: As per CL-10
Note on E33: 89326879: As per schedule CL-10
Note on E34: 89326879: As per schedule CL-10
Note on E35: 89326879: As per schedule CL-10
Note on E36: 89326879: As per Labour Schedule AL-6
Note on E37: 89326879: As per Labour Schedule BL-2
Note on E38: 89326879: As per Labour Schedule AL-6
Note on E39: 89326879: As per schedule AL-6
Note on E80: 89326879: As per Labour Schedule AL-6

## C-16
COST SCHEDULE C-16
D.T. CAPACITORS ON EXISTING DTR's OTHER THAN INDUSTRIAL (RETAINED & SHIFTED)
2018-19
S. No. | PARTICULARS | New SAP Bin code No. | Capacitor Rating - KVAR | Capacitor cost | Incidental Charges | Labour Charge per Capacitor Bank | Cost per Package | Cost per Package Round Off
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT Capacitor for 25 kVA DT | 7132200812 | 5 | 1561.71 | 140.5539 | 200 | 1902.2639 | 1902
2 | LT Capacitor for 63 kVA DT | 7132200813 | 10 | 3122.45 | 281.0205 | 200 | 3603.4705 | 3603
3 | LT Capacitor for 100 kVA DT | 7132200814 | 12 | 3751.83 | 337.6647 | 200 | 4289.4947 | 4289
4 | LT Capacitor for 200 kVA DT | 7132200814 | 12 | 3751.83 | 337.6647 | 200 | 4289.4947 | 4289
5 | LT Capacitor for 315 kVA DT | 7132200814 | 12 | 3751.83 | 337.6647 | 200 | 4289.4947 | 4289
| Incidental Charges @ 9% : - |  |  | 9%

## C-17
COST SCHEDULE C-17
11 kV MEDP STRUCTURE ON H-BEAM POLE, 11 METER LONG (TO BE SUPPLEMENTED FOR H.T. CONNECTION)
2018-19
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 46.4039 | 37874.8469
2 | DC Cross Arm of 100x50 mm channel (2.7 Mtr. Long) | 7130810512 | Set | 2 | 3977.41 | 7954.82
3 | 11 kV Polymer Disc Insulator | 7130820010 | No | 6 | 128.45 | 770.7
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 119.62 | 717.72
5 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 6 | 142.14 | 852.84
6 | (I) Stay set 16 mm | 7130860032 | No | 2 | 441.23 | 882.46
| (II) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 17 | 70.4396 | 1197.4739
(III) Stay Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 322.98 | 1291.92
7 | Concreting of pole @ 0.6 Cmt and 0.2 Cmt per stay and 0.05 Cmt for base padding (1:3:6) | 7130200202 | Cmt | 1.7 | 2510.8 | 4268.36 | only material cost (excluding labour & G.S.T.)
8 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 114.85 | 229.7
9 | Red Oxide Paint | 7130211158 | Ltr | 2 | 146.77 | 293.54
10 | Aluminium Paint | 7130210809 | Ltr | 2 | 327.94 | 655.88
11 | Barbed wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 76.075 | 304.3001
12 | Danger Board | 7130880041 | Each | 1 | 89.74 | 89.74
13 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 69.38 | 34.69
| 16x200 mm | 7130620631 | Kg | 5.5 | 67.06 | 368.83
14 | GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | 7130642039 | No | 2 | 849.08 | 1698.16
15 | G.I.Bend of 40 mm dia. | 7130640171 | Each | 1 | 104.16 | 104.16 | NEW BIN CODE ALLOTED
16 | 11 kV Polymer type Lightning Arrestor | 7130840029 | Each | 3 | 504.66 | 1513.98
17 | 11 kV CTPT unit of appropriate capacity |  | No
18 | Copper control cable 10 Core 2.5 Sqmm. (armoured) | 7130310660 | Mtr | 10 | 205.7332 | 2057.3324
19 | H.T. Static Trivector Meter 3 Ø 4 Wire 0.5 S with DLMS Protocol category A | 7131310033 | No | 1 | 3500.23 | 3500.23
20 | Universal Meter Box for HT meters. | 7132406425 | Each | 1 | 2614.17 | 2614.17
21 | Test terminal Box (TTB) | 7131310037 | Each | 1 | 894.97 | 894.97
22 | SUB TOTAL-1 |  |  |  |  | 70170.8233
23 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 6315.3741
24 | Labour charges for concreting |  | Cmt | 1.7 | 578.8434 | 984.0338
25 | Labour charges as per Sch No.- CL-5 |  |  |  |  | 10042.69
26 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 3587.5921
27 | SUB TOTAL-2 |  |  |  |  | 91100.5133
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.125 | 8771.3529
29 | Cost per DP for non-guaranteed works |  |  |  |  | 99871.8662
30 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 99872
Note:- All the rates are with considering price variation clause.

## C-18
COST SCHEDULE C-18
2018-19
SCHEDULE FOR NEW AUTOMATED 11 KV CAPACITOR BANK AT 33/11 KV SUB-STATIONS
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank |  | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank
[5 empty] | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. Bank shall be complete with Capacitor units of 121 KVAr at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin/Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Botls etc. | 7132200826 | Nos | 186917.23 | 1 | 186917.23
2 | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . Bank shall be complete with Capacitor units of 121 kVAr at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin/Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Bolts etc. | 7132200014 | Mtr. | 141355.63 |  |  | 1 | 141355.63
3 | 11 kV, Aluminium Wound, Dry type Series reactors
4 | 0.2% Reactor suitable for 363 Kvar step | 7132210106 | Set | 6864.39 | 3 | 20593.17 | 3 | 20593.17 | NEW BIN CODE ALLOTED
5 | 0.2% Reactor suitable for 726 Kvar step | 7132210108 | Set | 8380.18 | 6 | 50281.08 | 3 | 25140.54 | NEW BIN CODE ALLOTED
6 | 11 kV, 3-Phase Oil-Cooled RVT | 7132230471 | No. | 33323.81 | 1 | 33323.81 | 1 | 33323.81 | NEW BIN CODE ALLOTED
7 | 12 kV, Outdoor type Vacuum Capacitor switches | 7131980001 | Nos. | 67737.07 | 3 | 203211.21 | 2 | 135474.14
8 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure | 7131931091 | Set | 27806.59 | 1 | 27806.59 | 1 | 27806.59 | NEW BIN CODE ALLOTED
9 | Mounting GI structure for above isolator | 7131931095 | Set | 14225.81 | 1 | 14225.81 | 1 | 14225.81 | NEW BIN CODE ALLOTED
10 | 9 KV, 10 KA, Station Class, Polymer Lightning Arrestors | 7130840029 | set of 3 | 1513.98 | 1 | 1513.98 | 1 | 1513.98
| Indoor Type Automatic Control Unit along with APFC Relay | 7131940871 | No. | 46692.4 | 1 | 46692.4 | 1 | 46692.4 | NEW BIN CODE ALLOTED
11 | GI Structure for complete Equipment | 7130850198 | Kgs. | 82.25 | 1000 | 82250 | 800 | 65800 | NEW BIN CODE ALLOTED
12 | Unarmoured Control cable 8Cx2.5 Sqmm and junction box | 7130310658 | Mtr | 119.1884 | 120 | 14302.6056 | 120 | 14302.6056
13 | Unarmoured Control cable 10Cx2.5 Sqmm | 7130310681 | Mtr | 148.7322 | 60 | 8923.9296 | 60 | 8923.9296 | BIN CODE Changed. Old Bin 7130310660
14 | Unarmoured Control cable 2Cx2.5 Sqmm | 7130310652 | Mtr | 36.2593 | 60 | 2175.5568 | 60 | 2175.5568
15 | 11 KV VCB , 630 A, suitable for Capacitor Switching | 7131941762 | Nos. | 117747.13 | 1 | 117747.13
16 | 11 KV VCB , 400 A, suitable for Capacitor Switching | 7131941762 | Nos. | 117747.13 |  |  | 1 | 117747.13
17 | 11 kV Control & Relay Panel for Capacitor Bank | 7131960010 | Nos. | 83478.19 | 1 | 83478.19 | 1 | 83478.19 | NEW BIN CODE ALLOTED
18 | 11 KV Power Cable, HT XLPE, 120 Sq MM | 7130310078 | Mtr | 792.3696 | 15 | 11885.544
19 | 11 KV Power Cable, HT XLPE, 95 Sq MM | 7130310077 | Mtr | 531.3632 |  |  | 15 | 7970.4478
20 | 11 kV C.T. 200-100/5 Amps. | 7132230185 | Nos. | 12913.58 | 3 | 38740.74 | 3 | 38740.74
21 | Earthing through
(i) | 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4315.55 | 3 | 12946.65 | 3 | 12946.65
(ii) | M.S.Flat 50 x 6 mm | 7130600173 | Kg | 45.4764 | 100 | 4547.644 | 100 | 4547.644
22 | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2510.8 | 9.9 | 24856.92 | 9.9 | 24856.92 | only material cost (excluding labour & G.S.T.)
23 | SUB TOTAL-1 |  |  |  |  | 986420.19 |  | 827615.8838
24 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 88777.8171 |  | 74485.4295
25 | Labour Charges |  |  |  |  | 49321.0095 |  | 41380.7942
26 | Transport Charges |  |  |  |  | 29592.6057 |  | 24828.4765
27 | Labour charges for concreting |  | Cmt | 578.8434 | 9.9 | 5730.5497 | 9.9 | 5730.5497
28 | Service in lieu of Earthing Coal & Salt etc |  | No | 2628.1669 | 1 | 2628.1669 | 1 | 2628.1669
29 | SUB TOTAL-2 |  |  |  |  | 1162470.3389 |  | 976669.3007
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 123302.5237 |  | 103451.9855
31 | GRAND TOTAL |  |  |  |  | 1285772.8627 |  | 1080121.2862
32 | GRAND TOTAL (Round Off) |  |  |  |  | 1285773 |  | 1080121
Note on B25: 89326879: Earlier name was - C & R Panel for VCB

## C-19
COST SCHEDULE C-19
SCHEDULE FOR INSTALLATION OF COMPACT R.M.U. 11 kV CLASS SF6 / VCB TYPE (1 INCOMING + 2 BREAKER + 1 OUTGOING)
2018-19
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RMU (4 Way), One Incoming + Two Breakers + One Outgoing (2OD + 2 VL), 350 MVA, 650 Amps. | 7131941764 | No | 1080119.04 | 1 | 1080119.04
2 | Concreting of RMU Bed with CC 1:3:6 as per Labour Charges | 7130200202 | Cmt | 2510.8 | 0.37 | 928.996 | only material cost (excluding labour & G.S.T.)
3 | Concreting of Foundation with Reinforcement CC 1:3:6 as per Labour Charges | 7130200202 | Cmt | 2510.8 | 1.44 | 3615.552
4 | M.S.Strip 25 x 3 mm for earthing (of length 2 x 5 = 10 Mtr.) |  | Kg | 37.96 | 6 | 227.76
| GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 849.08 | 2 | 1698.16
5 | SUB TOTAL-1 |  |  |  |  | 1086589.508
6 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 97793.0557
7 | Labour Charges as per Sch. CL-11. |  |  |  |  | 8260
8 | Labour charges for concreting |  | Cmt | 578.8434 | 1.81 | 1047.7066
9 | Transportation Charges |  |  |  |  | 7531.2345
10 | SUB TOTAL-2 |  |  |  |  | 1201221.5048
11 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 135823.6885
12 | Grand Total |  |  |  |  | 1337045.1933
13 | Grand Total (Rounded off) |  |  |  |  | 1337045

## C-20
COST SCHEDULE C-20
SCHEDULE FOR CHEMICAL EARTHING OF METERING EQUIPMENT INSTALLED IN THE PREMISES OF HT CONSUMERS IN NORMAL / HARD ROCK SOIL
2018-19
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | M.S.Strip 25x3 mm (0.6 kg/Mtr.) |  | Kg | 37.96 | 10 | 379.6
2 | Chem Rod Earthing electrode (Chemical Earthing) | 7132486843 | No. | 8945.71 | 1 | 8945.71 | RATE EXCLUDING G.S.T.
3 | G.I. Nuts & Bolts 16x40 mm | 7130620133 | Kg | 95.97 | 1.5 | 143.955
4 | G.I. Nuts & Bolts 16x65 mm | 7130620140 | Kg | 95.97 | 1.5 | 143.955
5 | G.I. Spring Washer | 7130622922 | Kg | 149.07 | 1 | 149.07
6 | SUB TOTAL-1 |  |  |  |  | 9762.29
7 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 878.6061
8 | Labour Charges |  | No. | 1010.6166 | 1 | 1010.6166
9 | Transportation Charges |  |  |  |  | 1051.4016
10 | SUB TOTAL-2 |  |  |  |  | 12702.9143
11 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.125 |  | 1220.2863
12 | Grand Total |  |  |  |  | 13923.2005
13 | Grand Total (Rounded off) |  |  |  |  | 13923
Note:- | Chemical Earthing consists of Galvanized Mild Steel pipe of size 2000 mm x 50 mmn Outer diameter or higher size as per site conditions, filled with a highly conductive material and a GI Strip minimum 16 mm x 3 mm covering total of pipe, forming the electrode for obtaining earth resistance less than 1 ohm.