## A-6
COST SCHEDULE A-6
2022-23
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER EXISTING RAILWAY TRACK / ROAD FOR 60 MTR. LONG RAIL / ROAD CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | Using HDD Technique (for Railway works) on 3x400 sq.mm AB XLPE Cable | Using HDD Technique (for Road crossing works) on 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD; 6 Mtr long | 7132461004 | Mtr | 1444.85 | 120 | 173382 | 173382
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 511.57 | 18 | 9208.26 | 9208.26
3 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2951.14 | 190 | 560716.6 | 560716.6
4 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 41869.07 | 4 | 167476.28 | 167476.28
5 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1345.87 | 24 | 32300.88 | 32300.88
6 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
7 | M.S.Flat (50x6) mm | 7130600173 | kg | 63.06 | 100 | 6306 | 6306
8 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 4 | 2224 | 2224
9 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 80 | 2640 | 2640
10 | Sand | 7132498006 | Cmt | 735 | 1.2 | 882 | 882
11 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3233.2 | 6 | 19399.2 | 19399.2
12 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 76.32 | 18 | 1373.76 | 1373.76
13 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 350.63 | 6 | 2103.78 | 2103.78
14 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 1058.93 | 10 | 10589.3 | 10589.3
15 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway authorities including liaisoning work etc. |  | LS | LS | LS | 25000
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1019602.06 | 994602.06
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 864069.5424 | 842883.1017
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 76470.1545 | 74595.1545
19 | Service in lieu of Earthing Coal & Sand etc |  | No | 3020.1367 | 10 | 30201.3667 | 30201.3667
20 | Labour Charges for laying of HDPE Pipe (using HDD Technique ** ) as per Schedule AL-5 |  |  |  |  | 251770.7466 | 251770.7466
21 | Labour Charges for excavation of cable trench beyond the length of HDPE Pipe upto DP Structure |  | CMT | 291.9956 | 12 | 3503.9476 | 3503.9476
22 | Transport charges @ 4% on Column no. 17 |  |  |  |  | 34562.7817 | 33715.3241 | NAME CHANGED
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 16, 18, 19, 20, 21, 22 |  |  |  |  | 177013.8821 | 173548.5749
24 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22, 23) |  |  |  |  | 1437592.4217 | 1410218.2161
25 | Applicable CGST @ 9% on Row 24 |  |  | 0.09 |  | 129383.3179 | 126919.6395
26 | Applicable SGST @ 9% on Row 24 |  |  | 0.09 |  | 129383.3179 | 126919.6395
27 | Charges payable to Railway including supervision charges etc. [15% of Col. 24] |  |  |  |  | 215638.8632
28 | Municipality Charges payable to Local bodies as per Demand note |  | LS
29 | Total Estimated Cost including GST [for Col. 07 = Row 24+25+26+27] & [for Col. 08 = Row 24+25+26+28] |  |  |  |  | 1911997.9208 | 1664057.4951
30 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1911998 | 1664057
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
** | Horizontal Directional Drilling (HDD) Technique
This schedule is prepared for 60 Mtr Corridor of Railway / Road crossing. Estimate may be framed as per actual site conditions and actual width of the rail / road corridor.
*** | The charges to be paid for according railway permission shall be made as per actuals i.e. based on the demand note / payment received for the same.
*
***
Fill appropriate cost
Note on E13: 89326879: Assuming 2 kg M-seal @ Rs 450/- per kg + PVC Plate 10 mm thick
Note on G27: 89326879: ***
Note on B29: Barun Chakraborty: Earlier name was - Transportation Charges
Note on H35: 89326879: Fill appropriate cost here

## A-1
COST SCHEDULE A-1
1 KM OF 33 kV LINE ON PCC POLES / H-BEAMS WITH MAXIMUM SPAN OF 100 METERS USING RACCOON CONDUCTOR
2022-23
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4451.53 | 44515.3
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 62.81 | 302932.63
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7656.89 | 76568.9
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2899.86 | 28998.6 | 10 | 2899.86 | 28998.6 | 10 | 2899.86 | 28998.6
5 | Back Clamp for Cross Arm
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 10 | 403.7 | 4037 |  |  |  | 10 | 403.7 | 4037
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 10 | 447.87 | 4478.7
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 482.48 | 4824.8 | 10 | 482.48 | 4824.8 | 10 | 482.48 | 4824.8
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 149.3 | 1493 | 10 | 149.3 | 1493 | 10 | 149.3 | 1493
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 333.95 | 10018.5 | 30 | 333.95 | 10018.5 | 30 | 333.95 | 10018.5
9 | Raccoon ACSR Conductor (80 Sqmm, Al. Eq) with 3% sag | 7130830060 | Mtr | 3100 | 76.32 | 236592 | 3100 | 76.32 | 236592 | 3100 | 76.32 | 236592
10 | Jointing Sleeves suitable ( for 80 Sqmm, Al. Eq. ACSR cond.) | 7130830050 | No | 6 | 47.47 | 284.82 | 6 | 47.47 | 284.82 | 6 | 47.47 | 284.82
11 | (i) Stay set 20 mm | 7130860033 | No | 3 | 986.29 | 2958.87 | 3 | 986.29 | 2958.87 | 3 | 986.29 | 2958.87
| (ii) Stay Clamp For PCC Pole | 7130810193 | Pair | 3 | 403.7 | 1211.1 |  |  |  | 3 | 403.7 | 1211.1
| (iii) Stay Clamp For "H" Beam | 7130810692 | Pair |  |  |  | 3 | 447.87 | 1343.61
| (iv) Stay Wire 7/8 SWG @ 8.5 kg/ stay | 7130860076 | Kg | 25.5 | 90.68 | 2312.34 | 25.5 | 90.68 | 2312.34 | 25.5 | 90.68 | 2312.34
12 | Concreting of supports @ 0.6 Cmt. Per pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC; and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole. (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Material cost including GST and labour.
13 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 181.98 | 254.772 | 6 | 181.98 | 1091.88 | 1.4 | 181.98 | 254.772
14 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 406.6 | 609.9 | 6 | 406.6 | 2439.6 | 1.5 | 406.6 | 609.9
15 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 106.03 | 2120.6 | 20 | 106.03 | 2120.6 | 20 | 106.03 | 2120.6
16 | Danger Board | 7130880041 | No | 10 | 123.66 | 1236.6 | 10 | 123.66 | 1236.6 | 10 | 123.66 | 1236.6
17 | Binding wire and tape | 7130830006 | Kg | 3.5 | 204.16 | 714.56 | 3.5 | 204.16 | 714.56 | 3.5 | 204.16 | 714.56
18 | M.S. Nuts and Bolts |  | Kg | 17 |  |  | 17 |  |  | 18
| 16x65 mm | 7130620614 | Kg |  | 80.39 |  | 7 | 80.39 | 562.73 |  | 80.39
| 16x90 mm | 7130620619 | Kg | 3 | 80.39 | 241.17 |  | 80.39 |  | 3.5 | 80.39 | 281.365
| 16x140 mm | 7130620625 | Kg |  | 79.02 |  | 10 | 79.02 | 790.2 |  | 79.02
| 16x160 mm | 7130620627 | Kg | 14 | 79.02 | 1106.28 |  | 79.02 |  | 14.5 | 79.02 | 1145.79
19 | Guarding 33 kV |  | Rs |  |  | 15839.319 |  |  | 15839.319 |  |  | 15839.319
| (i) G.I. Wire 6 SWG | 7130870045 | Kg | 49 | 87.81 | 4302.69 | 49 | 87.81 | 4302.69 | 49 | 87.81 | 4302.69
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 20 | 87.81 | 1756.2 | 20 | 87.81 | 1756.2 | 20 | 87.81 | 1756.2
| (iii) 33 kV guarding channel | 7130897759 | Set | 1 | 4122.23 | 4122.23 | 1 | 4122.23 | 4122.23 | 1 | 4122.23 | 4122.23
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 447.87 | 1343.61 | 3 | 447.87 | 1343.61 | 3 | 447.87 | 1343.61
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 79.02 | 94.824 | 1.2 | 79.02 | 94.824 | 1.2 | 79.02 | 94.824
| (vi) I--Bolt Big Size | 7130620013 | No | 4 | 146.26 | 585.04 | 4 | 146.26 | 585.04 | 4 | 146.26 | 585.04
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 986.29 | 1972.58 | 2 | 986.29 | 1972.58 | 2 | 986.29 | 1972.58
| (viii) Stay wire 7/8 SWG & 8.5 Kg/stay | 7130860076 | Kg | 17 | 90.68 | 1541.56 | 17 | 90.68 | 1541.56 | 17 | 90.68 | 1541.56
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 80.39 | 120.585 | 1.5 | 80.39 | 120.585 | 1.5 | 80.39 | 120.585
20 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 365309.531 |  |  | 644793.359 |  |  | 412292.836
21 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 309584.3483 |  |  | 546435.05 |  |  | 349400.7085 | NEW ROW ADDED
22 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 27398.2148 |  | 0.075 | 48359.5019 |  | 0.075 | 30921.9627 | Earlier name was - Incidental Charges @ 9%
23 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 424.9206 | 4249.2056 | 0 | 0 | 0 | 0 | 0 | 0
24 | Labour charges as per Schedule No.- AL-1 |  |  |  |  | 50221.28 |  |  | 53419.43 |  |  | 53771.93
25 | Labour charges for concreting |  | Cmt | 2 | 665.1732 | 1330.3464 | 8 | 665.1732 | 5321.3855 | 7 | 665.1732 | 4656.2123
26 | Transport charges @ 4 % on row no.21 |  |  |  |  | 12383.3739 |  |  | 21857.402 |  |  | 13976.0283
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 20, 22, 23, 24, 25, 26 |  |  |  |  | 57611.494 |  |  | 96718.8848 |  |  | 64452.3712
28 | Total Estimated Cost excluding GST (Row 21, 22, 23, 24, 25, 26, 27) |  |  |  |  | 462778.263 |  |  | 772111.6542 |  |  | 517179.213
29 | Applicable CGST @ 9% on Row 28 |  |  |  | 0.09 | 41650.0437 |  | 0.09 | 69490.0489 |  | 0.09 | 46546.1292
30 | Applicable SGST @ 9% on Row 28 |  |  |  | 0.09 | 41650.0437 |  | 0.09 | 69490.0489 |  | 0.09 | 46546.1292
31 | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 546078.3504 |  |  | 911091.752 |  |  | 610271.4713
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 546078 |  |  | 911092 |  |  | 610271
Note:-
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on D14: Barun Chakraborty: Earlier unit was - No.
Note on D22: Barun Chakraborty: Earlier unit was - No.
Note on B46: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on F48: Barun Chakraborty: Earlier - 0.09
Note on I48: Barun Chakraborty: Earlier - 0.09
Note on L48: Barun Chakraborty: Earlier - 0.09

## A-3
COST SCHEDULE - A-3
1 KM OF 33 kV LINE ON PCC POLES / H-BEAM SUPPORT WITH MAXIMUM SPAN OF 100 METERS USING DOG CONDUCTOR
2022-23
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152 mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4451.53 | 44515.3
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 62.81 | 302932.63
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7656.89 | 76568.9
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2899.86 | 28998.6 | 10 | 2899.86 | 28998.6 | 10 | 2899.86 | 28998.6
5 | Back Clamp for Cross Arm
| (i) Stay Clamp For PCC Pole | 7130810193 | Pair | 10 | 403.7 | 4037 |  |  |  | 10 | 403.7 | 4037
| (ii) Stay Clamp For H-Beam Pole | 7130810692 | Pair |  |  |  | 10 | 447.87 | 4478.7
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 482.48 | 4824.8 | 10 | 482.48 | 4824.8 | 10 | 482.48 | 4824.8
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 149.3 | 1493 | 10 | 149.3 | 1493 | 10 | 149.3 | 1493
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 333.95 | 10018.5 | 30 | 333.95 | 10018.5 | 30 | 333.95 | 10018.5
9 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 3100 | 76.32 | 236592 | 3100 | 76.32 | 236592 | 3100 | 76.32 | 236592
10 | Jointing Sleeves (suitable for 100 Sqmm, Al. Eq. ACSR cond.) | 7130830051 | No | 6 | 47.47 | 284.82 | 6 | 47.47 | 284.82 | 6 | 47.47 | 284.82
11 | Stay set 20 mm | 7130860033 | No | 3 | 986.29 | 2958.87 | 3 | 986.29 | 2958.87 | 3 | 986.29 | 2958.87
12 | (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 3 | 403.7 | 1211.1 |  |  |  | 3 | 403.7 | 1211.1
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 3 | 447.87 | 1343.61
13 | Stay Wire 7/8 SWG @ 8.5 kg Per stay | 7130860076 | Kg | 25.5 | 90.68 | 2312.34 | 25.5 | 90.68 | 2312.34 | 25.5 | 90.68 | 2312.34
14 | Concreting of H-Beam supports @ 0.6 cmt. Per pole and @ 0.3 Cmt per stay and @ 0.05 cmt per pole for base padding for PCC / H- Beam pole (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Material cost including GST and labour.
15 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 181.98 | 254.772 | 6 | 181.98 | 1091.88 | 1.4 | 181.98 | 254.772
16 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 406.6 | 609.9 | 6 | 406.6 | 2439.6 | 1.5 | 406.6 | 609.9
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 106.03 | 2120.6 | 20 | 106.03 | 2120.6 | 20 | 106.03 | 2120.6
18 | Danger Boards | 7130880041 | No | 10 | 123.66 | 1236.6 | 10 | 123.66 | 1236.6 | 10 | 123.66 | 1236.6
19 | Binding wire and tape | 7130830006 | Kg | 3.5 | 204.16 | 714.56 | 3.5 | 204.16 | 714.56 | 3.5 | 204.16 | 714.56
20 | M.S. Nuts and Bolts |  | Kg | 18 |  |  | 18 |  |  | 18
| 16x40 mm | 7130620609 | Kg |  | 81.75 |  | 0.5 | 81.75 | 40.875 |  | 81.75
| 16x65 mm | 7130620614 | Kg |  | 80.39 |  | 7.5 | 80.39 | 602.925 |  | 80.39
| 16x90 mm | 7130620619 | Kg | 3.5 | 80.39 | 281.365 |  | 80.39 |  | 3.5 | 80.39 | 281.365
| 16x140 mm | 7130620625 | Kg |  | 79.02 |  | 10 | 79.02 | 790.2 |  | 79.02
| 16x160 mm | 7130620627 | Kg | 14.5 | 79.02 | 1145.79 |  | 79.02 |  | 14.5 | 79.02 | 1145.79
21 | Guarding |  |  |  | 63622.579 |  |  | 63622.579 |  |  | 63622.579
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 87.81 | 4302.69 | 49 | 87.81 | 4302.69 | 49 | 87.81 | 4302.69
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 87.81 | 1756.2 | 20 | 87.81 | 1756.2 | 20 | 87.81 | 1756.2
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 1 | 4122.23 | 4122.23 | 1 | 4122.23 | 4122.23 | 1 | 4122.23 | 4122.23
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 447.87 | 1343.61 | 3 | 447.87 | 1343.61 | 3 | 447.87 | 1343.61
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 79.02 | 94.824 | 1.2 | 79.02 | 94.824 | 1.2 | 79.02 | 94.824
| (vi) I-Bolt Big Size | 7130620013 | No | 4 | 146.26 | 585.04 | 4 | 146.26 | 585.04 | 4 | 146.26 | 585.04
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 403.7 | 807.4 | 2 | 403.7 | 807.4 | 2 | 403.7 | 807.4
| (viii) Stay wire 7/8 SWG & 8.5 Kg/ stay | 7130860076 | Kg | 17 | 2970 | 50490 | 17 | 2970 | 50490 | 17 | 2970 | 50490
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 80.39 | 120.585 | 1.5 | 80.39 | 120.585 | 1.5 | 80.39 | 120.585
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 413172.496 |  |  | 692657.689 |  |  | 460076.096
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 350146.1831 |  |  | 586998.0415 |  |  | 389894.9966
24 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 30987.9372 |  | 0.075 | 51949.3267 |  | 0.075 | 34505.7072
25 | Labour charges for concreting |  | Cmt | 2 | 665.1732 | 1330.3464 | 8 | 642.6794 | 5141.4353 | 7 | 642.6794 | 4498.7559
26 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 424.9206 | 4249.2056
27 | Labour charges as per Schedule No.- AL-3 |  |  |  |  | 52291.28 | -- | -- | 56524.43 |  |  | 55841.93
28 | Transport charges @ 4% on Column no. 23 |  |  |  |  | 14005.8473 |  |  | 23479.9217 |  |  | 15595.7999 | NAME CHANGED
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 22, 24, 25, 26, 27, 28 |  |  |  |  | 64504.6391 |  |  | 103719.1003 |  |  | 71314.7861
30 | Total Estimated Cost excluding GST (Row 23, 24, 25, 26, 27, 28, 29) |  |  |  |  | 517515.4386 |  |  | 827812.2554 |  |  | 571651.9756
31 | Applicable CGST @ 9% on Row 30 |  |  |  | 0.09 | 46576.3895 |  | 0.09 | 74503.103 |  | 0.09 | 51448.6778
32 | Applicable SGST @ 9% on Row 30 |  |  |  | 0.09 | 46576.3895 |  | 0.09 | 74503.103 |  | 0.09 | 51448.6778
33 | Total Estimated Cost including GST (Row 30+31+32) |  |  |  |  | 610668.2176 |  |  | 976818.4614 |  |  | 674549.3313
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 610668 |  |  | 976818 |  |  | 674549
Note:
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on B53: Barun Chakraborty: Earlier name was - Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1)

## A-3 (A)
COST SCHEDULE -- A-3 (A)
2022-23
SCHEDULE FOR AUGMENTATION OF 1 kM OF 33 kV LINE FROM RACCOON TO DOG CONDUCTOR
S.No. | Particulars | New SAP Bin Code | Unit | Qty | Cost per Unit | Cost
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | ACSR Dog Conductor 100 sq.mm | 7130830063 | Km | 3.1 | 95458.44 | 295921.164
2 | Jointing Sleeves suitable for Dog ACSR Conductor | 7130830051 | No | 6 | 185.27 | 1111.62
3 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 6 | 333.95 | 2003.7
4 | Guarding
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 87.81 | 4302.69
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 87.81 | 1756.2
| (iii) 33 kV Guarding Channel (Set) | 7130897759 | Set | 1 | 4122.23 | 4122.23
| (iv) M.S Nut & Bolt 16x140 mm. | 7130620625 | Kg | 1.2 | 79.02 | 94.824
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 146.26 | 585.04
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 986.29 | 1972.58
| (vii) Stay Wire 7/8 SWG @ 8.5 Kg. Stay | 7130860076 | Kg | 17 | 90.68 | 1541.56
| (viii) MS Nut & Bolt 16x90 mm | 7130620619 | Kg | 1.5 | 80.39 | 120.585
5 | Concreting of Stay Set @ 0.3 Cmt per stay (1:3:6) | 7130200202 | Cmt | 0.6 | 2970 | 1782 | Material cost including GST and labour.
6 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 315314.193
7 | Material cost excluding GST ( Sub Total-1/1.18 ) |  |  |  |  | 267215.4178
8 | Incidental Charges @ 7.5 % on Sub - Total-1 : - |  |  |  | 0.075 | 23648.5645
9 | Labour charges for concreting |  | Cmt | 0.6 | 665.17 | 399.102
10 | Labour charges as per Schedule No.- AL-3(A) [New labour schedule introduced] |  |  |  |  | 31332.53
11 | Transport charges @ 4% on Column no. 7 |  |  |  |  | 10688.6167 | NEW ROW ADDED
12 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 6, 8, 9, 10, 11 |  |  |  |  | 47672.8758
13 | Total Estimated Cost excluding GST (Row 7, 8, 9, 10, 11, 12) |  |  |  |  | 380957.1068
14 | Applicable CGST @ 9% on Row 13 |  |  |  | 0.09 | 34286.1396
15 | Applicable SGST @ 9% on Row 13 |  |  |  | 0.09 | 34286.1396
16 | Returnable cost of old conductor assuming 25 years of life & 20 years in service |  |  | 3.1 | 7310.8 | 22663.48
17 | Total Estimated Cost including GST (Row 13+14+15-16) |  |  |  |  | 426865.906
18 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 426866
Note on B24: Barun Chakraborty: Earlier name was - Labour Charges (activities defined)
Note on F30: Kanchan Mahesh Thakur: rates of 1996-97

## A-4
COST SCHEDULE A-4
1 KM OF 33 kV LINE ON 37.1 KG / MTR 13 M. LONG H-BEAM SUSPENSION TYPE WITH PANTHER CONDUCTOR (WITH MAXIMUM SPAN OF 50 METERS)
2022-23
S. No. | PARTICULARS | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M long (482.30 Kg) x 20 No = 9646 Kgs | 7130601958 | Kg | 9646 | 62.81 | 605865.26
2 | DC Cross arm (100x50 mm) Channel 2.4 Mtr. (1.5 X 20 = 30) | 7130810512 | Set | 30 | 4899.4186 | 146982.5581
3 | 33 kV Suspension Hardware suitable for Panther Conductor (3x20=60) | 7130820312 | Set | 60 | 2612.24 | 156734.4
4 | 33 kV Polymer Disc Insulator (9x20=180) | 7130820013 | No. | 180 | 204.36 | 36784.8
5 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 20 | 149.3 | 2986
6 | ACSR Panther Conductor with 5% sag | 7130830070 | Mtr. | 3150 | 223.12 | 702828
7 | Jointing Sleeves suitable for Panther conductor | 7130830971 | No. | 6 | 286.33 | 1717.98
8 | Stay Set 20 mm Complete | 7130860033 | Set. | 12 | 986.29 | 11835.48
9 | Stay Clamp for "H" Beam | 7130810692 | Pair | 100 | 447.87 | 44787
10 | Stay Wire 7/8 SWG @ 8.5 Kg/Stay | 7130860076 | Kg. | 170 | 90.68 | 15415.6
11 | Concreting of H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt. per Pole for base Padding & @ 0.3 Cmt. Per stay (1:3:6) | 7130200202 | Cmt. | 17.2 | 2970 | 51084 | Material cost including GST and labour.
12 | Red Oxide Paint | 7130211158 | Ltr. | 26 | 181.98 | 4731.48
13 | Aluminium Paint | 7130210809 | Ltr. | 26 | 406.6 | 10571.6
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg. | 40 | 106.03 | 4241.2
15 | Danger Boards | 7130880041 | No. | 20 | 123.66 | 2473.2
16 | Binding Wire & Tape | 7130830006 | Kg. | 8 | 204.16 | 1633.28
17 | MS Nut & Bolts |  | Kg. | 123
| 16x40 mm | 7130620609 | Kg. | 2 | 81.75 | 163.5
| 16x65 mm | 7130620614 | Kg. | 30 | 80.39 | 2411.7
| 16x90 mm | 7130620619 | Kg. | 20 | 80.39 | 1607.8
| 16x140 mm | 7130620625 | Kg. |  | 79.02
| 16x160 mm | 7130620627 | Kg. | 1 | 79.02 | 79.02
| 16x200 mm | 7130620631 | Kg. |  | 79.02
| 16x250 mm | 7130620637 | Kg. | 70 | 79.02 | 5531.4
18 | MS Angle 65x65x6 for Tie | 7130600032 | Kg. | 435 | 51.48 | 22393.8
19 | Strain Plate (65x8 mm) | 7130810624 | No. | 120 | 118.53 | 14223.6
20 | Guarding 33 kV for single span
| (i) G.I. Wire 6 SWG | 7130870045 | Kg. | 40 | 87.81 | 3512.4
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg. | 20 | 87.81 | 1756.2
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 2 | 4122.23 | 8244.46
| (iv) M.S Nut & Bolt 16x250 mm. | 7130620637 | Kg. | 5 | 79.02 | 395.1
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 146.26 | 585.04
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 986.29 | 1972.58
| (vii) Stay Wire 7/8 SWG & 8.5 Kg. Stay | 7130860076 | Kg. | 17 | 90.68 | 1541.56
| (viii) Stay Clamp for "H" Beam | 7130810692 | Pair | 2 | 447.87 | 895.74
| (ix) MS Nut & Bolt 16x90 mm | 7130620619 | Kg. | 1 | 80.39 | 80.39
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1866066.1281
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1581411.973
23 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 139954.9596
24 | Labour charges for concreting |  | Cmt | 17.2 | 665.1732 | 11440.9788
25 | Labour Charges per Km as per Schedule - AL-4 |  | Km | 1 |  | 156701.0182
26 | Transport charges @ 4% on Column no. 22 |  |  |  |  | 63256.4789 | NAME CHANGED
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 21, 23, 24, 25, 26 |  |  |  |  | 279677.4455
28 | Total Estimated Cost excluding GST (Row 22, 23, 24, 25, 26, 27) |  |  |  |  | 2232442.854
29 | Applicable CGST @ 9% on Row 28 |  |  |  | 0.09 | 200919.8569
30 | Applicable SGST @ 9% on Row 28 |  |  |  | 0.09 | 200919.8569
31 | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 2634282.5677
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 2634283
Note on B50: Barun Chakraborty: Earlier name was - Transport Charges up to 50 km average lead from area Stores to Construction Camp Including Side Transport
Note on D50: Barun Chakraborty: Earlier - LS
Note on E50: Barun Chakraborty: Earlier - LS

## A-11
COST SCHEDULE A-11
SCHEDULE FOR LAYING OF 1 kM 33 kV CABLE DIRECT IN GROUND SINGLE CABLE LINE USING OPEN TRENCH METHOD
2022-23
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 2700.49 | 1040 | 2808509.6
2 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2951.14 | 1040 |  | 3069185.6
3 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 120- 240 sq mm Underground XLPE cable | 7130310089 | Set | 70050.26 | 2 | 140100.52
4 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 300- 400 sq mm Underground XLPE cable | 7130310090 | No | 78444 | 2 |  | 156888
5 | End terminating jointing kit upto 240 sqmm XLPE cable | 7130352037 | Set | 28226.94 | 2 | 56453.88
6 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 41869.07 | 2 |  | 83738.14
7 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 1345.87 | 10 | 13458.7 | 13458.7
8 | G.I. Wire 8 SWG (for earthing connect to LA & cable) | 7130870043 | Kg | 87.81 | 5 | 439.05 | 439.05
9 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 20 | 11120 | 11120
10 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 4000 | 132000 | 132000
11 | River Sand (For 10 cm. base & 10 cm. filling of trench above cable & then cable covering tiles over complete length of trench) | 7132498006 | Cmt | 735 | 150 | 110250 | 110250
12 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3233.2 | 6 | 19399.2 | 19399.2
13 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 76.32 | 18 | 1373.76 | 1373.76
14 | Aluminium T-clamp suitable for Dog / Raccoon conductor for connecting L.A. | 7130830585 | No. | 350.63 | 6 | 2103.78 | 2103.78
15 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. | 7130642039 | No | 1058.93 | 2 | 2117.86 | 2117.86
16 | M.S. Nuts & Bolts | Fill the appropriate Bin Code | Kg | 79.02 | 3 | 237.06 | 237.06
17 | Bhatta brick | 7132498054 | No | 6.39 | 4400 | 28116 | 28116
18 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Road constructing authorities including liaisoning work etc. [ To be provisioned as per actual requirement ] |  | LS | LS | LS | 25000 | 25000
19 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 3350679.41 | 3655427.15
20 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 2839558.822 | 3097819.6186
21 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 251300.9557 | 274157.0363
22 | Service in lieu of Earthing Coal & Sand etc |  | No | 3020.1359 | 10 | 30201.3589 | 30201.3589
23 | Labour charges as per Schedule No.- AL-11 [New labour schedule introduced] |  |  |  |  | 711758.0115 | 711758.0115
24 | Transport charges @ 4% on Column no. 20 |  |  |  |  | 113582.3529 | 123912.7847 | NAME CHANGED
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 19, 21, 22, 23, 24 |  |  |  |  | 557190.2611 | 599432.0427
26 | Total Estimated Cost excluding GST (Row 20, 21, 22, 23, 24, 25) |  |  |  |  | 4503591.7622 | 4837280.8527
27 | Applicable CGST @ 9% on Row 26 |  |  | 0.09 |  | 405323.2586 | 435355.2767
28 | Applicable SGST @ 9% on Row 26 |  |  | 0.09 |  | 405323.2586 | 435355.2767
29 | Charges payable to Nagar Nigam / Nagar Palika / Nagar Panchayat / Gram Panchayat including supervision charges etc.
30 | Total Estimated Cost including GST (Row 26+27+28+29) |  |  |  |  | 5314238.2794 | 5707991.4062
31 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 5314238 | 5707991
(a) | Cable and accessories size can be replaced as per actual requirement
(b) | When multiple cables have to be laid in the common trench, the following excavation is to be followed-- (i) 1.0 Mtr width x 1.5 Mtr depth for laying of 02 cables; (ii) 1.25 Mtr width x 1.5 Mtr depth for laying of 03 cables; (iii) 1.5 Mtr width x 1.5 Mtr depth for laying of 04 cables and so on.
(c) | Between two cables, fly ash brick is to be provided as separator
(d) | All other items are to be changed as per size of trench and number of cables in a trench.
ACTIVITY OF Col. 21 (xi) INCLUDED in (vi)
xi | Jumpering of Lightning arrestor and fixing of aluminium clamps |  | Set | 291.28 | 2 | 582.56 | 582.56
Note on B32: Barun Chakraborty: Earlier name was - Labour Charges - S.No. 23 (i) to (x) detailed [individual work mentioned]
Note on B33: Barun Chakraborty: Earlier name was - Transportation Charges

## B-1
COST SCHEDULE B -1
SCHEDULE FOR 33/11 kV, 3.15 MVA, 1.6 MVA SUB-STATION WITH TWO BAYS FOR OUTGOING FEEDERS AND 5 MVA SUB-STATION WITH THREE BAYS FOR OUTGOING FEEDERS AT NEW SITE
2022-23
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Proposed 33/11 kV S/s expandable to 2x1.6 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x3.15 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x5 MVA with control room
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 |  | LAND AND CIVIL WORKS (Rate as per SoR PWD)
| i | Construction of 1.5 Mtr high barbed wire fencing in angle iron post as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Mtr | 406 | 400 | 162400 | 400 | 162400 | 400 | 162400
| ii | Drilling of 150 mm dia bore well (upto 100 Mtr depth) with 1.5 HP Submersible motor pump and water supply line for switch yard including all taxes, royalty, T&P, materials, labours, transportation etc complete. |  | Job | 160088 | 1 | 160088 | 1 | 160088 | 1 | 160088
| iii | Construction of A1 type Control Room with toilet as per Drg. No. 04-01/AR/24-R2 date 13.06.2007 including all taxes royalty, T&P, materials, labours, transportation etc. complete. |  | Job | 906710 | 1 | 906710 | 1 | 906710 | 1 | 906710
| iv (a) | Construction of 2.4 Mtr high Chain link wire mesh fencing on Hard Soil or Hard Moorum as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | M | 2494 | 125 | 311750 | 125 | 311750 | 125 | 311750
| iv (b) | Construction of 2.4 Mtr high Chain link wire mesh fencing on Black Cotton Soil as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | M | 2860 | 125 | 357500 | 125 | 357500 | 125 | 357500
| v | Construction of 4.50 m x 2.15 m size yard / area gate as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Each | 35276 | 2 | 70552 | 2 | 70552 | 2 | 70552
| vi | Providing and filling in plinth with sand / crusher dust and hard moorum under floor in layers not exceeding 20 cm in depth consolidating each deposited layer by ramming and watering with a lead upto 50 M and lift upto 1.5 M. (Moorum measured in stacks will be reduced by 16% for voids). |  | Cmt | 371 | 300 | 111300 | 300 | 111300 | 300 | 111300
| vii | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete (Metal measured in stacks will be reduced by 8% for voids). |  | Cu. M | 1200 | 180 | 216000 | 180 | 216000 | 180 | 216000
| viii (a) | Construction of 4.0 Mtr wide Cement Concrete Road on hard soil or hard moorum as per given drawing including cost of mixture machine, vibrator, curing all materials, T&P, labour, transportation, loading, unloading, royalty taxes etc. complete. |  | Mtr | 4133 | 120 | 495960 | 120 | 495960 | 120 | 495960
| viii (b) | Construction of 4.0 Mtr wide Cement Concrete Road on black cotton soil as per given drawing including cost of mixture machine, vibrator, curing all materials, T&P, labour, transportation, loading, unloading, royalty taxes etc. complete. | 4: Mtr; 5: 4579; 7: 0; 9: 0; 11: 0
| ix | Construction of 7.50 M long 600 mm internal dia. NP-3 Hume pipe culvert as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty taxes etc. complete. |  | No. | 33635 | 1 | 33635 | 1 | 33635 | 1 | 33635
| x | Construction of 1.0 M high (from G.L.) brick masonary retaining wall as per given drawing including all labour, material, T&P, curing, transportation, loading, unloading, royalty taxes etc. complete. |  | RM | 2156 | 130 | 280280 | 130 | 280280 | 130 | 280280 | Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
| xi | Providing filling and compacting local earth (from approved source pit) in layers not exceeding 20 cm in depth consolidating each deposited layer by ramming and watering, including dressing etc. complete |  | Cu. M | 242 | 600 | 145200 | 600 | 145200 | 600 | 145200
| xii | Sub total-1 | 7: 2893875; 9: 2893875; 11: 2893875
2 |  | EQUIPMENTS
| i | 33/11 kV transformer 1.60 MVA | 7132220091 | No | 1065077.63 | 1 | 1065077.63 | -- | -- | -- | --
|  | 33/11 kV transformer 3.15 MVA | 7132220095 | No | 3163634.22 | -- |  | 1 | 3163634.22 | -- | --
|  | 33/11 kV transformer 5.00 MVA | 7132220097 | No | 4283437.71 | -- |  | -- |  | 1 | 4283437.71
| ii | 33 kV VCB (With CT's & panel) | 4: No; 5: 412251.88; 6: --; 8: 1
|  | (i) 33 kV VCB (Without CT's & Panel) | 7131943380 | No | 303153.58 | -- |  | 1 | 303153.58 | 1 | 303153.58
|  | (ii) 33 kV Control Panel | 7131960524 | No | 39001.74 | -- |  | 1 | 39001.74 | 1 | 39001.74
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 23365.52 | -- |  | 3 | 70096.56 | 3 | 70096.56
| iii | 11 kV VCB for X'mer protection (With CTs & panel) | 4: No; 5: 231555.28; 6: 1; 8: 1; 10: 1
|  | (i) 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 149663.06 | 1 | 149663.06 | 1 | 149663.06 | 1 | 149663.06
|  | (ii) 11 kV Control Panel for Transformer Protection | 7131960522 | Each | 38434.25 | 1 | 38434.25 | 1 | 38434.25 | 1 | 38434.25
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | No | 14485.99 | 3 | 43457.97 | 3 | 43457.97 | 3 | 43457.97
| iv | 11 kV VCB for feeder protection with CTs & panel. | 4: No; 5: 437239; 6: 2; 8: 2; 10: 3
|  | (i) 11 kV VCB with Relay & Control Panel | 7131960497 | No | 175161.53 | 2 | 350323.06 | 2 | 350323.06 | 3 | 525484.59 | 7131941762+7131960008=7131960497 | 25498.47
|  | (ii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 14485.99 | 6 | 86915.94 | 6 | 86915.94 | 9 | 130373.91
| v | 33 kV Isolator (600 A.) Set without earth switch | 7131930752 | No | 43236.47 | 2 | 86472.94 | 2 | 86472.94 | 2 | 86472.94
| vi | 11 kV Isolator (600 A.) (including 2 Nos. for capacitor bank) Set | 7131930663 | No | 24983.38 | 6 | 149900.28 | 6 | 149900.28 | 8 | 199867.04
| vii | 33 kV DO Fuse unit | 7131930415 | Each | 2729.94 | 3 | 8189.82 | 3 | 8189.82 | 9 | 24569.46
| viii | 11 kV DO Fuse unit | 7131930412 | Each | 1020.31 | 3 | 3060.93 | 3 | 3060.93 | 6 | 6121.86
| ix | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3233.2 | 3 | 9699.6 | 3 | 9699.6 | 3 | 9699.6
| x | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 348.68 | 12 | 4184.16 | 12 | 4184.16 | 15 | 5230.2
| xi | 33 kV AB Switch | 7131930321 | Each | 22715.4 | 1 | 22715.4 | 1 | 22715.4 | 1 | 22715.4
| xii | 11 kV AB Switch | 7131930221 | Each | 10230.88 | 3 | 30692.64 | 3 | 30692.64 | 4 | 40923.52
| xiii | Single phase 33 kV PT | 7132230057 | Each | 19641.7 | 3 | 58925.1 | 3 | 58925.1 | 3 | 58925.1
| xiv | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 83656.01 | 1 | 83656.01 | 1 | 83656.01 | 1 | 83656.01
| xv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 41332.3 | 2 | 82664.6 | 2 | 82664.6 | 3 | 123996.9
| xvi | Single phase 11 kV PT's | 7132230056 | Each | 12242.87 | 3 | 36728.61 | 3 | 36728.61 | 3 | 36728.61
| xvii | LT Meter (CT Operated) 100/5 A with CT's | 4: No; 5: 3495.47; 6: 1; 8: 1; 10: 1
|  | (i) LT Meter (CT Operated) 100/5 A | 7131310997 | No | 1913.09 | 1 | 1913.09 | 1 | 1913.09 | 1 | 1913.09
|  | (ii) LT CT 100/5 A | 7132230016 | No | 527.46 | 3 | 1582.38 | 3 | 1582.38 | 3 | 1582.38
| xviii | H.T. STATIC TRIVECTOR METERS | 4: No; 5: 12235.68; 6: 3; 8: 3; 10: 4
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 4078.56 | 3 | 12235.68 | 3 | 12235.68 | 4 | 16314.24
| xix | Lead Acid Battery with automatic charger | 4: No; 5: 71728.47; 6: 1; 8: 1; 10: 1
|  | (i) Battery | 7132404366 | No | 58920.28 | 1 | 58920.28 | 1 | 58920.28 | 1 | 58920.28
| 1 | (ii) Battery Charger | 7132468558 | No | 12808.19 | 1 | 12808.19 | 1 | 12808.19 | 1 | 12808.19
| xx | 33/0.4 kV station transformer (50 kVA) | 7132210215 | Each | 139656.84 | 0 | 0 | 0 | 0 | 2 | 279313.68
| xxi | Energy efficient 11/0.4 kV station transformer (100 kVA) [LEVEL-2] * | 7132210020 | Each | 131034.24 | 1 | 131034.24 | 1 | 131034.24
| xxii | LT Distribution box for 63 kVA X'mer | 7131950065 | Each | 17597.77 | 0 | 0 | 0 | 0 | 2 | 35195.54
| xxiii | LT Distribution box for 100 kVA X'mer | 7131950105 | Each | 21998.12 | 1 | 21998.12 | 1 | 21998.12
| xxiv | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 6 Nos = 2448.6 Kgs | 7130601958 | Kg | 62.81 | 2448.6 | 153796.566 | 2448.6 | 153796.566 | 2448.6 | 153796.566
| xxv | Control cable
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr. | 204.44 | 360 | 73598.4 | 360 | 73598.4 | 480 | 98131.2
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr. | 107.4 | 360 | 38664 | 360 | 38664 | 510 | 54774
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr. | 61.25 | 180 | 11025 | 240 | 14700 | 300 | 18375
| xxvi | Tee Clamp for Dog Conductor | 7130830585 | No | 350.63 | 96 | 33660.48 | 96 | 33660.48 | 108 | 37868.04
| xxvii | Danger Board for 33 kV & 11 kV equipment / supply pole | 7130880041 | No | 123.66 | 10 | 1236.6 | 10 | 1236.6 | 10 | 1236.6
| xxviii | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 83.25 | 300 | 24975 | 300 | 24975 | 300 | 24975
| xxix | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3724.89 | 5 | 18624.45 | 5 | 18624.45 | 6 | 22349.34
| xxx | Sub-total - 2 | 7: 2906834.476; 9: 5421317.946; 11: 7099563.156
3 |  | STRUCTURE AND BUS BAR ARRANGEMENTS: -
| i | 8 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x8 mtr =296.8 kg/pole x 10 Nos = 2968 Kgs. | 7130601958 | Kg | 62.81 | 2968 | 186420.08 | 2968 | 186420.08 | 3561.6 | 223704.096
| ii | 7 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x7mtr = 259.7 Kg/pole x 4 Nos = 1038.8 Kgs. | 7130601958 | Kg | 62.81 | 1038.8 | 65247.028 | 1038.8 | 65247.028 | 1038.8 | 65247.028
| iii | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 8 Nos = 3264.8 Kgs | 7130601958 | Kg | 62.81 | 3264.8 | 205062.088 | 3264.8 | 205062.088 | 4081 | 256327.61
| iv | MS DC Cross arm (100 x 50 x 6 mm Channel) 5.2 Mtr long Set | 7130810684 | No | 10516.35 | 22 | 231359.7 | 22 | 231359.7 | 28 | 294457.8
| v | MS DC Cross arm (100 x 50 x 6 mm Channel) 3.8 Mtr long Set | 7130810006 | Set | 8465.81 | 2 | 16931.62 | 2 | 16931.62 | 9 | 76192.29
| vi | MS DC Cross arm (100 x 50 x 6 mm Channel) 2.7 Mtr long Set | 7130810608 | Set | 6686.34 | 9 | 60177.06 | 9 | 60177.06 | 11 | 73549.74
| vii | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 2065.47 | 1 | 2065.47 | 1 | 2065.47 | 2 | 4130.94
| viii | R.S. Joist (175x85 mm) | 7130600675 | Kg | 67.13 | 468 | 31416.84 | 468 | 31416.84 | 546 | 36652.98
| ix | ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr | 95.46 | 500 | 47730 | 500 | 47730 | 600 | 57276
| x | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 333.95 | 6 | 2003.7 | 6 | 2003.7 | 9 | 3005.55
| xi | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 148.62 | 9 | 1337.58 | 12 | 1783.44 | 12 | 1783.44
| xii | Polymer Disc Insulator for 33 kV Side | 7130820013 | Each | 204.36 | 81 | 16553.16 | 81 | 16553.16 | 81 | 16553.16
| xiii | 33 kV Strain Hardware fitting | 7130820248 | Each | 304.86 | 81 | 24693.66 | 81 | 24693.66 | 102 | 31095.72
| xiv | Polymer Disc insulator for 11 kV side (double disc) | 7130820010 | Each | 126.83 | 108 | 13697.64 | 108 | 13697.64 | 150 | 19024.5
| xv | 33 kV Strain Plate 8 mm thick | 7130810624 | Each | 118.53 | 198 | 23468.94 | 198 | 23468.94 | 246 | 29158.38
| xvi | Red Oxide Paint | 7130211158 | Ltr | 181.98 | 40 | 7279.2 | 40 | 7279.2 | 45 | 8189.1
| xvii | Aluminium Paint | 7130210809 | Ltr | 406.6 | 40 | 16264 | 40 | 16264 | 45 | 18297
| xviii | Sub-total - 3 | 7: 951707.766; 9: 952153.626; 11: 1214645.334
4 |  | OTHER MISCELLANEOUS ITEMS: -
| i | Concreting of structures & foundation (1:3:6) | 7130200202 | Cmt | 2970 | 51.6 | 153252 | 60.6 | 179982 | 67.2 | 199584 | Material cost including GST and labour.
| ii | PVC insulated Single Core 70 Sqmm Armoured cable. | 7130311010 | Mtr. | 92.03 | 10 | 920.3 | 10 | 920.3 | 10 | 920.3
| iii | 16 Sqmm 4-core Cable for Switch yard lighting, tripping arrangement & system control (armoured) | 7130311084 | Mtr. | 76.68 | 300 | 23004 | 300 | 23004 | 300 | 23004
| iv | 18 W LED Street Light complete set | 7131210030 | Set | 2379.23 | 4 | 9516.92 | 4 | 9516.92 | 4 | 9516.92
| v | 70 W LED Street Light complete set | 7131210032 | Set | 4347.8 | 6 | 26086.8 | 6 | 26086.8 | 6 | 26086.8
| vi | AC Distribution board for AC/DC Supply | 7131920028 | No | 11255.65 | 1 | 11255.65 | 1 | 11255.65 | 1 | 11255.65
| vii | Fixing of 33/11 kV S/S (Name Plate) Board made up of 2 mm thick MS Sheet of size 5'x8' as per approved drawing. | 7132406800 | Job | 11594.76 | 1 | 11594.76 | 1 | 11594.76 | 1 | 11594.76
| viii | Earthing of Sub-station including Distribution Transformer earthing. | bar: 4; 6; 8; 10
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 5382.12 | 21 | 113024.52 | 21 | 113024.52 | 21 | 113024.52
|  | (ii) GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 1058.93 | 40 | 42357.2 | 40 | 42357.2 | 40 | 42357.2
|  | (iii) MS flat 50x6 mm size (2.5 kg per meter) | 7130600173 | Kg | 63.06 | 1000 | 63060 | 1000 | 63060 | 1000 | 63060
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 87.81 | 31 | 2722.11 | 31 | 2722.11 | 31 | 2722.11
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 113.09 | 25 | 2827.25 | 25 | 2827.25 | 25 | 2827.25
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 113.09 | 10 | 1130.9 | 10 | 1130.9 | 10 | 1130.9
|  | (vii) GI Spring washers | 7130622922 | Kg | 185.92 | 5 | 929.6 | 5 | 929.6 | 5 | 929.6
|  | MS Nuts & Bolts | 4: Kg; 6: 186; 8: 270; 10: 270
|  | (i) MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 81.75 | 10 | 817.5 | 15 | 1226.25 | 15 | 1226.25
|  | (ii) MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 80.39 | 5 | 401.95 | 10 | 803.9 | 10 | 803.9
|  | (iii) MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 80.39 | 15 | 1205.85 | 25 | 2009.75 | 25 | 2009.75
|  | (iv) MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 79.02 | 66 | 5215.32 | 85 | 6716.7 | 85 | 6716.7
|  | (v) MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 79.02 | 80 | 6321.6 | 110 | 8692.2 | 110 | 8692.2
|  | (vi) MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 79.02 | 10 | 790.2 | 25 | 1975.5 | 25 | 1975.5
| ix | Furniture
|  | (i) Table 4'x2.5' |  | No | 5780 | 1 | 5780 | 1 | 5780 | 1 | 5780
|  | (ii) Chair | 7132409830 | No | 2914.6 | 2 | 5829.2 | 2 | 5829.2 | 2 | 5829.2
|  | (iii) Small Steel Almirah 50'' | 7132401672 | No | 5450 | 1 | 5450 | 1 | 5450 | 1 | 5450
| x | Fire fighting equipments | bar: 4
|  | (i) Fire fighting equipments (dry chemical powder type 5 Kg capacity) | 7132490006 | No | 5357.02 | 2 | 10714.04 | 2 | 10714.04 | 2 | 10714.04
|  | (ii) Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | 7132421002 | No | 5990.38 | 2 | 11980.76 | 2 | 11980.76 | 2 | 11980.76
| xi | Electrically insulated 11 kV mats infront of electrical control panel | 7132448003 | No | 4928.43 | 3 | 14785.29 | 3 | 14785.29 | 3 | 14785.29
| xii | Sub-total - 4 | 7: 530973.72; 9: 564375.6; 11: 583977.6
5 |  | Total material cost including Civil works & GST both | 7: 7283390.962; 9: 9831722.172; 11: 11792061.09
6 |  | Total material cost including Civil works but excluding GST (Row 5 / 1.18) | 7: 6172365.222; 9: 8331967.9424; 11: 9993272.1102
7 |  | Incidental Charges @ 7.5 % on " Row-5 " above (Row 5 * 0.075) | 5: 0.075; 7: 546254.3221; 9: 737379.1629; 11: 884404.5818
8 | (i) | Services on S/s earthing |  | No | 30213.9869 | 1 | 30213.9869 | 1 | 30213.9869 | 1 | 30213.9869
| (ii) | Services on Cable trench (separate trench for power cable & control cable). |  | RM | 2155 | 70 | 150850 | 70 | 150850 | 80 | 172400
| (iii) | Services on Painting of structures |  | No | 19446.815 | 1 | 19446.815 | 1 | 19446.815 | 1 | 19446.815
| (iv) | Services on Labelling of equipments |  | No | 16205.6791 | 1 | 16205.6791 | 1 | 16205.6791 | 1 | 16205.6791
9 |  | Labour charges as per sch. (BL-1+BL-3) | 7: 232912.2; 9: 248589.26; 11: 282704.85
10 |  | Labour charges for concreting |  | Cmt | 665.1732 | 51.6 | 34322.9365 | 60.6 | 40309.4951 | 67.2 | 44699.6382
11 |  | Transport charges @ 4% on Column no. 06 | 7: 246894.6089; 9: 333278.7177; 11: 399730.8844
12 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 5, 7, 8 [(i), (ii), (iii), (iv)], 9, 10, 11, | 7: 1070061.4388; 9: 1425999.4111; 11: 1705233.4407
13 |  | Total estimated cost of Sub-station (Including Civil works but excluding GST) [Row = 6, 7, 8 [(i), (ii), (iii), (iv)], 9, 10, 11, 12, | 7: 8519527.2094; 9: 11334240.4703; 11: 13548311.9862
14 |  | Total Cost (Rs In lakhs) | 7: 85.1953; 9: 113.3424; 11: 135.4831
15 |  | Applicable CGST @ 9% on Row 13 | 5: 0.09; 7: 766757.4488; 9: 1020081.6423; 11: 1219348.0788
16 |  | Applicable SGST @ 9% on Row 13 | 5: 0.09; 7: 766757.4488; 9: 1020081.6423; 11: 1219348.0788
17 |  | Grand Total estimated cost of S/s including GST (Row 13+15+16). | 7: 10053042.1071; 9: 13374403.7549; 11: 15987008.1438
18 |  | Grand Total estimated cost including GST (Rounded off) | 7: 10053042; 9: 13374404; 11: 15987008
19 |  | Grand Total cost (Rs in LAKHS) | 7: 100.5304; 9: 133.744; 11: 159.8701
Note:
| (1) | All the rates are with considering price variation clause.
| (2) | In case of non-availability of H-Beam for structure double welded RS Joist may be used (1) 8 meter long double welded RS Joist and cost of it shall be taken in place of cost of item No.3 (i) unit rate as Rs 10640.00 & quantity should be 10 Nos for 3.15 & 1.6 MVA and 12 Nos for 5 MVA (2) 7 meter long double welded RS Joist and cost of it shall be taken as in place of cost of item No.3 (ii) unit rate as Rs 9372.00 & quantity should be 04 Nos each for 3.15 & 1.6 MVA and 5 MVA
| (3) | The cost of land is not taken in to account since normally CSPDCL acquires Govt. land at negligible cost. How ever needs to be procure other than Govt. land then should be added actual cost.
| * | ISI Marked Energy Efficiency level-2 transformer
Note on H25: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
Note on J25: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
Note on L25: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
Note on C135: Barun Chakraborty: Earlier name was - Transport charges

## B-3
COST SCHEDULE B-3
|  |  | ( 33 kV SUB-STATIONS ) |  |  |  |  | 2022-23
SCHEDULE FOR INSTALLATION OF ADDITIONAL TRANSFORMER FOR PARALLEL OPERATION WITH TWO ADDITIONAL BAY ON 11 kV SIDE
S. No. | S.No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | Sub-station capacity |  |  | Reason
[7 empty] | 1.6 MVA | 3.15 MVA | 5.0 MVA
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 |  | EQUIPMENTS
| i | Power Transformer 33/11 kV
|  | Power Transformer 1.6 MVA | 7132220091 | No | 1065077.63 | 1 | 1065077.63
|  | Power Transformer 3.15 MVA | 7132220095 | No | 3163634.22 | 1 |  | 3163634.22
|  | Power Transformer 5 MVA | 7132220097 | No | 4283437.71 | 1 |  |  | 4283437.71
| ii | 33 kV VCB with CT's and panels. |  | No | 412251.88
|  | (i) 33 kV VCB ( without CT's and panels) | 7131943380 | No | 303153.58 | 1 |  | 303153.58 | 303153.58
|  | (ii) 33 kV Control Panel | 7131960524 | No | 39001.74 | 1 |  | 39001.74 | 39001.74
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 23365.52 | 3 |  | 70096.56 | 70096.56
| iii | 11 kV VCB for X'mer protection with CT's and panels. |  | No | 231555.28 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | Each | 149663.06 | 1 | 149663.06 | 149663.06 | 149663.06
|  | (ii) 11 kV Control Panel for X-mer Protection | 7131960522 | Each | 38434.25 | 1 | 38434.25 | 38434.25 | 38434.25
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | Each | 14485.99 | 3 | 43457.97 | 43457.97 | 43457.97
| iv | 11 kV VCB for feeder protection with CT's and panels. |  | No | 437239 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | No | 149663.06 | 2 | 299326.12 | 299326.12 | 299326.12
|  | (ii) 11 kV Control Panel for feeder protection | 7131960008 | Each | 25498.47 | 2 | 50996.94 | 50996.94 | 50996.94
|  | (iii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 14485.99 | 6 | 86915.94 | 86915.94 | 86915.94
| v | 33 kV DO Fuse Unit | 7131930415 | Each | 2729.94 | 3 | 8189.82
| vi | 33 kV isolator, 600 A. Without earth switch | 7131930752 | No | 43236.47 | 3 | 129709.41 | 129709.41 | 129709.41
| vii | 11 kV isolator, 600 A | 7131930663 | No | 24983.38 | 5 | 124916.9 | 124916.9 | 124916.9
| viii | 33 kV Polymer Lightning Arrestor | 7130840021 | Each | 3233.2 | 3 | 9699.6 | 9699.6 | 9699.6
| ix | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 348.68 | 9 | 3138.12 | 3138.12 | 3138.12
| x | H.T. STATIC TRIVECTOR METERS |  | No | 12235.68
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 4078.56 | 3 | 12235.68 | 12235.68 | 12235.68
| xi | 33 kV Single Phase PT | 7132230057 | Each | 19641.7 | 3 | 58925.1 | 58925.1 | 58925.1
| xii | 11 kV Single Phase PT | 7132230056 | Each | 12242.87 | 3 | 36728.61 | 36728.61 | 36728.61
| xiii | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 83656.01 | 1 | 83656.01 | 83656.01 | 83656.01
| xiv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 41332.3 | 2 | 82664.6 | 82664.6 | 82664.6
| xv | 33 kV AB switch | 7131930321 | Each | 22715.4 | 0 | 0 | 0 | 0
| xvi | 11 kV AB switch | 7131930221 | Each | 10230.88 | 2 | 20461.76 | 20461.76 | 20461.76
| xvii | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3724.89 | 5 | 18624.45 | 18624.45 | 18624.45
2 |  | STRUCTURE AND BUS BAR ARRANGEMENT
| (i) | DO fuse supporting structure set on 7 Mtr long H- Beam 37.1 kg/mtr 33 kV & 11 kV side (2 No. each side) i.e. 37.1 kg x 7 = 259.7 kg/pole x 4 Nos = 1038.8 Kgs | 7130601958 | Kg | 62.81 | 1038.8 | 65247.028 | 65247.028 | 65247.028
| (ii) | 33 kV additional bay ( 02 No H-Beam 152x152 mm 08 mtr long) with 6 Nos, 5.2 Mtr channel |  | Set | 158698.832 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.20 Kgs | 7130601958 | Kg | 62.81 | 1187.2 | 74568.032 | 74568.032 | 74568.032
|  | (ii) D.C.Cross arm Channel 5.2 mtr 100x50 mm | 7130810684 | No | 10516.35 | 8 | 84130.8 | 84130.8 | 84130.8
| (iii) | 11 kV, 2 Addl. bus bar structure 08 mtr long H- Beam 37.1 Kg/mtr with 4 Nos, 5.2 Mtr long DC cross arm (100 x 50 mm) |  | Set | 503519.696 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.2 Kgs. | 7130601958 | Kg | 62.81 | 1187.2 | 74568.032 | 74568.032 | 74568.032
|  | (ii) H-Beam 152x152 mm 11 mtr long 37.1 kg/mtr i.e.= 408.1 kg/pole x 4 No = 1632.40 Kgs | 7130601958 | Kg | 62.81 | 1632.4 | 102531.044 | 102531.044 | 102531.044
|  | (iii) R.S. Joist (175x85 mm) [ 8x2 Mtr ] | 7130600675 | Kg | 67.13 | 273 | 18326.49 | 18326.49 | 18326.49
|  | (iv) D.C.Cross arm Channel 5.2 mtr 100x50 mm (set) | 7130810684 | No | 10516.35 | 24 | 252392.4 | 252392.4 | 252392.4
|  | (v) D.C.Cross arm 5 ft. Centre 100x50 mm Channel | 7130810608 | Set | 8465.81 | 5 | 42329.05 | 42329.05 | 42329.05
|  | (vi) D.C.Cross arm 8 ft. Centre 100x50 mm Channel | 7130810517 | Set | 6686.34 | 2 | 13372.68 | 13372.68 | 13372.68
| (iv) | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 83.25 | 300 | 24975 | 24975 | 24975
| (v) | ACSR Dog conductor | 7130830063 | Mtr | 95.46 | 300 | 28638 | 28638 | 28638
| (vi) | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 333.95 | 3 | 1001.85 | 1001.85 | 1001.85
| (vii) | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 148.62 | 6 | 891.72 | 891.72 | 891.72
| (viii) | Strain hardware with strain set suitable for Dog conductor: -
|  | (a) 33 kV side with 3 disc insulator per phase. |  | Set | 36663.84 | 18
|  | (i) 33 kV Polymer Disc insulator . | 7130820013 | No | 204.36 | 72 | 14713.92 | 14713.92 | 14713.92
|  | (ii) 33 kV Strain Hardware | 7130820248 | Each | 304.86 | 72 | 21949.92 | 21949.92 | 21949.92
|  | (b) 11 kV side with 2 disc insulator per phase. |  | Set | 13714.44
|  | (i) 11 kV Polymer Disc insulator | 7130820010 | No | 126.83 | 12 | 1521.96 | 1521.96 | 1521.96
|  | (ii) 33 kV Strain Hardware | 7130820248 | No | 304.86 | 12 | 3658.32 | 3658.32 | 3658.32
|  | (iii) Strain plate 8 mm thick | 7130810624 | No | 118.53 | 72 | 8534.16 | 8534.16 | 8534.16
| (ix) | T-clamp for jumper connection with AB Switches & DO fuses / Isolator. | 7130830585 | No | 350.63 | 96 | 33660.48 | 33660.48 | 33660.48
| (x) | Stay Clamp for "H" Beam | 7130810692 | Pair | 447.87 | 42 | 18810.54 | 18810.54 | 18810.54
| (xi) | Red Oxide Paint | 7130211158 | Ltr | 181.98 | 6 | 1091.88 | 1091.88 | 1091.88
| (xii) | Aluminium Paint | 7130210809 | Ltr | 406.6 | 6 | 2439.6 | 2439.6 | 2439.6
3 |  | OTHER MISCELLANEOUS ITEMS
| i | Concreting of structure @ 0.45 Cmt. per bus structure (1:3:6) = 7.2 Cmt for 16 Nos structure. | 7130200202 | Kg | 2970 | 8.6 | 25542 | 25542 | 25542 | Material cost including GST and labour.
| ii | Concreting of Transformer foundation (1:3:6) = 15 cmt | 7130200202 | Kg | 2970 | 15 | 44550 | 44550 | 44550 | Material cost including GST and labour.
| iii | Concreting of 11 kV VCB foundation (1:3:6) = 18 cmt. | 7130200202 | Kg | 2970 | 18 | 53460 | 53460 | 53460 | Material cost including GST and labour.
| iv | Concreting of 33 kV VCB foundation (1:3:6) = 7 cmt. | 7130200202 | Kg | 2970 | 7 | 20790 | 20790 | 20790 | Material cost including GST and labour.
| v | Control cable for Xmer & VCB
|  | a) 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 204.44 | 180 | 36799.2 | 36799.2 | 36799.2
|  | b) 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 107.4 | 720 | 77328 | 77328 | 77328
|  | c) 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 61.25 | 180 | 11025 | 11025 | 11025
| vi | Earthing for addl X'mer & VCB
Document – As per W/o of G.S. Flat mesh earthing of 33/11 kV S/s as per No. CE/RR/TR/4328/9029 Raipur, Dt. 05/03/2007 (Rate taken from Sch.- III)
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 5382.12 | 9 | 48439.08 | 48439.08 | 48439.08
|  | (ii) GI Pipe of 40 mm dia 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 1058.93 | 24 | 25414.32 | 25414.32 | 25414.32
|  | (iii) MS flat 50x6 mm size | 7130600173 | Kg | 63.06 | 400 | 25224 | 25224 | 25224
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 87.81 | 31 | 2722.11 | 2722.11 | 2722.11
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 113.09 | 25 | 2827.25 | 2827.25 | 2827.25
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 113.09 | 10 | 1130.9 | 1130.9 | 1130.9
|  | (vii) GI Spring washers | 7130622922 | Kg | 185.92 | 5 | 929.6 | 929.6 | 929.6
| vii | M.S. Nut- Bolts |  | Kg |  | 213
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 81.75 | 10 | 817.5 | 817.5 | 817.5
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 80.39 | 8 | 643.12 | 643.12 | 643.12
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 80.39 | 25 | 2009.75 | 2009.75 | 2009.75
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 79.02 | 70 | 5531.4 | 5531.4 | 5531.4
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 79.02 | 80 | 6321.6 | 6321.6 | 6321.6
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 79.02 | 20 | 1580.4 | 1580.4 | 1580.4
4 |  | SUB TOTAL - A (1+2+3) [Material cost including GST] |  |  |  |  | 3605260.106 | 6107878.756 | 7227682.246
5 |  | Material cost excluding GST (Sub Total- A / 1.18) |  |  |  |  | 3055305.1746 | 5176168.4373 | 6125154.4458 | NEW ROW ADDED
6 |  | Incidental Charges @ 7.5% on Sub-Total - A : - |  |  | 0.075 |  | 270394.5079 | 458090.9067 | 542076.1684 | Earlier name was - Incidental Charges @ 9%
7 |  | (i) Services on Earthing |  | No. | 13396.6959 | 1 | 13396.6959 | 13396.6959 | 13396.6959 | No. of earthing = 6; services on 6 earthing =6x1943=11658/-
|  | (ii) Services on Painting |  | No. | 19446.815 | 1 | 19446.815 | 19446.815 | 19446.815
|  | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete (Metal measured in stacks will be reduced by 8% for voids). |  | Cmt | 1200 | 45 | 54000 | 54000 | 54000 | NAME CHANGED
|  | Services on Labelling of equipments |  | No | 16205.679 | 1 | 16205.679 | 16205.679 | 16205.679
|  | Services on X'mer foundation [2.5(L)*2(W)*3(H)] |  | Cmt | 4902.9546 | 15 | 73544.3184 | 73544.3184 | 73544.3184
|  | Services on foundation of 11 kV VCB [2(L)*2(W)*1.5(H)] |  | Cmt | 4902.9546 | 18 | 88253.1821 | 88253.1821 | 88253.1821
|  | Services on foundation of 33 kV VCB [2(L)*2(W)*1.75(H)] |  | Cmt | 4902.9546 | 7 | 34320.6819 | 34320.6819 | 34320.6819
|  | Construction of brick masonry cable trench with cover |  | RM | 2155 | 45 | 96975 | 96975 | 96975
8 |  | Labour charges: - |  |  |  |  | 255701.6469 | 268742.6469 | 280127.6469
| i | X'mer erection (Labour sch BL-3) |  |  |  |  | 61065 | 74106 | 85491
| ii | Other items as per schedule [Labour Schedule BL-2+(4*BL-4)] |  |  |  |  | 162309.23 | 162309.23 | 162309.23
| iii | Labour charges for concreting |  | Cmt | 665.1732 | 48.6 | 32327.4169 | 32327.4169 | 32327.4169
9 |  | Transport charges @ 4 % on material excluding GST |  |  |  |  | 122212.207 | 207046.7375 | 245006.1778
10 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 4, 6, 7, 8, 9 |  |  |  |  | 581213.855 | 929737.6774 | 1086379.3264
11 |  | Total Estimated Cost excluding GST (Row 5, 6, 7, 8, 9, 10) |  |  |  |  | 4680969.7636 | 7435928.778 | 8674886.1376
12 |  | Applicable CGST @ 9% on Row 11 |  |  | 0.09 |  | 421287.2787 | 669233.59 | 780739.7524
13 |  | Applicable SGST @ 9% on Row 11 |  |  | 0.09 |  | 421287.2787 | 669233.59 | 780739.7524
14 |  | Total estimated cost of S/s including GST (Row 11+12+13). |  |  |  |  | 5523544.3211 | 8774395.9581 | 10236365.6424
15 |  | Total estimated cost of S/s including GST (Rounded off) |  |  |  |  | 5523544 | 8774396 | 10236366
Note: |  | (1) All the rates are with considering price variation clause.
(2) In case of non-availability of H-Beam for structure double welded RS Joist may be used and cost should be taken on actual material used
*
Note on C31: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category A
Note on C92: Barun Chakraborty: Earlier name was - SUB TOTAL - A (1+2+3)
Note on C97: 89326879: Earlier name was - Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete and including spreading in 100 mm thick layers complete (Metal measured in stacks will be reduced by 8% for voids).
Note on E102: 89326879: Earlier unit taken as Mtr

## B-4
COST SCHEDULE B-4
|  | (33/11 kV SUB-STATIONS) |  |  |  |  | 2022-23
11 kV OUT DOOR YARD EXTENSION FOR ADDL. BAY WITH CIRCUIT BREAKER
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | 1.6 MVA & Above
[6 empty] | Qnty | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | H-Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 No = 593.6 Kgs | 7130601958 | Kg | 62.81 | 594 | 37309.14
2 |  | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1 x 11 mtr = 408.1 kg/pole x 2 Nos = 816.2 Kgs. | 7130601965 | Kg | 62.4 | 816.2 | 50930.88
3 |  | MS DC Cross arm (100x50 mm), 5.2 Mtr long for bus bar | 7130810684 | Set | 10516.35 | 6 | 63098.1
4 |  | MS DC Cross arm (100x50 mm), 8' centre for bus bar | 7130810517 | Set | 6686.34 | 2 | 13372.68
5 |  | Strain set with hardware suitable for 100 Sqmm ACSR conductor for 11 kV bus. |  | Set |  | 21
| (i) | 11 kV Polymer Disc insulator for double disc | 7130820010 | No | 126.83 | 42 | 5326.86
| (ii) | Hardware suitable for 100 Sqmm ACSR Dog conductor for 11 kV bus. | 7130820248 | No | 304.86 | 21 | 6402.06
6 |  | 11 kV Polymeric Pin insulator with Pin | 7130820008 | Each | 148.62 | 3 | 445.86
7 |  | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 348.68 | 3 | 1046.04
8 |  | 11 kV Isolator (600 A.) | 7131930663 | Each | 24983.38 | 2 | 49966.76
9 |  | 11 kV AB Switch | 7131930221 | Each | 10230.88 | 1 | 10230.88
10 |  | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2970 | 1.8 | 5346 | Material cost including GST and labour.
11 |  | ACSR 100 Sqmm Al. Eq. Dog Conductor | 7130830063 | Mtr | 95.46 | 50 | 4773
12 |  | Terminal clamp for jumpering of 100 Sqmm Al. Eq ACSR Conductor / Isolator | 7130830585 | No | 350.63 | 24 | 8415.12
13 |  | 11 kV feeder control VCB with CT's (One 11 kV VCB controlling two feeders) with control panel. |  | No | 222344.39 | 1
| (i) | 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 149663.06 | 1 | 149663.06
| (ii) | 11 kV feeder Control Panel | 7131960008 | No | 25498.47 | 1 | 25498.47
| (iii) | 11 kV CT's 300-150/5 Amps | 7132230188 | No | 14485.99 | 3 | 43457.97
| (iv) | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3724.89 | 1 | 3724.89
14 |  | Concreting of foundation of VCB (1:3:6) | 7130200202 | Cmt | 2970 | 6 | 17820 | Material cost including GST and labour.
15 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 204.44 | 60 | 12266.4
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 107.4 | 120 | 12888
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 61.25 | 60 | 3675
16 |  | H.T. STATIC TRIVECTOR METER for feeder metering. |  | No | 4078.56 | 1
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 4078.56 | 1 | 4078.56
17 |  | 11 kV CT/PT unit 200-100/5 Amp. | 7132230412 | Each | 41332.3 | 1 | 41332.3
18 |  | Red Oxide Paint | 7130211158 | Ltr | 181.98 | 2 | 363.96
19 |  | Aluminium Paint | 7130210809 | Ltr | 406.6 | 2 | 813.2
20 |  | M.S. Nuts & Bolts |  | Kg |  | 30
| a | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 81.75 | 3 | 245.25
| b | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 80.39 | 2 | 160.78
| c | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 80.39 | 2 | 160.78
| d | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 79.02 | 6 | 474.12
| e | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 79.02 | 15 | 1185.3
| f | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 79.02 | 2 | 158.04
21 |  | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 574629.46
22 |  | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 486974.1186
23 |  | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 43097.2095
24 | a | Services on Painting of structure |  | No | 4537.5902 | 1 | 4537.5902
| b | Construction of brick masonry cable trench with cover |  | RM | 2155 | 5 | 10775
25 |  | Labour charges |  |  |  |  | 36729.9009
| i | as per Schedule No. BL-4 |  |  |  |  | 31541.55
| ii | for concreting of structure |  | Cmt | 665.1732 | 1.8 | 1197.3117
| iii | for foundation of VCB |  | Cmt | 665.1732 | 6 | 3991.0391
26 |  | Transport charges @ 4% on Column no. 22 |  |  |  |  | 19478.9647 | NAME CHANGED
27 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 21, 23, 24, 25, 26 |  |  |  |  | 86156.0157
28 |  | Total Estimated Cost excluding GST (Row 22, 23, 24, 25, 26, 27) |  |  |  |  | 687748.7996
29 |  | Applicable CGST @ 9% on Row 28 |  |  | 0.09 |  | 61897.392
30 |  | Applicable SGST @ 9% on Row 28 |  |  | 0.09 |  | 61897.392
31 |  | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 811543.5835
32 |  | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 811544
Note :- |  | All the rates are with considering price variation clause.
Note on C54: Barun Chakraborty: Earlier name was - Transport charges upto 50 Km lead from area stores to construction site for addl. lead refer Schedule T-2.

## B-5
COST SCHEDULE B-5
| (33/11 kV SUB-STATIONS) |  |  |  | 2022-23
33 kV OUT DOOR YARD EXTENSION FOR ADDITIONAL BAY.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 Nos = 593.6 Kgs | 7130601958 | Kg | 62.81 | 593.6 | 37284.016
2 | MS DC cross arm (100x50 mm), 5.2 Mtr. long for bus bar | 7130810684 | Set | 10516.35 | 6 | 63098.1
3 | Strain set with hardware suitable for 80 Sqmm ACSR conductor for 33 kV bus (3 disc insulator per disc) |  | Set | 13769.1 | 15
| (i) 33 kV Polymer Disc Insulator | 7130820013 | No | 204.36 | 45 | 9196.2
| (ii) 33 kV Hardware | 7130820248 | Each | 304.86 | 15 | 4572.9
4 | 33 kV Isolator (600 Amps.) without earth switch | 7131930752 | No | 43236.47 | 2 | 86472.94
5 | Terminal clamp for isolators | 7130830585 | No | 350.63 | 12 | 4207.56
6 | T-clamps for bus jumper | 7130830585 | No | 350.63 | 6 | 2103.78
7 | ACSR 100 Sqmm Al. Eq. Conductor | 7130830063 | Mtr | 95.46 | 50 | 4773
8 | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2970 | 0.9 | 2673 | Material cost including GST and labour.
9 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | Each | 333.95 | 6 | 2003.7
10 | Red Oxide Paint | 7130211158 | Ltr | 181.98 | 2 | 363.96
11 | Aluminium Paint | 7130210809 | Ltr | 406.6 | 2 | 813.2
12 | M.S. Nuts & Bolts |  | Kg |  | 40
| MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 81.75 | 2 | 163.5
| MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 80.39 | 3 | 241.17
| MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 80.39 | 5 | 401.95
| MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 79.02 | 15 | 1185.3
| MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 79.02 | 10 | 790.2
| MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 79.02 | 5 | 395.1
13 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 220739.576
14 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 187067.4373
15 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 16555.4682
16 | Services on Painting on structure |  | No | 4537.5902 | 1 | 4537.5902
17 | Labour charges as per Schedule No BL-5 |  |  |  |  | 24006.9631
18 | Labour charges for concreting |  | Cmt | 665.1732 | 0.9 | 598.6559
19 | Transport charges @ 4% on Column no. 14 |  |  |  |  | 7482.6975
20 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 13, 15, 16, 17, 18, 19 |  |  |  |  | 34240.1189
21 | Total Estimated Cost excluding GST (Row 14, 15, 16, 17, 18, 19, 20) |  |  |  |  | 274488.931
22 | Applicable CGST @ 9% on Row 21 |  |  | 0.09 |  | 24704.0038
23 | Applicable SGST @ 9% on Row 21 |  |  | 0.09 |  | 24704.0038
24 | Total Estimated Cost including GST (Row 21+22+23) |  |  |  |  | 323896.9385
25 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 323897
Note: -For the provision of 33 kV VCB installation, the cost Schedule No.- B-6 may be referred to. All the rates are with considering price variation clause
Note on B28: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on B34: Barun Chakraborty: Earlier name was - Transport charges upto 50 Km lead from Area stores to construction site for addl. lead refer Schedule T-2.

## B-8
COST SCHEDULE B-8
AUGMENTATION OF 33/11 kV SUB-STATION CAPACITY BY REPLACEMENT OF POWER TRANSFORMER
2022-23
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | 1.6 to 3.15 MVA |  | 3.15 to 5.0 MVA without 33 kV VCB |  | 3.15 to 5.0 MVA with 33 kV VCB
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 33/11 kV 3.15 MVA X-mer | 7132220095 | No | 3163634.22 | 1 | 3163634.22 | -- | -- | -- | --
2 | 33/11 kV 5.0 MVA X-mer | 7132220097 | No | 4283437.71 | -- | -- | 1 | 4283437.71 | 1 | 4283437.71
3 | 33 kV VCB (With CT's and control panel) |  | No |  | 1 |  | -- | -- | 1
| (i) 33 kV VCB (without CT's and panels) | 7131943380 | No | 303153.58 | 1 | 303153.58 |  |  | 1 | 303153.58
| (ii) 33 kV Control Panel | 7131960524 | No | 39001.74 | 1 | 39001.74 |  |  | 1 | 39001.74
| (iii) 33 kV CT's (300-150/5) Amps | 7132230263 | No | 23365.52 | 3 | 70096.56 |  |  | 3 | 70096.56
4 | Concreting of foundation for 33 kV VCB (1:3:6) | 7130200202 | Cmt | 2970 | -- | -- | -- | -- | 7 | 20790 | Material cost including GST and labour.
5 | Control cabling
a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 204.44 | 60 | 12266.4 | 60 | 12266.4 | 60 | 12266.4
b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 107.4 | 120 | 12888 | 120 | 12888 | 120 | 12888
c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 61.25 | 60 | 3675 | 60 | 3675 | 60 | 3675
6 | Terminal clamp for transformer | 7130830586 | No | 280.2 |  |  |  |  | 7 | 1961.4
7 | T-clamps for jumper | 7130830586 | No | 280.2 | -- | -- | -- | -- | 3 | 840.6
8 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 3604715.5 |  | 4312267.11 |  | 4748110.99
9 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 3054843.6441 |  | 3654463.6525 |  | 4023822.8729 | NEW ROW ADDED
10 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 270353.6625 |  | 323420.0333 |  | 356108.3243 | Earlier name was - Incidental Charges @ 9%
11 | Labour charges as per Schedule No BL-8 |  |  |  |  | 80242.01 |  | 80242.01 |  | 80242.01
12 | Labour charges for concreting |  | Cmt | 665.1732 | -- | -- | -- | -- | 7 | 4656.2123
13 | Transport charges @ 4 % on material excluding GST |  |  |  |  | 122193.7458 |  | 146178.5461 |  | 160952.9149
14 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 08, 10, 11, 12, 13, |  |  |  |  | 509688.1148 |  | 607763.4624 |  | 668176.7799
15 | Total Estimated Cost excluding GST (Row 09, 10, 11, 12, 13, 14) |  |  |  |  | 4037321.1771 |  | 4812067.7043 |  | 5293959.1143
16 | Applicable CGST @ 9% on Row 15 |  |  | 0.09 |  | 363358.9059 |  | 433086.0934 |  | 476456.3203
17 | Applicable SGST @ 9% on Row 15 |  |  | 0.09 |  | 363358.9059 |  | 433086.0934 |  | 476456.3203
18 | (-) Cost of Old Transformer assuming 25 years of life & 5 years in service. |  |  |  |  | 712530 |  | 939310 |  | 111619
19 | Total Estimated Cost of Augmentation including GST (Row 15+16+17-18) |  |  |  |  | 4051508.989 |  | 4738929.8911 |  | 6135252.7548
20 | Total Estimated Cost of Augmentation including GST (Rounded off) |  |  |  |  | 4051509 |  | 4738930 |  | 6135253
Note:- All the rates are with considering price variation clause.
Note on B23: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on G33: Kanchan Mahesh Thakur: rates of 1996-97
Note on I33: Kanchan Mahesh Thakur: rates of 1996-97
Note on K33: Kanchan Mahesh Thakur: rates of 1996-97