## Sheet1 (hidden)
COMPARATIVE STATEMENT OF RATES FROM YEAR 2016-17 to 2017-18
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2016-17 | 2017-18 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
PART-I, 33 kV LINES AND D.P. STRUCTURES
(A) |  | 33 kV line on PCC Pole / H-Beam poles with Raccoon conductor.
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-1(i) | Per Km | 290208 | 294651 | 1.531
| ii | On H-Beam 152 x 152 mm 37.1 Kg/ Mtr 13 Mtr long | A-1(ii) | Per Km | 459820 | 457540 | -0.49585
| iii | On 365 Kg 11 Mtrs long PCC poles | A-1(iii) | Per Km | 332390 | 327410 | -1.4982
(B) |  | 33 kV Four Pole structure on PCC / H-Beam Pole | A-2 (A)
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-2 (A) (i) | Each | 234974 | 229401 | -2.3718
| ii | H-Beam Pole | A-2 (A) (ii) | Each | 292201 | 287977 | -1.4456
(C) |  | 33 kV DP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-2 (B)(i) | Each | 57588 | 54683 | -5.0445
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-2 (B)(ii) | Each | 88088 | 86977 | -1.2612
| iii | On 365 Kg 11 Mtrs long PCC poles | A-2 (B)(iii) | Each | 62662 | 61014 | -2.63
(D) |  | 33 kV line on PCC Pole / H-Beam Pole with Dog conductor.
| i | On 280 Kg, 9.1 Mtrs long PCC poles | A-3(i) | Per Km | 335828 | 346806 | 3.2689
| ii | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3(ii) | Per Km | 507332 | 509694 | 0.46557
| iii | On 365 Kg 11 Mtrs long PCC poles | A-3(iii) | Each | 378854 | 378457 | -0.10479
(E) |  | Augmentation of 1 km. of 33 kV line from Raccoon to Dog conductor. | A-3 (A) | Per Km | 217937 | 223794 | 2.6875
(F) |  | Additional (Mid Span) Pole for 33 kV Line | A-3 (B)
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3 (B)(i) | Per No. | 28510 | 28207 | -1.0628
(G) |  | 33 kV line on H-Beam supports suspension type with Panther Conductor (Maximum span of 50 Mtrs) | A-4
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-4 (i) | Per Km | 1418591 | 1401138 | -1.2303
(H) |  | 33 kV DP Structure on H-Beam supports with Panther Conductor | A-5
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-5 (i) | Each | 102479 | 101776 | -0.68599
(I) |  | 33 kV Under ground cable crossing under existing Railway track / Road for 60 Mtr long Corridor / route length of HDPE pipe under 2.5 M. deep for ground level single feeder line | A-6 | 60 Mtr
| a | Using HDD Technique
| i | With 3 core U/G XLPE 240 sqmm Cable | A-6(i) | 60 Mtr | 1036752 | 1078165 | 3.9945
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-6(ii) | 60 Mtr | 1158328 | 1200627 | 3.6517
| b | Using Pipe Pushing Method.
| i | With 3 core U/G XLPE 240 sqmm Cable | A-6(iii) | 60 Mtr | 2526667 | 2655984 | 5.1181
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-6(iv) | 60 Mtr | 2648242 | 2778446 | 4.9166
(J) |  | 33 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level single feeder line | A-6 (A) | 50 Mtr | 621183 | 622997 | 0.29202
(K) |  | Last span cabling of 33 kV H.T. Connection
|  | Using H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-7
| i | With 3x185 sq.mm AB XLPE Cable | A-7(i) | 50 Mtr | 181872 | 186985 | 2.8113
| ii | With 3x240 sq.mm AB XLPE Cable | A-7(ii) | 50 Mtr | 204432 | 209751 | 2.6018
(L) |  | 33 kV MEDP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-8 (i) | Each | 81715 | 79259 | -3.0056
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-8 (ii) | Each | 106547 | 106353 | -0.18208
(M) |  | Last span cabling of 33 kV line using Covered Conductor of size
| i | 70 sq.mm (207 Amp) | A-9 (i) | 50 Mtr | 124984 | 129377 | 3.5148
| ii | 99 sq.mm (258 Amp) | A-9 (ii) | 50 Mtr | 129998 | 134391 | 3.3793
(N) |  | Schedule for 33 kV Underground Cable crossing under Railway Track / Road for 60 Mtr. Long Corridor / Route Length of HDPE Pipe, under 2.5 Mtr. Deep from Ground Level Single Feeder Line Using Open Trench Method. | A-10 (i)
| i | With 3 core U/G XLPE 240 sqmm Cable | A-10(i) | 60 Mtr | 906066.3082 | 939768 | 3.7196
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-10(ii) | 60 Mtr | 1027642.0326 | 1062230 | 3.3658
Part-II, 33/11 kV SUB-STATIONS
(A) |  | New Sub-stations:
| i | 1.6 MVA, 33/11 kV S/s expandable to 2 x 1.6 MVA with control room | B-1(i) | Each | 6866103 | 6913029 | 0.68344
| ii | 3.15 MVA, 33/11 kV S/s expandable to 2 x 3.15 MVA with control room | B-1(ii) | Each | 8595749 | 8571098 | -0.28678
| iii | 5 MVA, 33/11 kV S/s expandable to 2 x 5 MVA with control room | B-1(iii) | Each | 10290155 | 10257514 | -0.31721
(B) |  | 33/11 kV Power Transformer
| i | 1.6 MVA | B-2(i) | Each | 933187 | 892025 | -4.4109
| ii | 3.15 MVA | B-2(ii) | Each | 2283793 | 2177129 | -4.6705
| iii | 5.0 MVA | B-2(iii) | Each | 3239383 | 3100279 | -4.2942
(C) |  | Installation of additional transformer for parallel operation with one additional bay on 11 kV side
| i | 1.6 MVA | B-3(i) | Each | 2893992 | 3379693 | 16.7831
| ii | 3.15 MVA | B-3(ii) | Each | 4572396 | 4999595 | 9.343
| iii | 5.0 MVA | B-3(iii) | Each | 5527838 | 5922555 | 7.1405
(D) |  | 11 kV Out door yard extension for additional bay with circuit breaker. | B-4 | Each | 483256 | 490515 | 1.5021
(E) |  | 33 kV Out door yard extension for additional bay without circuit breaker. | B-5 | Each | 212243 | 214257 | 0.94891
(F) |  | Installation of 33 kV VCB | B-6 | Each | 417910 | 418353 | 0.106
(G) |  | Augmentation of Power Transformer
| i | 1.6 to 3.15 MVA | B-8(i) | Each | 2660176 | 2562548 | -3.67
| ii | 3.15 to 5.0 MVA without 33 kV VCB | B-8(ii) | Each | 3251545 | 3113230 | -4.2538
| iii | 3.15 to 5.0 MVA with 33 kV VCB | B-8(iii) | Each | 3642023 | 3503832 | -3.7943
H) |  | Installation of 1.6 MVA 33/11 kV Sub-Station ON LINE | B-9 | Each | 1265650 | 1232202 | -2.6428
PART-III, 11 kV LINES AND D.P.STRUCTURES
(A) |  | 11 kV line on 140 Kg 8.0 Mtr long PCC poles with
| i | Rabbit conductor | C-1(I) | Per Km | 225086 | 224725 | -0.16038
| ii | Weasel conductor | C-1(II) | Per Km | 182425 | 183048 | 0.34151
(B) |  | 11 kV DP structure on 140 Kg, 8.0 Mtr long PCC poles | C-2 | Each | 35616 | 34966 | -1.825
PART-IV, 11 kV LINES AND D.P.STRUCTURES ON RAIL & H-BEAM
(A) |  | 11 kV line on H-Beam / PCC Pole with Rabbit conductor
| i | On H-Beam 11 meter long | C-3(i) | Per Km | 400368 | 394185 | -1.5443
| ii | On 365 Kg 11 Mtrs long PCC poles | C-3(ii) | Per Km | 284712 | 275498 | -3.2363
(B) | ii | Additional (Mid span) Poles for 11 kV Line on H-Beam | C-3 (A) | Per No. | 22159 | 21448 | -3.2086
(C) | iii | 11 kV Line on A.B.Cable | C-3 (B)
| a | Using H-Beam 152x152 mm, 37.1Kg/mtr 11 Mtrs long supports.
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[i] | Per Km | 1200223 | 1191557 | -0.72203
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[ii] | Per Km | 1335256 | 1328211 | -0.52761
| b | Using 200 Kg; 9.0 Mtr long PCC Pole
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[iii] | Per Km | 748914 | 772395 | 3.1353
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[iv] | Per Km | 883946 | 909049 | 2.8399
(D) | iv | Augmentation of 11 kV Line from Weasel to Raccoon Conductor | C-3 (C) | Per Km | 161933 | 165350 | 2.1101
(E) | v | Augmentation of 11 kV Line from Weasel to Rabbit Conductor | C-3 (D) | Per Km | 115754 | 118860 | 2.6833
(F) | vi | 11 kV Overhead XLPE Cable Line on H-Beam Pole with average span 30 Mtrs. | C-3 (E) | Per Km | 2396943 | 2430693 | 1.408
(G) |  | 11 kV DP structure on
| i | H-Beam 11 meter long | C-4(i) | Each | 67035 | 65741 | -1.9303
| ii | On 365 Kg 11 Mtrs long PCC poles | C-4(ii) | Each | 47583 | 45755 | -3.8417
(H) |  | 11 kV line on RS Joist (175X85 mm) 11.0 Meters long with
| i | Rabbit conductor | C-5(I) | Per Km | 300939 | 300432 | -0.16847
| ii | Weasel conductor | C-5(II) | Per Km | 260829 | 261456 | 0.24039
(I) |  | 11 kV DP structure on RS Joist 175X85 mm 11.0 Mtr. long | C-6 | Each | 50509 | 49946 | -1.1147
(J) |  | 11 kV line on PCC pole
| a | On 365 Kg 11 Mtrs long PCC poles
| i | Using Raccoon conductor | C-8(I) | Per Km | 327385 | 318489 | -2.7173
| ii | Using Dog conductor | C-8(II) | Per Km | 371815 | 366833 | -1.3399
(K) |  | 11 kV line on H-Beam (152x152 mm) 13 meter long with
| i | Raccoon conductor | C-9(I) | Per Km | 474359 | 468479 | -1.2396
| ii | Dog conductor | C-9(II) | Per Km | 518789 | 516824 | -0.37877
(L) |  | Additional (Mid Span) Poles for new 11 kV Line with Raccoon Conductor | C-9(A) | Per No. | 24793 | 24082 | -2.8677
(M) |  | 11 kV under ground cable crossing under railway track for 60 mtr length, under 2.5 mtr deep for ground level | C-12
| i | Using HDD Technique | C-12 (i) | 60 Mtr | 781977 | 819848 | 4.843
| ii | Using Pipe Pushing Method. | C-12 (ii) | 60 Mtr | 2271892 | 2397667 | 5.5361
(N) |  | 11 kV under ground cable Road crossing for 50 mtr length, under 2.5 mtr deep for ground level | C-12 (A) | 50 Mtr | 333362 | 334544 | 0.35457
(O) |  | Laying of 1 Km 11 kV Line using
| i | 3 Core 95 Sqmm underground cable | C-15(I) | Per Km | 926447 | 1061168 | 14.5417
| ii | 3 Core 240 Sqmm underground cable | C-15(II) | Per Km | 1407717 | 1555528 | 10.5001
| iii | 3 Core 400 Sqmm underground cable | C-15(III) | Per Km | 1982562 | 2146102 | 8.2489
(P) |  | D.T. Capacitors on existing DTR's (Retained & shifted) | C-16
| i | LT Capacitor for 25 kVA DT | C-16 (i) | Per No. | 1984 | 1984 | 0
| ii | LT Capacitor for 63 kVA DT | C-16 (ii) | Per No. | 3766 | 3766 | 0
| iii | LT Capacitor for 100 kVA DT | C-16 (iii) | Per No. | 4486 | 4486 | 0
| iv | LT Capacitor for 200 kVA DT | C-16 (iv) | Per No. | 4486 | 4486 | 0
| v | LT Capacitor for 315 kVA DT | C-16 (v) | Per No. | 4486 | 4486 | 0
(Q) |  | 11 kV MEDP Structure on H-Beam Pole
| i | 37.1 Kg /Mtrs 11 Mtrs long H-Beam supports | C-17 (i) | Each | 73838 | 72854 | -1.3326
(R) |  | New Automated 11 kV Capacitor Bank at 33/11 kV Sub-stations
| i | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. | C-18 (i) | Each | 1051129 | 1124599 | 6.9896
| ii | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . | C-18 (ii) | Each | 872674 | 946173 | 8.4223
(S) |  | Schedule for installation of compact R.M.U. 11 kV Class SF6 / VCB type (1 Incoming + 2 Breaker + 1 Outgoing) | C-19 | Each | 1166351 | 1166226 | -0.010717
(T) |  | Schedule for Chemical Earthing of Metering Equipment installed in the premises of HT consumers in normal / hard rock soil. | C-20 | Each | 12140 | 12854 | 5.8814
PART-V, 11/0.4 kV Transformer S/s.
A (A-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(I) | Each | 119446 | 113690 | -4.8189
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(II) | Each | 172454 | 169813 | -1.5314
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(III) | Each | 251071 | 241686 | -3.738
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(IV) | Each | 378952 | 373318 | -1.4867
(B-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(I) | Each | 143836 | 137866 | -4.1506
| ii | 63 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(II) | Each | 196844 | 193989 | -1.4504
| iii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11mtr long | C-7(B-1)(III) | Each | 250890 | 241328 | -3.8112
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(IV) | Each | 379297 | 373557 | -1.5133
(B-1) A |  | Relocation of 11/0.4 kV Out-door type Transformer Sub-station using H-Beam Pole and 3.5 Core PVC Cable [Based on Cost Schedule C-7 (B-1) except X-mer Cost]
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (I) | Each | 89146 | 86714 | -2.7281
| ii | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (II) | Each | 105263 | 103139 | -2.0178
| iii | 100 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (III) | Each | 123707 | 121207 | -2.0209
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr,11 mtr long | C-7(B-1) A (IV) | Each | 156292 | 153161 | -2.0033
(B-1) B |  | Renovation of Existing Distribution Transformer
| i | 25 kVA Transformer | C-7(B-1) B (I) | Each | 19827 | 22140 | 11.6659
| ii | 63 kVA Transformer | C-7(B-1) B (II) | Each | 35897 | 38302 | 6.6997
| iii | 100 kVA Transformer | C-7(B-1) B (III) | Each | 45084 | 47174 | 4.6358
| iv | 200 kVA Transformer | C-7(B-1) B (IV) | Each | 76498 | 77886 | 1.8144
| v | 315 kVA Transformer | C-7(B-1) B (V) | Each | 88994 | 90321 | 1.4911
(A-2) |  | 11/0.4 kV Out-door type Transformer sub-station using 1 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(I) | Each | 119679 | 113817 | -4.8981
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(II) | Each | 172408 | 169440 | -1.7215
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(III) | Each | 249131 | 240586 | -3.4299
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(IV) | Each | 368657 | 364826 | -1.0392
(B-2) | v | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(I) | Each | 144069 | 137992 | -4.2181
| vi | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(II) | Each | 196797 | 193616 | -1.6164
| vii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(III) | Each | 249394 | 240227 | -3.6757
| viii | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(IV) | Each | 369446 | 365065 | -1.1858
(B) |  | Augmentation of 11/.4 kV S/s capacity (Assuming 25 years of life & 10 years in service)
| i | 25 kVA to 63 kVA | C-10 (I) | Each | 130670 | 132602 | 1.4785
| ii | 63 kVA to 100 kVA | C-10 (II) | Each | 209641 | 208698 | -0.44982
| iii | 100 kVA to 200 kVA | C-10 (III) | Each | 339624 | 342792 | 0.9328
(C) | i | 11/.4 kV Out door Sub-station (16 kVA Transformer) | C-11 | Each | 115010 | 112364 | -2.3007
(D) |  | Single pole mounted low capacity Single phase / Three phase 11/.4 kV Distribution Transformer Sub-station
| i | 16 kVA Three phase | C-13(III) | Each | 92936 | 93434 | 0.53585
(E) |  | Plinth mounted 11/.4 kV Outdoor Sub-station
| i | 63 kVA Transformer | C-14(I) | Each | 223352 | 211937 | -5.1108
| ii | 100 kVA Transformer | C-14(II) | Each | 277122 | 258939 | -6.5614
| iii | 200 kVA Transformer | C-14(III) | Each | 427457 | 412870 | -3.4125
PART-VI, L.T. LINES
(A) |  | 3 phase, 5 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 4 Rabbit + 1 Squirrel | D-1(I) | Per Km | 265563 | 268958 | 1.2784
| ii | 3 Rabbit + 2 Squirrel | D-1(II) | Per Km | 245947 | 250089 | 1.6841
| iii | 4 Weasel + 1 Squirrel | D-1(III) | Per Km | 213106 | 218059 | 2.3242
| iv | 3 Weasel + 2 Squirrel | D-1(IV) | Per Km | 206605 | 211915 | 2.5701
| v | 5 Squirrel | D-1(V) | Per Km | 187100 | 193485 | 3.4126
(B) |  | 3 phase, 4 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 3 Rabbit + 1 Squirrel | D-2(I) | Per Km | 228470 | 231205 | 1.1971
| ii | 3 Weasel + 1 Squirrel | D-2(II) | Per Km | 189127 | 193031 | 2.0642
| iii | 4 Squirrel | D-2(III) | Per Km | 169622 | 174601 | 2.9354
(C) |  | 1 phase, 3 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-3(I) | Per Km | 177557 | 179745 | 1.2323
| ii | 2 Weasel + 1 Squirrel | D-3(II) | Per Km | 164442 | 167020 | 1.5677
| iii | 3 Squirrel | D-3(III) | Per Km | 151439 | 154733 | 2.1751
(D) |  | 3 Phase, 5 Wire LT line on 125 x 70 mm, 9.3 Mtrs long R.S. Joist with 3 Rabbit & 2 Weasel conductors (Span upto 45 Meters) | D-4(I) | Per Km | 362955 | 360452 | -0.68962
(E) |  | 3 Phase, 5 Wire LT line on 175 x 85 mm, 9.3 Mtrs long R.S. Joist with 3 Raccoon & 2 Weasel conductors (Span upto 65 Meters) | D-4(II) | Per Km | 395690 | 395890 | 0.050545
(F) |  | 1 Phase, 3 Wire LT line on 9.3 Mtrs long 125x70 mm R.S. Joist with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-5(I) | Per Km | 261626 | 254915 | -2.5651
| ii | 2 Weasel + 1 Squirrel | D-5(II) | Per Km | 248512 | 242190 | -2.5439
| iii | 3 Squirrel | D-5(III) | Per Km | 235509 | 229904 | -2.38
(G) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (i) | Per Km | 339492 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (ii) | Per Km | 273723 | 264172 | -3.4893
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (iii) | Per Km | 461479 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (iv) | Per Km | 395711 | 387798 | -1.9997
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6 [1] (v) | Per Km | 589306 | DELETED
| ii | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (vi) | Per Km | 523537 | 510840 | -2.4252
(H ) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (i) | Per Km | 433821 | 369101 | -14.9186 | Cable rate reduced by 23%
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| ii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (ii) | Per Km | 556663 | 493582 | -11.332
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| iii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (iii) | Per Km | 684490 | 616623 | -9.915
(I) |  | 1 phase 3 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x25+1x16+1x25 sq.mm. | D-6 [3] | Per Km | 245263 | 239794 | -2.2299
(J) |  | 3 phase 4 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 3x16+1x25 sq.mm. | D-6 [4] | Per Km | 280146 | 274079 | -2.1657
(K) |  | 3 phase 5 Wire L.T. Line on R.S.Joist (175x85) mm, 9.3 Mtr. Long (By replacement of existing bare LT conductor) for Urban area using AB XLPE Cable of size
| i | 1100 Volt grade AB Cable 3x50+1x25+1x35 | D-6(A) (i) | Per Km | 273057 | DELETED
(L) |  | Additional pole of R.S. Joist (125x70) mm (Mid span) for L.T.Line with A.B.Cable. | D-6(B) | Per No. | 9780 | 9209 | -5.8384
(M) |  | HVDS system of 200 kVA parent DTR taking 4 KM LT to be converted | D-7 | 4 Km | 1917922 | 1945906 | 1.4591
(N) |  | HVDS system of 100 kVA parent DTR taking 3 KM LT to be converted | D-8 | 3Km | 960861 | 935426 | -2.6471
(O) |  | HVDS system of 63 kVA parent DTR taking 2 KM LT to be converted | D-9 | 2Km | 692611 | 676802 | -2.2825
(P) |  | Conversion of 1 Km LT line into 11 kV line | D-10 | Per Km | 78149 | 76543 | -2.055
(Q) |  | LT line conversion using Rabbit conductor maximum span of 45 mtrs
| i | 1 phase 2 wire to 1 phase 3 wire conversion | D-11(I) |  | 66251 | 68984 | 4.1252
| ii | 1 phase 2 wire to 3 phase 4 wire conversion | D-11(II) |  | 106799 | 110491 | 3.457
| iii | 1 phase 3 wire to 3 phase 4 wire conversion | D-11(III) |  | 68889 | 71635 | 3.9861
| iv | 1 phase 3 wire to 3 phase 5 wire conversion | D-11(IV) |  | 109350 | 113054 | 3.3873
(R) |  | Conversion of 1 Km 1 Phase 3 wire LT line into 11 kV line | D-12 | Per Km | 194760 | 197052 | 1.1768
(S) |  | Conversion of 1 Km 3 Phase 5 wire LT line into 11 kV line | D-13 | Per Km | 220985 | 223565 | 1.1675
(T) |  | Distribution Box on existing LT Lines for Service Connections.
| i | Single phase Distn. Box for 09 Connections | D-14 (i) | Per No. | 1350 | 1091 | -19.1852
| ii | Three phase Distn. Box for 05 Connections | D-14 (ii) | Per No. | 1577 | 1295 | -17.8821
(U) |  | 1 phase 2 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x16+1x25 sq.mm. | D-15 | Per Km | 253584 | DELETED
PART-VII, METERING
(A) |  | Metering of 11/0.4 kV Distribution X'mer
| i | 25 kVA Transformer | E-1(I) | Each | 8957 | 9574 | 6.8885
| ii | 63 kVA Transformer | E-1(II) | Each | 8957 | 9574 | 6.8885
| iii | 100 kVA Transformer | E-1(III) | Each | 8957 | 9574 | 6.8885
| iv | 200 kVA Transformer | E-1(IV) | Each | 8678 | 9282 | 6.9601
Meter modernisation- Replacing the existing meters with electronic meters which are highly capable of improving billing efficiency.
(B) | i | Cost of meter replacement of single phase consumer along with shifting of meter outside the premises. | E-2 | Each
| i | With Armoured service cable | E-2(i) | Each | 2629 | 2653 | 0.91289
| ii | With Unarmoured service cable | E-2(ii) | Each | 2335 | 2359 | 1.0278
(C) | ii | Cost of meter replacement of three phase consumer along with shifting of meter outside the premises. | E-3 | Each
| i | With Armoured service cable | E-3(i) | Each | 4947 | 5011 | 1.2937
| ii | With Unarmoured service cable | E-3(ii) | Each | 4718 | 4782 | 1.3565
(D) | iii | Cost of meter replacement of three phase consumer CT Operated meter along with shifting of meter outside the premises. | E-4 | Each | 2600 | 2618 | 0.69231
(E) | iv | Meter shifting of Single phase consumer to outside of premises with New Service Cable. | E-5 | Each
| i | With Armoured service cable | E-5(i) | Each | 1649 | 1673 | 1.4554
| ii | With Unarmoured service cable | E-5(ii) | Each | 1355 | 1379 | 1.7712
(F) | v | Meter shifting of Three phase consumer to outside of premises with New Service Cable. | E-6 | Each
| i | With Armoured service cable | E-6(i) | Each | 2767 | 2831 | 2.313
| ii | With Unarmoured service cable | E-6(ii) | Each | 2538 | 2602 | 2.5217
[5 empty] | Total Hike in % |  | 0.1

## COMPARATIVE
COMPARATIVE STATEMENT OF RATES FROM YEAR 2018-19 to 2019-20
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2018-19 | 2019-20 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
PART-I, 33 kV LINES AND D.P. STRUCTURES
(A) |  | 33 kV line on PCC Pole / H-Beam poles with Raccoon conductor.
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-1(i) | Per Km | 356392 | 364250 | 2.2049
| ii | On H-Beam 152 x 152 mm 37.1 Kg/ Mtr 13 Mtr long | A-1(ii) | Per Km | 579006 | 622785 | 7.5611
| iii | On 365 Kg 11 Mtrs long PCC poles | A-1(iii) | Per Km | 409377 | 418977 | 2.345
(B) |  | 33 kV Four Pole structure on PCC / H-Beam Pole | A-2 (A)
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-2 (A) (i) | Each | 252957 | 256712 | 1.4844
| ii | H-Beam Pole | A-2 (A) (ii) | Each | 334277 | 350661 | 4.9013
(C) |  | 33 kV DP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-2 (B)(i) | Each | 62901 | 65849 | 4.6867
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-2 (B)(ii) | Each | 106979 | 116925 | 9.2972
| iii | On 365 Kg 11 Mtrs long PCC poles | A-2 (B)(iii) | Each | 73218 | 76465 | 4.4347
(D) |  | 33 kV line on PCC Pole / H-Beam Pole with Dog conductor.
| i | On 280 Kg, 9.1 Mtrs long PCC poles | A-3(i) | Per Km | 416152 | 423555 | 1.7789
| ii | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3(ii) | Per Km | 638767 | 682091 | 6.7824
| iii | On 365 Kg 11 Mtrs long PCC poles | A-3(iii) | Each | 467735 | 476637 | 1.9032
(E) |  | Augmentation of 1 km. of 33 kV line from Raccoon to Dog conductor. | A-3 (A) | Per Km | 263370 | 264841 | 0.55853
(F) |  | Additional (Mid Span) Pole for 33 kV Line | A-3 (B)
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3 (B)(i) | Per No. | 37059 | 41169 | 11.0904
(G) |  | 33 kV line on H-Beam supports suspension type with Panther Conductor (Maximum span of 50 Mtrs) | A-4
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-4 (i) | Per Km | 1688417 | 1785090 | 5.7257
(H) |  | 33 kV DP Structure on H-Beam supports with Panther Conductor | A-5
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-5 (i) | Each | 121424 | 131260 | 8.1005
(I) |  | 33 kV Under ground cable crossing under existing Railway track / Road for 60 Mtr long Corridor / route length of HDPE pipe under 2.5 M. deep for ground level single feeder line | A-6 | 60 Mtr
| a | Using HDD Technique for Railway works with 3 core U/G XLPE 400 sqmm Cable | A-6(i) | 60 Mtr | 1320891 | 1391090 | 5.3145
| b | Using HDD Technique for Road crossing works with 3 core U/G XLPE 400 sqmm Cable | A-6(ii) | 60 Mtr | 1293641 | 1364669 | 5.4905
(J) |  | Last span cabling of 33 kV H.T. Connection
|  | Using H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-7
| i | With 3x185 sq.mm AB XLPE Cable | A-7(i) | 50 Mtr | 215630 | 230984 | 7.1205
| ii | With 3x240 sq.mm AB XLPE Cable | A-7(ii) | 50 Mtr | 240307 | 255673 | 6.3943
(K) |  | 33 kV MEDP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-8 (i) | Each | 91528 | 90272 | -1.3723
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-8 (ii) | Each | 129728 | 135163 | 4.1895
(L) |  | Last span cabling of 33 kV line using Covered Conductor of size
| i | 70 sq.mm (207 Amp) | A-9 (i) | 50 Mtr | 151464 | 119988 | -20.7812
| ii | 99 sq.mm (258 Amp) | A-9 (ii) | 50 Mtr | 156662 | 125188 | -20.0904
(M) |  | Schedule for 33 kV Underground Cable crossing under Railway Track / Road for 60 Mtr. Long Corridor / Route Length of HDPE Pipe, under 2.5 Mtr. Deep from Ground Level Single Feeder Line Using Open Trench Method. | A-10 (i)
| i | With 3 core U/G XLPE 240 sqmm Cable | A-10(i) | 60 Mtr | 1031650 | 1068412 | 3.5634
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-10(ii) | 60 Mtr | 1144048 | 1181717 | 3.2926
(N) |  | Schedule for laying of 1 km. 33 kV Cable Direct in Ground Single Cable Line using Open Trench Method. | A-11
| i | With 3 core U/G XLPE 240 sqmm Cable | A-11(i) | Per Km | 3708835 | 3851063 | 3.8348
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-11(ii) | Per Km | 3955051 | 4097402 | 3.5992
Part-II, 33/11 kV SUB-STATIONS
(A) |  | New Sub-stations:
| i | 1.6 MVA, 33/11 kV S/s expandable to 2 x 1.6 MVA with control room | B-1(i) | Each | 7310256 | 7796888 | 6.6568
| ii | 3.15 MVA, 33/11 kV S/s expandable to 2 x 3.15 MVA with control room | B-1(ii) | Each | 9318229 | 9896968 | 6.2108
| iii | 5 MVA, 33/11 kV S/s expandable to 2 x 5 MVA with control room | B-1(iii) | Each | 11163138 | 11787508 | 5.5931
(B) |  | 33/11 kV Power Transformer
| i | 1.6 MVA | B-2(i) | Each | 919511 | 932371 | 1.3986
| ii | 3.15 MVA | B-2(ii) | Each | 2532958 | 2635514 | 4.0489
| iii | 5.0 MVA | B-2(iii) | Each | 3558199 | 3698214 | 3.935
(C) |  | Installation of additional transformer for parallel operation with one additional bay on 11 kV side
| i | 1.6 MVA | B-3(i) | Each | 3709955 | 3850522 | 3.7889
| ii | 3.15 MVA | B-3(ii) | Each | 5676488 | 5905712 | 4.0381
| iii | 5.0 MVA | B-3(iii) | Each | 6701535 | 6968190 | 3.979
(D) |  | 11 kV Out door yard extension for additional bay with circuit breaker. | B-4 | Each | 562251 | 579116 | 2.9996
(E) |  | 33 kV Out door yard extension for additional bay without circuit breaker. | B-5 | Each | 235119 | 243362 | 3.5059
(F) |  | Installation of 33 kV VCB | B-6 | Each | 446574 | 454793 | 1.8405
(G) |  | Augmentation of Power Transformer
| i | 1.6 to 3.15 MVA | B-8(i) | Each | 2942211 | 3048019 | 3.5962
| ii | 3.15 to 5.0 MVA without 33 kV VCB | B-8(ii) | Each | 3569910 | 3709451 | 3.9088
| iii | 3.15 to 5.0 MVA with 33 kV VCB | B-8(iii) | Each | 3985388 | 4130668 | 3.6453
H) |  | Installation of 1.6 MVA 33/11 kV Sub-Station ON LINE | B-9 | Each | 1316266 | 1330783 | 1.1029
PART-III, 11 kV LINES AND D.P.STRUCTURES
(A) |  | 11 kV line on 140 Kg 8.0 Mtr long PCC poles with
| i | Rabbit conductor | C-1(I) | Per Km | 270023 | 276188 | 2.2831
| ii | Weasel conductor | C-1(II) | Per Km | 220616 | 226377 | 2.6113
(B) |  | 11 kV DP structure on 140 Kg, 8.0 Mtr long PCC poles | C-2 | Each | 41094 | 43843 | 6.6895
PART-IV, 11 kV LINES AND D.P.STRUCTURES ON RAIL & H-BEAM
(A) |  | 11 kV line on H-Beam / PCC Pole with Rabbit conductor
| i | On H-Beam 11 meter long | C-3(i) | Per Km | 506596 | 552311 | 9.024
| ii | On 365 Kg 11 Mtrs long PCC poles | C-3(ii) | Per Km | 355149 | 366351 | 3.1542
(B) | ii | Additional (Mid span) Poles for 11 kV Line on H-Beam | C-3 (A) | Per No. | 28746 | 32192 | 11.9878
(C) | iii | 11 kV Line on A.B.Cable | C-3 (B)
| a | Using H-Beam 152x152 mm, 37.1Kg/mtr 11 Mtrs long supports.
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[i] | Per Km | 1459762 | 1580358 | 8.2613
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[ii] | Per Km | 1610262 | 1730934 | 7.4939
| b | Using 200 Kg; 9.0 Mtr long PCC Pole
| i | With 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm | C-3 (B)[iii] | Per Km | 882525 | 913799 | 3.5437
| ii | With 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm | C-3 (B)[iv] | Per Km | 1033025 | 1064375 | 3.0348
(D) | iv | Augmentation of 11 kV Line from Weasel to Raccoon Conductor | C-3 (C) | Per Km | 195588 | 196258 | 0.34256
(E) | v | Augmentation of 11 kV Line from Weasel to Rabbit Conductor | C-3 (D) | Per Km | 140589 | 141585 | 0.70845
(F) | vi | 11 kV Overhead XLPE Cable Line on H-Beam Pole with average span 30 Mtrs. | C-3 (E) | Per Km | 3222793 | 3438652 | 6.6979
(G) |  | 11 kV DP structure on
| i | H-Beam 11 meter long | C-4(i) | Each | 83694 | 92406 | 10.4093
| ii | On 365 Kg 11 Mtrs long PCC poles | C-4(ii) | Each | 58219 | 61176 | 5.0791
(H) |  | 11 kV line on RS Joist (175X85 mm) 11.0 Meters long with
| i | Rabbit conductor | C-5(I) | Per Km | 372572 | 381472 | 2.3888
| ii | Weasel conductor | C-5(II) | Per Km | 326617 | 335748 | 2.7956
(I) |  | 11 kV DP structure on RS Joist 175X85 mm 11.0 Mtr. long | C-6 | Each | 61153 | 63729 | 4.2124
(J) |  | 11 kV line on PCC pole
| a | On 365 Kg 11 Mtrs long PCC poles
| i | Using Raccoon conductor | C-8(I) | Per Km | 405877 | 416783 | 2.687
| ii | Using Dog conductor | C-8(II) | Per Km | 461671 | 471655 | 2.1626
(K) |  | 11 kV line on H-Beam (152x152 mm) 13 meter long with
| i | Raccoon conductor | C-9(I) | Per Km | 602016 | 653100 | 8.4855
| ii | Dog conductor | C-9(II) | Per Km | 657810 | 707972 | 7.6256
(L) |  | Additional (Mid Span) Poles for new 11 kV Line with Raccoon Conductor | C-9(A) | Per No. | 32500 | 36417 | 12.0523
(M) |  | 11 kV under ground cable crossing under existing Railway track / Road for 60 mtr long Rail / Road corridor route length of HDPE pipe, under 2.5 mtr deep for ground level single feeder line | C-12
| a | Using HDD Technique for Railway works on 3x240 sqmm. U/G XLPE Cable | C-12 (i) | 60 Mtr | 970821 | 1048095 | 7.9597
| b | Using HDD Technique for Road crossing works on 3x240 sqmm. U/G XLPE Cable | C-12 (ii) | 60 Mtr | 943571 | 1021674 | 8.2774
(N) |  | Laying of 1 Km 11 kV Cable direct in ground single cable Line using open trench method
| i | 3 Core 95 Sqmm underground cable | C-15(I) | Per Km | 1470358 | 1536209 | 4.4786
| ii | 3 Core 240 Sqmm underground cable | C-15(II) | Per Km | 1972972 | 2039075 | 3.3504
(O) |  | D.T. Capacitors on existing DTR's (Retained & shifted) | C-16
| i | LT Capacitor for 25 kVA DT | C-16 (i) | Per No. | 1902 | 1932 | 1.5773
| ii | LT Capacitor for 63 kVA DT | C-16 (ii) | Per No. | 3603 | 3664 | 1.693
| iii | LT Capacitor for 100 kVA DT | C-16 (iii) | Per No. | 4289 | 4362 | 1.702
| iv | LT Capacitor for 200 kVA DT | C-16 (iv) | Per No. | 4289 | 4362 | 1.702
| v | LT Capacitor for 315 kVA DT | C-16 (v) | Per No. | 4289 | 4362 | 1.702
(P) |  | 11 kV MEDP Structure on H-Beam Pole
| i | 37.1 Kg /Mtrs 11 Mtrs long H-Beam supports | C-17 (i) | Each | 91101 | 99195 | 8.8846
(Q) |  | New Automated 11 kV Capacitor Bank at 33/11 kV Sub-stations
| i | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. | C-18 (i) | Each | 1162470 | 1181503 | 1.6373
| ii | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . | C-18 (ii) | Each | 976669 | 993572 | 1.7307
(R) |  | Schedule for installation of compact R.M.U. 11 kV Class SF6 / VCB type (1 Incoming + 2 Breaker + 1 Outgoing) | C-19 | Each | 1201222 | 1205348 | 0.34348
(S) |  | Schedule for Chemical Earthing of Metering Equipment installed in the premises of HT consumers in normal / hard rock soil. | C-20 | Each | 12703 | 13047 | 2.708
(T) |  | Schedule for 11 kV Capacitor Bank to be installed at 11 kV Line D.P. Structure | C-21 | Each | NA | 75796 |  | NEW ADDED
PART-V, 11/0.4 kV Transformer S/s.
A (A-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(I) | Each | 128546 | 135828 | 5.6649
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC pole | C-7(A-1)(II) | Each | 192886 | 203074 | 5.2819
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(III) | Each | 276788 | 287067 | 3.7137
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-1)(IV) | Each | 423998 | 441502 | 4.1283
(B-1) |  | 11/0.4 kV Out-door type Transformer Sub-station using 3.5 Core PVC cable.
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(I) | Each | 162958 | 175621 | 7.7707
| ii | 63 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(II) | Each | 227299 | 242867 | 6.8491
| iii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11mtr long | C-7(B-1)(III) | Each | 277302 | 294178 | 6.0858
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1)(IV) | Each | 425192 | 449294 | 5.6685
(B-1) A |  | Relocation of 11/0.4 kV Out-door type Transformer Sub-station using H-Beam Pole and 3.5 Core PVC Cable [Based on Cost Schedule C-7 (B-1) except X-mer Cost]
| i | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (I) | Each | 109049 | 118234 | 8.4228
| ii | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (II) | Each | 130057 | 139009 | 6.8831
| iii | 100 kVA on H-Beam 152x152 mm,37.1 Kg/Mtr, 11 mtr long | C-7(B-1) A (III) | Each | 149338 | 157471 | 5.446
| iv | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr,11 mtr long | C-7(B-1) A (IV) | Each | 184572 | 192263 | 4.1669
(B-1) B |  | Renovation of Existing Distribution Transformer
| i | 25 kVA Transformer | C-7(B-1) B (I) | Each | 28748 | 30858 | 7.3396
| ii | 63 kVA Transformer | C-7(B-1) B (II) | Each | 46852 | 49213 | 5.0393
| iii | 100 kVA Transformer | C-7(B-1) B (III) | Each | 57469 | 59592 | 3.6942
| iv | 200 kVA Transformer | C-7(B-1) B (IV) | Each | 91200 | 92604 | 1.5395
| v | 315 kVA Transformer | C-7(B-1) B (V) | Each | 85285 | 86686 | 1.6427
(A-2) |  | 11/0.4 kV Out-door type Transformer sub-station using 1 Core PVC cable.
| i | 25 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(I) | Each | 128546 | 135828 | 5.6649
| ii | 63 kVA on 140 Kg, 8.0 Mtr long PCC poles | C-7(A-2)(II) | Each | 189669 | 200588 | 5.7569
| iii | 100 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(III) | Each | 272534 | 283150 | 3.8953
| iv | 200 kVA on 175 x 85 mm, 9.0 Mtr long reinforced R.S. Joist. | C-7(A-2)(IV) | Each | 412495 | 430985 | 4.4825
(B-2) | v | 25 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(I) | Each | 162958 | 175621 | 7.7707
| vi | 63 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(II) | Each | 224082 | 240382 | 7.2741
| vii | 100 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(III) | Each | 273048 | 290261 | 6.304
| viii | 200 kVA on H-Beam 152x152 mm, 37.1 Kg/Mtr, 11 mtr long | C-7(B-2)(IV) | Each | 413689 | 438776 | 6.0642
(B) |  | Augmentation of 11/.4 kV S/s capacity (Assuming 25 years of life & 10 years in service)
| i | 25 kVA to 63 kVA | C-10 (I) | Each | 145726 | 157151 | 7.8401
| ii | 63 kVA to 100 kVA | C-10 (II) | Each | 237080 | 250693 | 5.7419
| iii | 100 kVA to 200 kVA | C-10 (III) | Each | 386625 | 408315 | 5.6101
(C) | i | 11/.4 kV Out door Sub-station (16 kVA Transformer) | C-11 | Each | 127611 | 134942 | 5.7448
(D) |  | Single pole mounted low capacity Single phase / Three phase 11/.4 kV Distribution Transformer Sub-station
| i | 16 kVA Three phase | C-13(III) | Each | 105348 | 110389 | 4.7851
(E) |  | Plinth mounted 11/.4 kV Outdoor Sub-station
| i | 63 kVA Transformer | C-14(I) | Each | 242860 | 257679 | 6.1019
| ii | 100 kVA Transformer | C-14(II) | Each | 291894 | 308830 | 5.8021
| iii | 200 kVA Transformer | C-14(III) | Each | 470402 | 501683 | 6.6498
PART-VI, L.T. LINES
(A) |  | 3 phase, 5 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 4 Rabbit + 1 Squirrel | D-1(I) | Per Km | 324077 | 333226 | 2.8231
| ii | 3 Rabbit + 2 Squirrel | D-1(II) | Per Km | 301755 | 311006 | 3.0657
| iii | 4 Weasel + 1 Squirrel | D-1(III) | Per Km | 264152 | 273820 | 3.66
| iv | 3 Weasel + 2 Squirrel | D-1(IV) | Per Km | 256812 | 266452 | 3.7537
| v | 5 Squirrel | D-1(V) | Per Km | 234790 | 244347 | 4.0704
(B) |  | 3 phase, 4 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 3 Rabbit + 1 Squirrel | D-2(I) | Per Km | 279348 | 288245 | 3.1849
| ii | 3 Weasel + 1 Squirrel | D-2(II) | Per Km | 234404 | 243691 | 3.962
| iii | 4 Squirrel | D-2(III) | Per Km | 212383 | 221586 | 4.3332
(C) |  | 1 phase, 3 wire LT line on 140 Kg, 8.0 Mtr long PCC poles with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-3(I) | Per Km | 218482 | 227252 | 4.0141
| ii | 2 Weasel + 1 Squirrel | D-3(II) | Per Km | 203501 | 212401 | 4.3734
| iii | 3 Squirrel | D-3(III) | Per Km | 188820 | 197664 | 4.6838
(D) |  | 3 Phase, 5 Wire LT line on 125 x 70 mm, 9.3 Mtrs long R.S. Joist with 3 Rabbit & 2 Weasel conductors (Span upto 45 Meters) | D-4(I) | Per Km | 442164 | 456798 | 3.3096
(E) |  | 3 Phase, 5 Wire LT line on 175 x 85 mm, 9.3 Mtrs long R.S. Joist with 3 Raccoon & 2 Weasel conductors (Span upto 65 Meters) | D-4(II) | Per Km | 486295 | 496803 | 2.1608
(F) |  | 1 Phase, 3 Wire LT line on 9.3 Mtrs long 125x70 mm R.S. Joist with following conductors
| i | 1 Rabbit + 1 Weasel + 1 Squirrel | D-5(I) | Per Km | 316232 | 326977 | 3.3978
| ii | 2 Weasel + 1 Squirrel | D-5(II) | Per Km | 301250 | 312125 | 3.61
| iii | 3 Squirrel | D-5(III) | Per Km | 286569 | 297389 | 3.7757
(G) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (ii) | Per Km | 308175 | 323897 | 5.1016
3 phase line on RS Joist 175x85 mm ,19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (iv) | Per Km | 471253 | 489133 | 3.7941
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x25+1x16+1x25 | D-6 [1] (vi) | Per Km | 648023 | 716417 | 10.5543
(H ) |  | 3 phase line on 140 Kg, 8.0 Mtr long PCC poles with following XLPE Cable
| i | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (i) | Per Km | 403041 | 436663 | 8.3421
3 phase line on RS Joist 175x85 mm, 19.495 Kg/Mtr, 9.3 Mtr long poles with following XLPE Cable
| ii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (ii) | Per Km | 567003 | 602783 | 6.3104
3 phase line on H-Beam 152x152 mm, 37.1 Kg/Mtr, 9.0 Mtr long poles with following XLPE Cable
| iii | Using 1100 Volt grade AB Cable 3x70+1x16+1x50 | D-6 [2] (iii) | Per Km | 743772 | 830066 | 11.6022
(I) |  | 1 phase 3 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 1x25+1x16+1x25 sq.mm. | D-6 [3] | Per Km | 261809 | 275799 | 5.3436
(J) |  | 3 phase 4 Wire line on 140 kg 8.0 Mtr.long PCC poles with 1100 V grade AB XLPE Cable 3x16+1x25 sq.mm. | D-6 [4] | Per Km | 318657 | 334085 | 4.8416
(K) |  | Additional pole of R.S. Joist (125x70) mm (Mid span) for L.T.Line with A.B.Cable. | D-6(B) | Per No. | 11371 | 11831 | 4.0454
(L) |  | HVDS system of 200 kVA parent DTR taking 4 KM LT to be converted | D-7 | 4 Km | 2087220 | 2139278 | 2.4941
(M) |  | HVDS system of 100 kVA parent DTR taking 3 KM LT to be converted | D-8 | 3Km | 1039387 | 1073387 | 3.2712
(N) |  | HVDS system of 63 kVA parent DTR taking 2 KM LT to be converted | D-9 | 2Km | 755719 | 778605 | 3.0284
(O) |  | Conversion of 1 Km LT line into 11 kV line | D-10 | Per Km | 91372 | 97293 | 6.4801
(P) |  | LT line conversion using Rabbit conductor maximum span of 45 mtrs
| i | 1 phase 2 wire to 1 phase 3 wire conversion | D-11(I) |  | 81667 | 84317 | 3.2449
| ii | 1 phase 2 wire to 3 phase 4 wire conversion | D-11(II) |  | 130893 | 134418 | 2.693
| iii | 1 phase 3 wire to 3 phase 4 wire conversion | D-11(III) |  | 84886 | 87538 | 3.1242
| iv | 1 phase 3 wire to 3 phase 5 wire conversion | D-11(IV) |  | 134009 | 137535 | 2.6312
(Q) |  | Conversion of 1 Km 1 Phase 3 wire LT line into 11 kV line | D-12 | Per Km | 233577 | 231804 | -0.75906
(R) |  | Conversion of 1 Km 3 Phase 5 wire LT line into 11 kV line | D-13 | Per Km | 265819 | 264460 | -0.51125
(S) |  | Distribution Box on existing LT Lines for Service Connections.
| i | Single phase Distn. Box for 09 Connections | D-14 (i) | Per No. | 1215 | 1281 | 5.4321
| ii | Three phase Distn. Box for 05 Connections | D-14 (ii) | Per No. | 1436 | 1508 | 5.0139
PART-VII, METERING
(A) |  | Metering of 11/0.4 kV Distribution X'mer
| i | 25 kVA Transformer | E-1(I) | Each | 9457 | 9991 | 5.6466
| ii | 63 kVA Transformer | E-1(II) | Each | 9457 | 9991 | 5.6466
| iii | 100 kVA Transformer | E-1(III) | Each | 9457 | 9991 | 5.6466
| iv | 200 kVA Transformer | E-1(IV) | Each | 9157 | 9691 | 5.8316
Meter modernisation- Replacing the existing meters with electronic meters which are highly capable of improving billing efficiency.
(B) | i | Cost of meter replacement of single phase consumer along with shifting of meter outside the premises. | E-2 | Each
| i | With Armoured service cable | E-2(i) | Each | 2642 | 2725 | 3.1416
| ii | With Unarmoured service cable | E-2(ii) | Each | 2316 | 2399 | 3.5838
(C) | ii | Cost of meter replacement of three phase consumer along with shifting of meter outside the premises. | E-3 | Each
| i | With Armoured service cable | E-3(i) | Each | 4927 | 5112 | 3.7548
| ii | With Unarmoured service cable | E-3(ii) | Each | 4672 | 4856 | 3.9384
(D) | iii | Cost of meter replacement of three phase consumer CT Operated meter along with shifting of meter outside the premises. | E-4 | Each | 2283 | 2475 | 8.41
(E) | iv | Meter shifting of Single phase consumer to outside of premises with New Service Cable. | E-5 | Each
| i | With Armoured service cable | E-5(i) | Each | 1884 | 1929 | 2.3885
| ii | With Unarmoured service cable | E-5(ii) | Each | 1558 | 1603 | 2.8883
(F) | v | Meter shifting of Three phase consumer to outside of premises with New Service Cable. | E-6 | Each
| i | With Armoured service cable | E-6(i) | Each | 3160 | 3233 | 2.3101
| ii | With Unarmoured service cable | E-6(ii) | Each | 2904 | 2977 | 2.5138
[6 empty] | TOTAL HIKE | 678.7171
4.2687
678.7171
159
4.2687

## SOR RATE
RATE OF STOCK MATERIALS IN SoR OF 2019-20
RATE OF ALL MATERIALS ARE INCLUSIVE OF G.S.T. UNLESS MENTIONED SPECIFICALLY IN REMARKS COLUMN
Material Code | Description | Unit | Unit rate for 2019-20 | SAP DESCRIPTION | REMARKS
7130200201 | 1:1.5:3 Ratio | Cmt | 4073 |  |  | Material cost including GST and labour.
7130200202 | 1:3:6 Ratio | Cmt | 2970 |  | * | Material cost including GST and labour.
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 182.51 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 238.08 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Each | 33 |  |  | Material cost including GST and labour.
7130210809 | Aluminium Paint | Ltr. | 338.4 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 259.08
7130211158 | Red Oxide Paint | Ltr. | 151.45 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 180079.8 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5 | ISI MARK
7130310007 | 70 Sqmm. | Km. | 56404.41 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V | ISI MARK
7130310008 | 120 Sqmm. | Km. | 89898.08 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100 | ISI MARK
7130310020 | 3x400 Sq.mm. | km | 2219229.13 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 29231.77 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V | ISI MARK
7130310022 | 50 Sqmm. | Km. | 35850.1 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V | ISI MARK
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 72266.19 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM | ISI MARK
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 83077.9 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM | ISI MARK
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 101739.6 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM | ISI MARK
7130310038 | 2.5 Sqmm. | Per Mtr. | 7.11 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 30.01 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 62.18 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 109476.3 | 11KV PVC INSULATED 150SQMM SINGLE CORE X | ISI MARK
7130310042 | 16.0 Sqmm. | km | 40594.44 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 57675.48 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310048 | 25 Sq.mm. | km | 91659.73
7130310049 | 120 Sq.mm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310050 | 400 Sqmm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310051 | 3x95 Sq.mm. | km | 950280.47 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1166523.49
7130310053 | 3x185 Sq.mm. | km | 1333289.73 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 1695415.65 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 18395.19
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 26278.83
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 324086.39 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 458499.87
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 685585.97
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 646678.05
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 4014.82 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 4224.96 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 45825.3 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 130732.2 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM | ISI MARK
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 127849.04 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 55224 | LT AB CABLEB 3X16+1X25 SQMM | ISI MARK
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 59238.39 | LT AB CABLEB 3X25+1X25 SQMM | ISI MARK
7130310075 | 3x240 Sq.mm. | km | 2030747.47 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 541944.24
7130310077 | 95 Sq.mm | km | 548313.68 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 817646.19 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 990668.03 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 1526364.83 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310082 | PVC Insulated 1100 Volts grade Aluminium Twin Core Single Phase 4.0 sq.mm. Unarmoured service cable. | Per Mtr. | 15.15 | PVC Insulated 11kV 2 Core 4.0 sqmm cable |  | NEW BIN CODE ALLOTED
7130310083 | PVC Insulated 1100 Volts grade 70 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 339722.12 | PVC Insul. 70 Sqmm 4C Armour UG AL. Cable |  | NEW BIN CODE ALLOTED
7130310084 | PVC Insulated 1100 Volts grade 95 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 414241.81 | PVC Insul. 95 Sqmm 4C Armour UG AL Cable |  | NEW BIN CODE ALLOTED
7130310085 | PVC Insulated 1100 Volts grade 150 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 625380.93 | PVC Insu. 150 Sqmm 4C Armour UG Al Cable |  | NEW BIN CODE ALLOTED
7130310086 | PVC Insulated 1100 Volts grade 300 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 1194506.8 | PVC Insul. 300 Sqmm. 4C Armour Al. Cable |  | NEW BIN CODE ALLOTED
7130310087 | PVC Insulated 1100 Volts grade 400 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 1518156.05 | PVC Insul. 400 Sqmm. 4C Armour Al. Cable |  | NEW BIN CODE ALLOTED
7130310088 | 33 kV AB Cable Straight thru' joint kit suitable for 185 sqmm | Set | 34941.82 | 33 kV ABC Straight thru jointkit 185 sqmm |  | NEW BIN CODE ALLOTED
7130310089 | 33 kV XLPE UG Cable Straight through heat shrinkable cable jointing kit with lugs for 3 core 120-240 sq mm XLPE cable | Set | 58922.67 | 33kV UGCable Straight thru jointkit 120-240 sqmm |  | NEW BIN CODE ALLOTED
7130310090 | 33 kV XLPE UG Cable Straight through heat shrinkable cable jointing kit with lugs for 3 core 300-400 sq mm XLPE cable | No | 65983.05 | 33kV UGCable Straight thru jointkit 300-400 sqmm |  | NEW BIN CODE ALLOTED
7130310652 | 2 Core (UNARMOURED) | Km. | 39109.07 | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310654 | 4 Core (UNARMOURED) | Km. | 68143.06 | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310658 | 8 Core (UNARMOURED) | Km. | 129543.93 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310681 | 10 Core (UNARMOURED) | Km. | 161841.26 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310660 | 10 Core (ARMOURED) | Km. | 200541 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 166768.32 | CONTROL CABLE COP 12 CORE 2.5 SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 14195.55 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 37153.63 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 51467.72 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 101185.66 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 200836.48 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 250758.14 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC |  | ITEM DELETED: NOT TO BE USED
7130311057 | 150 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV |  | ITEM DELETED: NOT TO BE USED
7130311061 | 300 Sqmm. | km |  | Power Cable ARM ALU 3.5CORE 300/150SQMM |  | ITEM DELETED: NOT TO BE USED
7130311084 | 16.0 Sqmm. | km | 60690.04 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 10511.54
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 13139.42 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 15767.29 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 18395.19 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 19709.13
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 23650.95
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 827.3 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 893.65
7130320045 | Cable tie for AB Cable | Each | 26.54
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | No | 3986.65 | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 2542.72 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 2678.76
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 5.56 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 35218.1 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 852.74
7130352031 | 16 Sq.mm, 4 Core | Set | 852.74 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 915.78
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1287.4
7130352034 | 150 Sq.mm, 3.5 Core | Set | 1918.93
7130352035 | 300 Sq.mm, 3.5 Core | Set | 3101.26
7130352036 | 400 Sq.mm, 3.5 Core | Set | 3962.84
7130352037 | End terminating jointing kit upto 240 sqmm XLPE cable | Set | 23743.04 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x50 Sq.mm | Set | 14192.35
7130352039 | 3x95 Sq.mm | Set | 14192.35 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 18791.14 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 20551.36 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 20551.36 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 7377.45 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 8905.83 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 9162.03 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box (with 10 No. connectors) | No. | 3133.19 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 2.24 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 2.24 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 4.48
7130354277 | 32 Sq mm | Nos. | 5.6
7130354278 | 50 Sq mm | Nos. | 8.97 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 13.45 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 16.8 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 23.53 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 26.89 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 42.58
7130354284 | 225 Sq mm | Nos. | 48.17
7130354285 | 240 Sq mm | Nos. | 69.47
7130354286 | 300 Sq mm | Nos. | 81.8 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 105.33
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 682.19 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 86.99 | INSULATING PIERCING CONNECTOR AB CABLE(S
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 113.32 | INSULATING PIERCING CONNECTOR FOR AB CAB
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 157.95 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 123.62 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 174.7 | STRAIGHT THROUGH JOINT
7130390019 | End cap for 50/70 Sq.mm | Nos. | 29.86 | END CLAMP CAP FOR 50/70 SQMM
7130640040 | M.S. ANGLE 35 x 35 x 5 mm | MT | 36566.4 | M.S. ANGLE 35 x 35 x 5 mm |  | NEW BIN CODE ALLOTED
7130600023 | 50 x 50 x 6 mm | MT | 43121.82 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 43121.82 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 43121.82 | M S ANGLE 75X75X6 MM
7130600166 | 75x40 mm | MT | 43121.82 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 46927.14 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 43121.82 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 46927.14 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT | 39505.14 | R.S.JOIST 125 x 70 mm
7130600675 | 175 x 85 mm | MT | 44915.52 | R S JOIST 175X85 MM | ISI MARK
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 52290.91 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 52290.91 | RAIL 60 KG PER METER
7130601958 | 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 53879.18 | H BEAMS 152X152MM; 37.1 KG/MTR. | ISI MARK
7130601965 | 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 53879.18 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR | ISI MARK
7130610206 | Barbed wire | MT | 78501.83 | G.I. WIRES: - Barbed wire.
7130620013 | I-Bolt (big size) | No | 128.08 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 71.59
7130620133 | 16x40 mm | Kg | 99.03 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 99.03 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 71.59 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 72.78 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 72.78 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 71.59 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 70.4 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 70.4 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 69.2 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 69.2 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt | No | 428.75 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 153.83 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | RM | 1113.58 | G.I. PIPE 200MM FOR 400MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 964.85 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 3733.72 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | Caping of RCC Pipe on both end of pipe with Concreting and Bricks work | Cmt | 3734.11
7130640031 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 600 mm | RM | 2459 |  |  | Material cost including GST and labour.
7130640036 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 900 mm | RM | 4874 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG) |  | Material cost including GST and labour.
7130640037 | M.S.Pipe 200 mm dia with collars | RM (medium) | 1369.05
7130640038 | M.S.Pipe 200 mm dia with collars | RM (light) | 1069.16 | M.S. PIPE 200 MM DIA WITH COLLARS
7130640171 | G.I. Bend 40 mm | Each | 107.48
7130641396 | Gl Pipe 40 mm | Per Mtr | 222.08 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | No | 876.17 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 4453.22 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. 04-01/ST/62 R2 Date 05.06.2007 | RM | 2024.88 |  |  | Material cost including GST and labour.
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 138
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 609.82 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 442.63 | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 2255.2 | PCC POLE 140 KG; 8,0 MTR LONG |  | Material cost including GST and labour.
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 280 Kg; 9.1 Mtr long | Each | 4402.65 | PCC POLE 280 KG; 9,1 MTR LONG |  | Material cost including GST and labour.
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each |  | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT |  | ITEM DELETED: NOT TO BE USED
7130800672 | 350 Kg; 7.0 Mtr long | Each |  | PCC POLE 350 KG; 7,0 MTR LONG |  | ITEM DELETED: NOT TO BE USED
7130810005 | Through Bolt | No | 90.09 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr 100 x 50 mm. | Set | 7091.89 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810026 | Stay clamp for 140 kG PCC Pole | Pair | 160.97 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 300.41 | Stay clamp LT/Pair
7130810060 | LT U CLAMP | No. | 80.48 | LT U CLAMP
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 73.23 | Strain Plate
7130810077 | Pole Clamp | No. | 447.76 | POLE CLAMP
7130810102 | Service Ring | No. | 355.82 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 300.41 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 319.69 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 319.69 | HT STAY CLAMP R S JOIST A TYPE
7130810251 | Stay Clamp Rail "B" type | Pair | 319.69 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 319.69 | 33 KV TOP CLAMP SEMIFINISHED
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 643.77 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 766.7 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 889.61 | LT FIVE PIN CROSS ARM
7130810495 | 11 kV Cross Arm Cleat type | No. | 1091.69 | 11 KV V CROSS ARM
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 1730.26 | D.O. / LA Mounting channel 75x40 mm.
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2588.62 | 1.1 MTR DPDC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 4104.29 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 2981.34 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 4189.72 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 4736.61 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 2429.24 | 33 KV V CROSS ARM
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 5601.21 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 96.9 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 404.18 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 306.26 | 11 kV top clamp
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 3361.56 | 11 kV Cut point channel paint
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 8809.64 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 333.29 | Stay clamp for 'H' Beam
7130820008 | 11 kV Pin insulator with Pin | Each | 132.09 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 325.76 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 119.1 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 219.41 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 4.18 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 462.33 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 1890.72 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 33.18
7130820030 | Disc insulator | Each | 237.19 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 46.65 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 237.98 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 11.68 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 13.06 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 11.13 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 73.59 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 244.88 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 36.74 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 36.84 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 41.94 | HARDWARE FOR 75X90 MM LT SHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 123.43 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 256.44 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2197.28 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 160.41 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km |  | CONDUCTOR AAA SQURREL |  | ITEM DELETED: NOT TO BE USED
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km |  | CONDUCTOR AAA WEASEL |  | ITEM DELETED: NOT TO BE USED
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km |  | CONDUCTOR AAA RABBIT |  | ITEM DELETED: NOT TO BE USED
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km |  | CONDUCTOR AAA RACOON |  | ITEM DELETED: NOT TO BE USED
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 37.29 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 145.57 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 671.36
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 14289.01 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq) | ISI MARK
7130830054 | Bimetallic clamp for VCB | Each | 392.07
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 21057.87 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq) | ISI MARK
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 392.07
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 34701.37 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q) | ISI MARK
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 199.32
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 51309.57 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E | ISI MARK
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 67432.24 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq) | ISI MARK
7130830070 | 0.2 Sq inch ( 130 Sqmm Al.Eq.)(Panther) | Km | 151653.08 | CONDUCTOR ACSR PANTHER 130 sq mm | ISI MARK
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km |  | CONDUCTOR AAA DOG |  | ITEM DELETED: NOT TO BE USED
7130830585 | T-Clamp for Dog Conductor. | Each | 275.5 | T-CLAMPS FOR ACSR CONDUCTOR Dog Condutor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 220.16 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830586 | T-Clamp for Panther Conductor. | Each | 322.42 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 292.4 | Bimetallic clamps for transformer & kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 30.07 | SLEEVE JOINTING ALUMINIUM FOR 0.03 SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 224.97 | SLEEVE REPAIR ALUMINIUM FOR .2 SQ INCH AC
7130840021 | 33 kV Polymer Lightning Arrestor | Each | 3221.41 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 328.57 | LIGHTNING ARRESTORS 11 KV gapless type.
7130850198 | GI Structure for complete Equipment | Kg | 84.87
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 4736.61 | Transformer mounting 100 x 50 mm channel
7130850201 | Transformer Mounting with Belting for Addl. X-Arm | No. | 4576.19 | Transformer mounting 100 x 50 mm channel
7130860017 | I-Bolt - 16 mm | No. | 108.55 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 455.31 | STAY SET WITHOUT STAY WIRE 16 mm Paint 11 KV
7130860033 | Stay Set 20 mm (Painted) | Each | 829.62 | STAY SET WITHOUT STAY WIRE 20 mm (Painted)
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 71981.64 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 72686.67 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 789.29
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 118.52 | EARTHING COIL 8SWG GI WIRE 50 MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 369.81 | Earthing rod 25mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 65056.09 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 65009.66 | G.I. WIRES: - 4,0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 65009.66 | G.I. WIRES: - 5,0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 2252.9
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 1009.78 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 2408.9 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2141.24 | Jointing Kit&HW LT ABC CableStraight Sus
7130880006 | Cable marker for U/G cable | No. | 130.54 | CABLE MARKER FOR U/G CABLE
7130880006 | Pad Connector (for Panther conductor) | No. | 143.84 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 92.6 | Danger boards 33 KV & 11 KV.
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 5315.68 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 6707.09
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 15211.68 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 15936.05 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 59.14 | LT LINE SPACERS
7130890973 | Stainless steel strap with buckle (for installation of Service Distribution Box) | Set | 60.83
7131961526 | GSM Modem | Nos. | 3814.87 | GSM MODEM
7130893004 | Eye Hook | No. | 182.42 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 3453.23 | 33 KV guarding channel 100x50 mm.
7131210001 | Panel lndication lamps | Nos. | 123.35
7131210010 | LED 7 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210018 | LED 12 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210019 | LED 14 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210020 | LED 15 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210021 | LED Lamps with COMPLETE FITTING - 15 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210022 | LED LAMPS WITH COMPLETE FITTING - 20 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210852 | CFL 7 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210881 | 250 Watt Metal Halide | Each |  | METAL HALIDE LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131220182 | Tube Light Rod (T5 type) | Each |  | LAMPS: -Tube Light (40 Watts.) |  | ITEM DELETED: NOT TO BE USED
7131230003 | 250 Watt Sodium Vapour | Each |  | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER |  | ITEM DELETED: NOT TO BE USED
7131230116 | 250 Watt Mercury Vapour | Each |  | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO |  | ITEM DELETED: NOT TO BE USED
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each |  | S/ V HIGH PRESSURE LAMP 400W 230/250V |  | ITEM DELETED: NOT TO BE USED
7131280006 | CFL 15 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280007 | CFL 20 Watts | Each |  | CFL 20 WATTS LAMP |  | ITEM DELETED: NOT TO BE USED
7131280008 | CFL 23 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280009 | 125 Watt Mercury Vapour | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280010 | Halogen Filament (1000 Watts) | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280012 | Street Light fitting with tube light | Each |  | STREET LIGHT FITTING WITH TUBE LIGHT |  | ITEM DELETED: NOT TO BE USED
7131280013 | Street Light fitting with CFL | Each |  | STREET LIGHT FITTING WITH CFL |  | ITEM DELETED: NOT TO BE USED
7131280014 | HPSV lamp 150 watt | Each |  | HPSV LAMP 150 WATT |  | ITEM DELETED: NOT TO BE USED
7131280015 | HPSV Choke 250 watt | Each |  | HPSV LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each |  | 150 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each |  | 250 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280882 | CFL 11 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 1778 | ENERGY METER ENECTRONIC 10-60 AMPS | ISI MARK
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for __/110 Volts; __/1 Amps; or __/5 Amps) | Each | 1085600 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 174.93 |  |  | RATE EXCLUDING G.S.T.
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 751.46 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 752.99 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A | ISI MARK
7131300881 | CMRI (Common Meter Reading Instrument) | Each | 27055.25 | Common Meter Reading Instrument CMRI
7131310002 | CT operated electronic static bidirectional meter with DLMS for net metering | Each | 3060.78 |  |  | NEW ITEM ADDED
7131310005 | CT operated electronic static bidirectional meter with DLMS | Each | 1522.2 |  |  | NEW ITEM ADDED
7131310013 | 3 Ø 4 Wire 0.5S, 5 Amp. consumer meter | Each | 3829.1 | HT TRIVECTOR METER 5 AMPS | ISI MARK
7131310015 | CT operated electronic static meters with AMR (Composite Unit) with LTCTs / Modem / Meter / Meter Box. | Each | 12340.31 | ELECTORNIC LTCT METER 3X4 100/5 A | ISI MARK
7131310033 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | Each | 3611.89 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310034 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category B | Each | 3611.89 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310035 | 3 Ø 3 Wire 0.2S, 1 Amp. bulk consumer meter | Each | 16982.09 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310036 | 3 Ø 4 Wire 0.2S, 1 Amp. bulk consumer meter | Each | 16982.09 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310042 | 3 Ø 4 Wire 0.2S 5A bulk consumer meter | Each | 16982.09 |  | ISI MARK
7131310037 | Test terminal Box (TTB) | Each | 923.52 | TTB
7131310997 | CT operated electronic static meters 100/5 Amp. With data storage. | Each | 1805 | 3 PHASE 4 WIRE LTCT OPERATED METER | ISI MARK
7131320009 | Digital Multimeter Electronic Type | Nos. | 3131.08 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) Digital | Nos. | 3871.98 |  |  | RATE EXCLUDING G.S.T.
7131324780 | Megger 500 V | Nos. | 3757.29
7131324806 | Megger up to 2.5 kV | Nos. | 5662.81 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 6356.09
7131334001 | Set of 3 O.C. relays instantaneous high set feature numerical | Nos. | 5858.7 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH
7131334002 | Set of 2 O.C. + 1 earth fault relay without numerical instantaneous high set feature | Nos. | 5858.7 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO
7131399007 | Master trip relays | Nos. | 1003
7131338004 | Transformer Oil Dielectric Breakdown testkit | Nos. | 63523.76 |  |  | RATE EXCLUDING G.S.T.
7131338025 | Neon tester | Nos. | 59.23 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 250.48
7131387502 | Thermometer (Wall Mounted) | Nos. | 495.57 | THERMOMETER (WALL MOUNTED)
7131390014 | Earthing Coil for messenger wire | Nos. | 191.9
7131390015 | Anchor sleeve for messenger wire | Nos. | 33.18
7131390016 | Universal hook & Bolts & nuts | Nos. | 464.88
7131820031 | LT Single Phase MCB 5 Amps. | Each | 106.37
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 106.37 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 450.8
7131820034 | LT Three Phase MCB 32 Amps. | Each | 450.8
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 3002.87
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 3253.55
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 3253.55
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2377.24
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 5443.3 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900004 | Locally fabricated - 3 Phase fuse units 150 Amps. (Robust fuse for circuit base). | Each | 722.16 | LT ROBUST POLE FUSE UNIT
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 7.7 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 309.19 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 475.35 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 13.19 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 14.29 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 304.8 | H.R.C. FUSE UNITS: -100 Amps.
7131900876 | H.R.C. Fuse 100 Amps. | Each | 118.84 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 765.84 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 847.27 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 595.66 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 595.66 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 577.24 | FUSE WIRE TINNED COPPER 10 SWG
7131900974 | T.C. Fuse Wire 8 SWG | Kg | 595.66 | FUSE WIRE TINNED COPPER 8 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 45.83 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 90.56 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 26.19 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 246.62 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 474.95 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 1052.32 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920001 | Load break switches only without panel | Unit | 43728.99 | LOAD BREAK SWITCH WITHOUT PANEL |  | NEW BIN CODE ALLOTED
7131920002 | Load break switches with panel | Unit | 95320.94 | LOAD BREAK SWITCH WITH PANEL |  | NEW BIN CODE ALLOTED
7131920003 | 3 Way Load break switch | Unit | 308373.8 | 3 WAY LOAD BREAK SWITCH |  | NEW BIN CODE ALLOTED
7131920112 | 11 kV Kiosk VCB | Each | 325864.74 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 779.71 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 1872.24 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 3621.51 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 5084.2 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 6897.94 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 10419.13 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  |  | 51.2435
7131930109 | 33 kV ; 600 Amps with earth switch. | Each |  | 33 KV 600 AMPS WITH EARTH SWITCH ISOLATO |  | ITEM DELETED: NOT TO BE USED
7131930221 | 11 kV Porcelain A.B. Switch | Each | 8496 | AB Switch with complete fitting 11 KV
7131930321 | 33 kV Porcelain A.B. Switch | Each | 18863.48 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1177.88 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 2886.87 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 23345.09 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 40401.22 | 33 KV Isolator 800A without earth switch
7131931091 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure | Set | 28693.62
7131931095 | Mounting GI structure for above isolator | Set | 14679.61
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 2502.57 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 23774.42 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 23774.42
7131940871 | Indoor Type Automatic Control Unit along with APFC Relay | No. | 48181.89
7131941762 | 11 kV VCB without control panel & CT's. | Each | 119502.62 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 244236.87 | 33KV VCB FOR 30 VOLT DC
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1022.07 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1231.19 | DISTRIBUTION BOX 3 PH 4 CONNECTOR
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 42226.35
7131950016 | 11 kV Sectionalizer. | Each | 362271.33
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 15779.98 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 19725.8 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 39449.95 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 33850.45 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131950208 | SMC LT Distribution Box for 100 kVA Distribution Transformer | Each | 19116 |  |  | NEW ITEM INTRODUCED
7131950209 | SMC LT Distribution Box for 315 kVA Distribution Transformer | Each | 32804 |  |  | NEW ITEM INTRODUCED
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 27059.11 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 29738.19 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 26777.87 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 28033.32 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960010 | 11 kV Control & Relay Panel for Capacitor Bank | Each | 86141.15
7131960520 | 2 Feeder Control (Static Relays) | Each | 40103.54 | 11KV MULTICIRCUIT (2F) CONTROL PANELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 40103.54 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 40103.54 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm; 3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 213.94
7132004003 | Hack saw frames + B185 | Nos. | 138
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 11.59
7132011171 | Cable Cutter | Nos. | 508.77
7132013331 | Discharge Rod | Nos. | 492.85 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 3131.08
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 1146.9
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 354.86
7132061858 | Combination Plier / Cutting Plier | Nos. | 236.9 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 76.15 | SCREW DRIVER 250MM
7132072007 | Screw driver 200 mm | Nos. | 71.32 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 66.48 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. |  | SCREW DRIVER INSULATED 255 MM |  | ITEM DELETED: NOT TO BE USED
7132074032 | Ring Spanners (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 1658.36 | RING SPANNER
7132074033 | Tube Spanners | Set. | 685.34
7132074034 | Double end spanner (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 784.45 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 508.86
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F & tommy Bar) | Set. | 1510.89 | BOX SPANNER
7132088614 | Pipe Wrench 24 inches size | Nos. | 1259.39
7132088615 | Pipe Wrench 18 inches size | Nos. | 691.16
7132200014 | 1089 kVAR, 12.1 kV, 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kVAR + 726 kVAR 12.1 KV. Bank shall be complete with Capacitor units of 121 kVAR at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin / Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Bolts etc. | Each | 145864.88 | 11 KV CAPACITOR 600KVAR
7132200812 | 5 kVAR | Each | 1611.53 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 3222.06 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 3871.51 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200815 | 20 kVAR | Each | 6424.94 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 192879.89 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each |  | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 25KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 63KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 100KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 200KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210012 | 315 kVA (CEA Design) Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | XMER 315KVA 11/0.43KV CEA REG. CU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210015 | 500 kVA [CEA Design] Copper Wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | 500 kVA [CEA Design] (4 Star) Copper Wound Transformer |  | ITEM DELETED: NOT TO BE USED
7132210106 | 0.2% Reactor suitable for 363 kVAR step | Set | 7083.36
7132210108 | 0.2% Reactor suitable for 726 kVAR step | Set | 8647.51
7132210215 | 50 kVA (Copper winding) | Each | 136597.53 | TRANSFORMER 33/.4KV 50KVA
7132220091 | Power Transformer 1600 kVA | Each | 805738.17 | TRANSFORMER 33/11KV 1.6 MVA POWER
7132220095 | Power Transformer 3150 kVA | Each | 2393149.15 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 5000 kVA | Each | 3379006.13 | TRANSFORMER 33/11KV 5 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 237215.36 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 356.08 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 218950.07 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 356.08 | L.T. C.T.200/5 Amps.
7132230021 | L.T.C.T. 300/5 Amps. | Each | 285.09 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 285.09 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1-1A | No. | 487901.14 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 25179.73 | 33KV CT 400-200/5-5A
7132230065 | 132 kV C.T. 600-300/1-1A | No. | 327045.54 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV
7132230075 | 132 kV C.T. 150-75/1-1A | No. | 373395.01 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1-1A | No. | 822690.98 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1-1A | No. | 538433.72 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1-1A | No. | 498097.94 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 38077.08
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 86339.7 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 13709.83 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 13447.4 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 26176.89 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5-5) Amps oil filled | Each | 19689.9 | 33KV CT's(200-100/5)A oil filled OD Type
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each |  | 33KV CT's (100-50/5)A oil filled OD Type |  | ITEM DELETED: NOT TO BE USED
7132230330 | 132 kV C.T. 100-50/1-1A | No. | 375737.03 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE
7132230332 | 132 kV C.T. 200-100/1-1A | No. | 349648.82 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1-1A | No. | 299323.85 | CURRENT X-MER 300-150/1/1A - 132KV
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A |  | ITEM DELETED: NOT TO BE USED
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 34927.99 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A |  | ITEM DELETED: NOT TO BE USED
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 38073.65 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 34307.96 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A |  | ITEM DELETED: NOT TO BE USED
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 37649.28 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230414 | 11 kV CTPT Unit 50/5 A | Each | 38836.49 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 74048.2 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 83038.2 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A |  | ITEM DELETED: NOT TO BE USED
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 77768.42 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A |  | ITEM DELETED: NOT TO BE USED
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 66731.77 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 62503.51 | OIL IMM 3 PH CTPT UNITS 33 KV-100 & 200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 63743.59 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 85041.37 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230471 | 11 kV 3 PH Residual Voltage Transformer | Each | 34386.84
7132230473 | 11 kV PT Station Type | No. |  |  |  | ITEM DELETED: NOT TO BE USED
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 10323.86 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 16566.35 | VOLTAGE TRANSFORMER 33 KV / 110 VOLTS SINGLE
7132230501 | 132 kV P.T. | No. | 258404.98 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 526838.77 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132401672 | Small Steel Almirah 50'' | No. | 10030 | STEEL ALMIRAH SMALL SIZE
7132404015 | Safety belts | Nos. | 637 | SAFETY BELTS
7132404016 | Safety helmets | Nos. | 144.05 | SAFETY HELMETS
7132404366 | Battery | No. | 55627.8 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 151.91 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 2662.68 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406420 | Pilfer proof SMC/FRPP/PPO LTCT meter box | Each | 3362.21
7132406425 | Universal Meter Box for HT meters. | Each | 3232.14 | Universal Meter Box for HT meters.
7132406721 | CT operated electronic static meters with DLMS. | Each | 2673.28 | LTCT METER WITH DLMS | ISI MARK
7132409830 | Office Chair cane seat & back with full arms rest | No. | 3776 | S-TYPE STEEL CHAIR WITH TEAK WOOD HAND
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 551.38 | RUBBER HAND GLOVES
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 5990.38 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 757.71 | RAIN COATS WITH HOODS |  | RATE EXCLUDING G.S.T.
7132427635 | Gum Boots | Nos. | 510.12 | GUM BOOTS |  | RATE EXCLUDING G.S.T.
7132438002 | Silica gel | Kg | 188.56 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 5.29 | POLYCARBONATE SEAL
7132444007 | Grounding Sticks (Galvanised Earthing Rods 25 mm, 3 Mtr. long) | Set. | 1035.21
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 4769.91 | METTING RUBBER 1900X1800X12MM
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 317.74
7132457798 | Transformer Oil In Barrel | KL | 85255.47 | TRANSFORMER OIL In Tanker/barrel
7132457798 | Transformer Oil In Tanker | KL | 72558.67 | TRANSFORMER OIL In Tanker/barrel
7132459005 | Poly Carbonate seal double anker type | Each | 6.04 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | 1183.33 | HDPE PIPE 200MM ID; 240MM OD
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 430.3 | JOINTING ARRANGEMENT OF HDPE PIPE
7132468558 | Battery charger | Each | 10532.35 | 30 Volt 100 AH lead acid battery charger
7132475019 | Files of sizes | Set. | 358.99
7132475019 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 128.74 |  |  | RATE EXCLUDING G.S.T.
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 14.75 | PVC INSULATION TAPES 19 MM WIDE AND IN R |  | RATE EXCLUDING G.S.T.
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 69.78 |  |  | RATE EXCLUDING G.S.T.
7132478004 | Tong tester Digital (1000 A, 500 V) with associated accessories | Nos. | 1566.5 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI
7132478011 | Hand Torch 5 cell | Nos. | 619.07
7132478012 | Hand Torch 3 cell | Nos. | 405.88 | HAND TORCH 3 CELLED
7132478012 | Cotton Waste | Kg | 63.87 | HAND TORCH 3 CELLED |  | RATE EXCLUDING G.S.T.
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 5357.02 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 57.98 |  |  | RATE EXCLUDING G.S.T.
7132490053 | Bitumen compound | Kg | 104.36
7132498006 | River sand | Cmt | 892.5 | RIVER SAND
7130310027 | 11 kV Covered Conductor 50 Sqmm XLPE insulation | Mtr. | 504.97 | 11KV COVERED CONDUCTOR XLPE 50SQMM
7130310029 | 11 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 608.7 | 11KV COVERED CONDUCTOR XLPE 70SQMM
7130310043 | 11 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 777.29 | 11KV COVERED CONDUCTOR XLPE 99SQMM
7130310047 | 33 kV Covered Conductor 157 Sqmm XLPE insulation | Mtr. | 1146.65 | 33KV COVERED CONDUCTOR XLPE 157SQMM
7130310048 | 33 kV Covered Conductor 241 Sqmm XLPE insulation | Mtr. | 1615.65 | 33KV COVERED CONDUCTOR XLPE 241SQMM
7130310045 | 33 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 716.9 | 33KV COVERED CONDUCTOR XLPE 70SQMM
7130310046 | 33 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 815.32 | 33KV COVERED CONDUCTOR XLPE 99SQMM
7130310025 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 12571.68 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310026 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 20446.28 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310034 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 137221.8 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310035 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 201772.75 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7131310168 | Spot Billing Machine | Each | 11938.19
11 kV Oil Immersed 3 Phase CT-PT Unit of capacity --
7132230410 | 200/5 Amp | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7132230403 | 100/5 Amp | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131960919 | 33 kV 2 feeder control panel (Static Relays) | Each | 40103.54
7130870040 | G.I.Strip 25x3 mm | Kg | 88.66
7130640039 | M.S.Strip 25x3 mm. (0.6 kg/Mtr.) | Kg | 39.17 | M.S.Strip 25x3 mm. |  | NEW BIN CODE ALLOTED
7132444005 | Numerical Poly Carbonate seals | No | 9.28
7130820013 | 33 kV Polymer Disc Insulator (45 kN) | No | 219.41
7131930110 | D.O.Fuse Polymer unit 11 kV | Each | 1611.25
7131930111 | D.O.Fuse Polymer unit 33 kV | Each | 2305.94
7130800001 | PCC Pole 200 kG; 9.0 Mtr. Long | Each | 3046.2 |  |  | Material cost including GST and labour.
7130800002 | PCC Pole 365 kG; 11 Mtr. Long | Each | 7605.2 |  |  | Material cost including GST and labour.
7130820001 | 11 kV Polymer Post Insulator | Nos. | 239.23
7130820002 | 33 kV Polymer Post Insulator | Nos. | 829.28
7130820010 | Silicon rubber composite insulator / 11 kV 45 kN Polymeric Insulator | Nos. | 119.1
7131930107 | Polymer A.B.Switch with complete fitting 11 kV | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131930108 | Polymer A.B.Switch with complete fitting 33 kV | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 200 Kg 8.0 Meter long PCC Pole | No | 2552.95 |  |  | Material cost including GST and labour.
7130311023 | 2.5 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 23.03 | 2.5 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311024 | 4.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 27.63 | 4.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311025 | 6.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 40.3 | 6.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311026 | 6.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 48.36 | 6.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311027 | 8.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 58.72 | 8.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311028 | 10 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 70.24 | 10 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311029 | 16 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 92.12 | 16 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311030 | 25 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 117.45 | 25 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311085 | 240 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 166413.18 | 240 sq.mm Single Core PVC Sheathed Unarmoured Cables |  | NEW ITEM ADDED
7132210017 | 16 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 48638.84 | XMER 16KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210018 | 25 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 54301.19 | XMER 25KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210019 | 63 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 98272.48 | XMER 63KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210020 | 100 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 129355.28 | XMER 100KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210021 | 200 kVA, Aluminium wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 243208.4 | XMER 200KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132220081 | 315 kVA, Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 581089.77 |  | ISI MARK
7132220082 | 500 kVA, Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each | 878421.17 |  | ISI MARK
7130640008 | RCC Block (with 6 mm MS Bar) | Each | 158 |  |  | Material cost including GST and labour.
7131210011 | LED 9 Watt Lamp (without holder) | Each | 72.23 | LED 9 W lamp with holder
7131210009 | LED Tube Light, 20 Watt | Set | 227.03 | LED Tube Light, 20 Watt |  | NEW BIN CODE ALLOTED
7131210030 | 18 W LED Street Light complete set | Set | 2336.88 | 18 W LED Street Light complete set |  | NEW BIN CODE ALLOTED
7131210031 | 35 W LED Street Light complete set | Set | 3018.76 | 35 W LED Street Light complete set |  | NEW BIN CODE ALLOTED
7131210032 | 70 W LED Street Light complete set | Set | 4270.41 | 70 W LED Street Light complete set |  | NEW BIN CODE ALLOTED
7131210033 | 110 W LED Street Light complete set | Set | 5803.49 | 110 W LED Street Light complete set |  | NEW BIN CODE ALLOTED
7131210034 | 190 W LED Street Light complete set | Set | 10235.13 | 190 W LED Street Light complete set |  | NEW BIN CODE ALLOTED
7131210035 | 190 W LED Flood Light complete set | Set | 9930.01 | 190 W LED Flood Light complete set |  | NEW BIN CODE ALLOTED
7131210036 | 110 W LED Flood Light complete set | Set | 6631.57 | 110 W LED Flood Light complete set |  | NEW BIN CODE ALLOTED
7131210023 | LED Lamps with complete fitting-24 W | Nos. |  | 24 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210024 | LED Lamps with complete fitting-48 W | Nos. |  | 48 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210025 | LED Lamps with complete fitting-60 W | Nos. |  | 60 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131941763 | 3 Way RMU, 2OD + 1VL, One Incomer + One Breaker + One Outgoing, 350 MVA, 650 Amps. | Unit | 784652.75 | 11 kV RMU 3 WAY,2 OD+1 VL, 350 MVA, 650 A.
7131941764 | 4 Way RMU, 2OD + 2VL, (One Incomer + Two Breakers + One Outgoing, 350 MVA, 650 Amps. | Unit | 1114574.84 | 11 kV RMU 4 WAY,2 OD+2 VL, 350 MVA, 650 A.
7131941765 | 5 Way RMU, 2OD + 3VL, (One Incomer + Three Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 1438620.41 | 11 kV RMU 5 WAY,2 OD+3 VL, 350 MVA, 650 A.
7131941766 | 6 Way RMU, 2OD + 4VL,(One Incomer + Four Breakers + One Outgoing, 350 MVA, 650 Amps. | Unit | 1762665.99 | 11 kV RMU 6 WAY,2 OD+4 VL, 350 MVA, 650 A.
7131941767 | 1OD for RMU | Unit | 282333.77 | 1OD for RMU
7131941768 | 1VL for 350 MVA, 650 Amps RMU | Unit | 329922.08 | 1VL for 350 MVA, 650 Amps RMU
7132230009 | Indoor Type 33 kV Metering Cubical CTPT Unit 10/5 A | Each | 218950.07 | INDOOR TYPE 33 KV 10/5A CT:PT CUBICAL UNIT
7132230011 | Indoor Type 33 kV Metering Cubical CTPT Unit 25/5 A | Each | 218950.07 | INDOOR TYPE 33 KV 25/5A CT:PT CUBICAL UNIT
7132230012 | Indoor Type 33 kV Metering Cubical CTPT Unit 200/5 A | Each | 237215.36 | INDOOR TYPE 33 KV 200/5A CT:PT CUBICAL UNIT
7132230008 | Indoor Type 11 kV Metering Cubical CTPT Unit 10/5 A | Each | 71698.43 | INDOOR TYPE 11 KV 10/5A CT:PT CUBICAL UNIT
7132230026 | Indoor Type 11 kV 15/5 A Metering Cubical CT-PT Units | Each | 71698.43 | Indoor Type 11kV 15/5A CTPT Cubical Unit |  | NEW BIN CODE ALLOTED
7132230010 | Indoor Type 11 kV Metering Cubical CTPT Unit 25/5 A | Each | 71698.43 | INDOOR TYPE 11 KV 25/5A CT:PT CUBICAL UNIT
7132230027 | Indoor Type 11 kV 50/5 A Metering Cubical CT-PT Units | Each | 71698.43 | Indoor Type 11kV 50/5A CTPT Cubical Unit |  | NEW BIN CODE ALLOTED
7131980004 | (0+1) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH ONE 630 A LOAD BREAK SWITCH. | No. | 238468.83
7131980005 | (0+3) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH THREE 630 A LOAD BREAK SWITCHES. | No. | 440960.38
7131980006 | (0+4) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR 630 A LOAD BREAK SWITCHES. | No. | 535006.39
7131980007 | (0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER IN BETWEEN AFTER ISOLATOR. | No. | 852528.09
7131980008 | (0+2)+BC+(0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH SIX NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER WITH LBS IN BETWEEN AFTER ISOLATOR. | No. | 1348250.47
7131980001 | 12 kV, Outdoor type Vacuum Capacitor switches | No. | 69897.89
7131920028 | AC Distribution board for AC/DC Supply | No. | 11255.65
7132486843 | Chem Rod Earthing electrode (Chemical Earthing) [As per specification given in Schedule-C-20] | Job | 9231.08 |  |  | RATE EXCLUDING G.S.T.
7130840003 | Surge Arrestor | No. | 852.08
7131950396 | Ground connection for Messenger Wire | No. | 129.46
7132406800 | 33/11 kV S/S (Name Plate) Board | Job | 9713.03
7131210840 | 11 kV Fault Passage Indicator for Overhead line | No. | 14554.7 |  |  | RATE EXCLUDING G.S.T.
7132455003 | SMC Meter Board 350x200x40 mm (minimum) thickness 2.5 mm | No. | 148.56 | SMC Meter Board 350x200x40 mm, thickness 2.5 mm |  | NEW BIN CODE ALLOTED
7132455004 | SMC Board 200x150x40 mm (minimum) thickness 2.5 mm | No. | 116.72 | SMC Board 200x150x40 mm thickness 2.5 mm |  | NEW BIN CODE ALLOTED
7131920004 | Piano type ISI mark 250V/5A switch. | No. | 10.61 | Piano type ISI mark 250V/5A switch. |  | NEW BIN CODE ALLOTED
7131920005 | 250V/5A ISI mark 3 pin Socket | No. | 26.53 | 250V/5A ISI mark 3 pin Socket |  | NEW BIN CODE ALLOTED
7131920006 | 250V/5A ISI mark holder. | No. | 15.92 | 250V/5A ISI mark holder. |  | NEW BIN CODE ALLOTED
7131390482 | Earthing terminal (having suitable size of 10 mm Dia GI bolt with 3 nos. nuts & washers) along with Staples/ Nut-Bolts/ Nails | No. | 53.06 | Earth terminal(10mm Dia GI bolt with 3 no) nuts & washers) along with Staples/ Nut-Bolts/ Nails |  | NEW BIN CODE ALLOTED
7130310081 | Internal wiring using 1.5 sqmm copper multistrands PVC insulated ISI marked cable (Average cable length 6 Mtr.) | Mtr | 7.22 | 1.5 sqmm copper multistrand PVC cable |  | NEW BIN CODE ALLOTED
7132461006 | 25 mm Dia PVC pipe or equivalent for internal house wiring (3 Mtr) | Feet | 5.76 | 25 mm Dia PVC pipe or equivalent (3 Mtr) |  | NEW BIN CODE ALLOTED
7132498054 | Bhatta brick | No. | 6.09 | Bhatta brick |  | NEW BIN CODE ALLOTED
7131397216 | Meter Sealing Wire | Kg | 193.67
7132010551 | Hand Operated type 25 sq.mm. to 400 sq.mm Crimping Tool | No. | 9126.52
7132010552 | Hydraulic type Crimping Tool with suitable Dies for crimping Lugs of size up to 400 sq.mm. | Set | 11016.76
7132478005 | RECHARGEABLE L.E.D. HAND TORCH | No | 789.73 | RECHARGEABLE L.E.D. HAND TORCH
7132089020 | Cable separator in RCC Pipe with Angle Cross of 50x50x6 mm Angle @ 2 No. in one pipe | No | 696.3 | Cable separator in RCC Pipe with 50x50x6 mm Angle
7132200004 | 11 kV Capacitor Unit with Expulsion Tube | Each | 106.2 |  | (cost per kVAR)
Note on B181: Barun Chakraborty: Earlier name was - Providing, Fabricating and fixing 8 SWG Chain link fencing (TATA Make) 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. T&D/DRG/MISC/2 Revision -2
Note on B331: Author: NEW ITEM ADDED
Note on B332: Author: NEW ITEM ADDED
Note on B333: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S Consumer meter
Note on B335: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category A
Note on B336: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category B
Note on B337: Barun Chakraborty: Earlier name was - 3 Ø 3 Wire 0.2S bulk consumer meter
Note on B338: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.2S bulk consumer meter
Note on B343: Barun Chakraborty: Earlier name was - Earth resistance tester (20/200/2000 Ω)
Note on B347: Barun Chakraborty: Earlier name was - Set of 3 O.C. relays instantaneous high set feature
Note on B348: Barun Chakraborty: Earlier name was - Set of 2 O.C.+ 1 earth fault relay without instantaneous high set feature
Note on B366: Barun Chakraborty: Earlier name was - Locally fabricated - 3 Phase fuse units (Robust fuse for circuit base)
Note on B423: Author: NEW ITEM ADDED
Note on B424: Author: NEW ITEM ADDED
Note on B441: Barun Chakraborty: Earlier name was - Combination Plier
Note on B521: Author: Earlier name was - Battery (Low Maintenance SAN container)
Note on B547: Barun Chakraborty: Earlier name was - Tong tester
Note on B602: Barun Chakraborty: Earlier name was - LED 9 Watt Lamp
Note on B634: Barun Chakraborty: Earlier name was - Chem Rod Earthing electrode (Chemical Earthing)
Note on C173: Author: Old Unit- Each
Note on C174: Author: Old Unit- Each
Note on C181: Author: Earlier Sq.Mtr
Note on C634: Barun Chakraborty: Earlier unit was - No.

## A-1
COST SCHEDULE A-1
1 KM OF 33 kV LINE ON PCC POLES / H-BEAMS WITH MAXIMUM SPAN OF 100 METERS USING RACCOON CONDUCTOR
2019-20
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4402.65 | 44026.5
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 53.8792 | 259859.2851
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7605.2 | 76052
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2429.24 | 24292.4 | 10 | 2429.24 | 24292.4 | 10 | 2429.24 | 24292.4
5 | Back Clamp for Cross Arm
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 10 | 300.41 | 3004.1 |  |  |  | 10 | 300.41 | 3004.1
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 10 | 333.29 | 3332.9
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 404.18 | 4041.8 | 10 | 404.18 | 4041.8 | 10 | 404.18 | 4041.8
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 118.52 | 1185.2 | 10 | 118.52 | 1185.2 | 10 | 118.52 | 1185.2
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 325.76 | 9772.8 | 30 | 325.76 | 9772.8 | 30 | 325.76 | 9772.8
9 | Raccoon ACSR Conductor (80 Sqmm, Al. Eq) with 3% sag | 7130830060 | Mtr | 3100 | 51.3096 | 159059.667 | 3100 | 51.3096 | 159059.667 | 3100 | 51.3096 | 159059.667
10 | Jointing Sleeves suitable ( for 80 Sqmm, Al. Eq. ACSR cond.) | 7130830050 | No | 6 | 37.29 | 223.74 | 6 | 37.29 | 223.74 | 6 | 37.29 | 223.74
11 | (i) Stay set 20 mm | 7130860033 | No | 3 | 829.62 | 2488.86 | 3 | 829.62 | 2488.86 | 3 | 829.62 | 2488.86
| (ii) Stay Clamp For PCC Pole | 7130810193 | Pair | 3 | 300.41 | 901.23 |  |  |  | 3 | 300.41 | 901.23
| (iii) Stay Clamp For "H" Beam | 7130810692 | Pair |  |  |  | 3 | 333.29 | 999.87
| (iv) Stay Wire 7/8 SWG @ 8.5 kg/ stay | 7130860076 | Kg | 25.5 | 71.9816 | 1835.5318 | 25.5 | 71.9816 | 1835.5318 | 25.5 | 71.9816 | 1835.5318
12 | Concreting of supports @ 0.6 Cmt. Per pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC; and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole. (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Material cost including GST and labour.
13 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 151.45 | 212.03 | 6 | 151.45 | 908.7 | 1.4 | 151.45 | 212.03
14 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 338.4 | 507.6 | 6 | 338.4 | 2030.4 | 1.5 | 338.4 | 507.6
15 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 78.5018 | 1570.0366 | 20 | 78.5018 | 1570.0366 | 20 | 78.5018 | 1570.0366
16 | Danger Board | 7130880041 | No | 10 | 92.6 | 926 | 10 | 92.6 | 926 | 10 | 92.6 | 926
17 | Binding wire and tape | 7130830006 | Kg | 3.5 | 160.41 | 561.435 | 3.5 | 160.41 | 561.435 | 3.5 | 160.41 | 561.435
18 | M.S. Nuts and Bolts |  | Kg | 17 |  |  | 17 |  |  | 18
| 16x65 mm | 7130620614 | Kg |  | 70.4 |  | 7 | 70.4 | 492.8 |  | 70.4
| 16x90 mm | 7130620619 | Kg | 3 | 70.4 | 211.2 |  | 70.4 |  | 3.5 | 70.4 | 246.4
| 16x140 mm | 7130620625 | Kg |  | 69.2 |  | 10 | 69.2 | 692 |  | 69.2
| 16x160 mm | 7130620627 | Kg | 14 | 69.2 | 968.8 |  | 69.2 |  | 14.5 | 69.2 | 1003.4
19 | Guarding 33 kV |  | Rs |  |  | 12522.6544 |  |  | 12522.6544 |  |  | 12522.6544
| (i) G.I. Wire 6 SWG | 7130870045 | Kg | 49 | 65.0097 | 3185.4733 | 49 | 65.0097 | 3185.4733 | 49 | 65.0097 | 3185.4733
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 20 | 65.0097 | 1300.1932 | 20 | 65.0097 | 1300.1932 | 20 | 65.0097 | 1300.1932
| (iii) 33 kV guarding channel | 7130897759 | Set | 1 | 3453.23 | 3453.23 | 1 | 3453.23 | 3453.23 | 1 | 3453.23 | 3453.23
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 333.29 | 999.87 | 3 | 333.29 | 999.87 | 3 | 333.29 | 999.87
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 69.2 | 83.04 | 1.2 | 69.2 | 83.04 | 1.2 | 69.2 | 83.04
| (vi) I--Bolt Big Size | 7130620013 | No | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 829.62 | 1659.24 | 2 | 829.62 | 1659.24 | 2 | 829.62 | 1659.24
| (viii) Stay wire 7/8 SWG & 8.5 Kg/stay | 7130860076 | Kg | 17 | 71.9816 | 1223.6879 | 17 | 71.9816 | 1223.6879 | 17 | 71.9816 | 1223.6879
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 70.4 | 105.6 | 1.5 | 70.4 | 105.6 | 1.5 | 70.4 | 105.6
20 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 274251.5848 |  |  | 510556.08 |  |  | 321196.8848
21 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 232416.5973 |  |  | 432674.6441 |  |  | 272200.7499 | NEW ROW ADDED
22 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 20568.8689 |  | 0.075 | 38291.706 |  | 0.075 | 24089.7664 | Earlier name was - Incidental Charges @ 9%
23 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 389.1481 | 3891.4812 | 0 | 0 | 0 | 0 | 0 | 0
24 | Labour charges as per Schedule No.- AL-1 |  |  |  |  | 47398.72 |  |  | 55457.81 |  |  | 52789.87
25 | Labour charges for concreting |  | Cmt | 2 | 609.1748 | 1218.3496 | 8 | 609.1748 | 4873.3984 | 7 | 609.1748 | 4264.2236
26 | Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 13635.8014 |  |  | 13635.8014 |  |  | 13635.8014
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 20, 22, 23, 24, 25, 26 |  |  |  |  | 45120.6007 |  |  | 77851.8495 |  |  | 51997.0683
28 | Total Estimated Cost excluding GST (Row 21, 22, 23, 24, 25, 26, 27) |  |  |  |  | 364250.4191 |  |  | 622785.2092 |  |  | 418977.4794
29 | Applicable CGST @ 9% on Row 28 |  |  |  | 0.09 | 32782.5377 |  | 0.09 | 56050.6688 |  | 0.09 | 37707.9731
30 | Applicable SGST @ 9% on Row 28 |  |  |  | 0.09 | 32782.5377 |  | 0.09 | 56050.6688 |  | 0.09 | 37707.9731
31 | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 429815.4945 |  |  | 734886.5469 |  |  | 494393.4257
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 429815 |  |  | 734887 |  |  | 494393
Note:-
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on B46: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D14: Barun Chakraborty: Earlier unit was - No.
Note on D22: Barun Chakraborty: Earlier unit was - No.
Note on F48: Barun Chakraborty: Earlier - 0.09
Note on I48: Barun Chakraborty: Earlier - 0.09
Note on L48: Barun Chakraborty: Earlier - 0.09

## A-2 (A)
COST SCHEDULE A-2 (A)
| 33 kV FOUR POLE STRUCTURE ON PCC / H-BEAM POLE | [5 empty] | 2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty | PCC Pole 280 kg 9.1 Mtr. Long | H-Beams 37.1 Kg/Mtr., 13 Mtr. Long
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 280 Kg.,9.1 Mtrs. long PCC Poles | 7130800033 | No | 4402.65 | 4 | 17610.6
2 | H-Beams 152 X 152 mm., 37.1 Kg/Mtr 13 Mtr. Long (482.3 Kg x 4 No = 1929.2 Kgs) | 7130601958 | Kg | 53.8792 | 1929.2 |  | 103943.7141
3 | D.C.cross- arm of 100 X 50 X 6 mm. suitable for 5' centre DP | 7130810608 | Set | 5601.21 | 2 | 11202.42 | 11202.42
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 256.44 | 24 | 6154.56 | 6154.56
5 | 33 kV Polymer Disc Insulator | 7130820013 | No | 219.41 | 24 | 5265.84 | 5265.84
6 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 67.4322 | 50 | 3371.612 | 3371.612
7 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No. | 325.76 | 8 | 2606.08 | 2606.08
8 | DC cross arm 3.8 Mtr. Channel of 100x50 mm | 7130810006 | Set | 7091.89 | 8 | 56735.12 | 56735.12
9 | (i) Stay Clamp For PCC Pole | 7130810193 | Pair | 300.41 | 16 | 4806.56
| (ii) Stay Clamp For "H" Beam | 7130810692 | Pair | 333.29 | 16 |  | 5332.64
10 | 33 kV AB Switch | 7131930321 | Each | 18863.48 | 4 | 75453.92 | 75453.92
11 | Concreting of supports @ 0.5 Cmt Per pole for PCC Pole and @ 0.05 Cmt per pole for base padding for PCC pole (1:3:6) | 7130200202 | Cmt. | 2970 | 2.2 | 6534 |  | Material cost including GST and labour.
| Concreting of supports @ 0.6 Cmt. Per pole for H-Beam and @ 0.05 Cmt per pole for base padding for H-Beam pole (1:3:6) | 7130200202 | Cmt. | 2970 | 2.6 |  | 7722 | Material cost including GST and labour.
12 | M.S.Angle 75x75x6 mm (for bracing 4 No. @ 60 kg each) | 7130600051 | Kg | 43.1218 | 60 | 2587.3092 | 2587.3092
13 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 118.52 | 4 | 474.08 | 474.08
14 | Red oxide paint | 7130211158 | Ltr | 151.45 | 6 |  | 908.7
15 | Aluminium paint | 7130210809 | Ltr | 338.4 | 6 |  | 2030.4
16 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 78.5018 | 8 | 628.0146 | 628.0146
17 | Danger Board | 7130880041 | No | 92.6 | 4 | 370.4 | 370.4
18 | Strain Plate (65x8) mm | 7130810624 | No | 96.9 | 12 | 1162.8 | 1162.8
19 | M.S.Nuts and Bolts |  | Kg
| 16x40 mm | 7130620609 | Kg | 71.59 | 2 |  | 143.18
| 16x65 mm | 7130620614 | Kg | 70.4 | 2 |  | 140.8
| 16x90 mm | 7130620619 | Kg | 70.4 | 10 | 704 | 704
| 16x200 mm | 7130620631 | Kg | 69.2 | 15 | 1038 | 1038
20 | T-Clamp for Dog Conductor. | 7130830585 | No | 275.5 | 6 | 1653 | 1653
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 198358.3158 | 289628.5899
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 168100.2677 | 245447.9575 | NEW ROW ADDED
23 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 14876.8737 | 21722.1442 | Earlier name was - Incidental Charges @ 9%
24 | Labour charges for concreting of PCC Pole |  | Cmt | 609.1748 | 2.2 | 1340.1845
25 | Labour charges for concreting of H-Beam Pole |  | Cmt | 609.1748 | 2.6 |  | 1583.8545
26 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 389.1481 | 4 | 1556.5925 | 0
27 | Labour charges as per Schedule No.- AL-2(A) |  |  |  |  | 25543.22 | 24626.36
28 | Transportation charges |  |  |  |  | 13409.6593 | 13409.6593
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on --
(i) | For PCC Pole - Row - 21, 23, 24, 26, 27, 28 |  |  |  |  | 31885.6057
(ii) | For H-Beam Pole - Row - 21, 23, 25, 27, 28 | [5 empty] | 43871.326
30 | Total Estimated Cost excluding GST --
(i) | For PCC Pole - Row - 22, 23, 24, 26, 27, 28, 29 |  |  |  |  | 256712.4034
(ii) | For H-Beam Pole - Row - 22, 23, 25, 27, 28, 29 | [5 empty] | 350661.3015
31 | Applicable CGST @ 9% on Row 30 |  |  | 0.09 |  | 23104.1163 | 31559.5171
32 | Applicable SGST @ 9% on Row 30 |  |  | 0.09 |  | 23104.1163 | 31559.5171
33 | Total Estimated Cost including GST (Row 30+31+32) |  |  |  |  | 302920.636 | 413780.3358
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 302921 | 413780
Note on B34: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on C19: 89326879: 2.6 cmt for H-Beam and 2.2 Cmt for PCC Pole
Note on C20: 89326879: 2.6 cmt for H-Beam and 2.2 Cmt for PCC Pole
Note on D16: Barun Chakraborty: Earlier unit was - No.

## A-2 (B)
COST SCHEDULE A-2 (B)
2019-20
33 kV DP STRUCTURE ON PCC POLES / H-BEAM POLE (TO BE SUPPLEMENTED WITH EVERY 1.0 KM OF LINE OF RACCOON / DOG CONDUCTOR)
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg/Mtr 13.0 Mtr long H-Beam |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 4402.65 | 8805.3
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 53.8792 | 51971.857
| (iii) 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 2 | 7605.2 | 15210.4
2 | DC cross arm of 100x50 mm Channel 5' Center | 7130810608 | Set | 1 | 5601.21 | 5601.21 | 1 | 5601.21 | 5601.21 | 1 | 5601.21 | 5601.21
3 | 33 kV Polymer Disc Insulator | 7130820013 | No | 18 | 219.41 | 3949.38 | 18 | 219.41 | 3949.38 | 18 | 219.41 | 3949.38
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 6 | 256.44 | 1538.64 | 6 | 256.44 | 1538.64 | 6 | 256.44 | 1538.64
5 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 325.76 | 977.28 | 3 | 325.76 | 977.28 | 3 | 325.76 | 977.28
6 | Horizontal & cross bracing 5' centre with set of 4 back clamps |  | No | 1 | 3788.9492 |  | 1 | 3920.4692 |  |  | 3788.9492
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 4 | 300.41 | 1201.64 |  |  |  | 4 | 300.41 | 1201.64
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 4 | 333.29 | 1333.16
| (iii) M.S.Angle 65X65x6 mm | 7130600032 | Kg | 60 | 43.1218 | 2587.3092 | 60 | 43.1218 | 2587.3092 | 60 | 43.1218 | 2587.3092
7 | (i) Stay set 20 mm | 7130860033 | No | 6 | 829.62 | 4977.72 | 6 | 829.62 | 4977.72 | 6 | 829.62 | 4977.72
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair | 6 | 300.41 | 1802.46 |  |  |  | 6 | 300.41 | 1802.46
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 6 | 333.29 | 1999.74
| (iv) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 51 | 71.9816 | 3671.0636 | 51 | 71.9816 | 3671.0636 | 51 | 71.9816 | 3671.0636
8 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 96.9 | 581.4 | 6 | 96.9 | 581.4 | 6 | 96.9 | 581.4
9 | Concreting @ 0.6 Cmt per pole for H-Beam supports and 0.5 Cmt per pole for 365 kG 11 Mtr. Long PCC @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam (1:3:6) | 7130200202 | Cmt | 1.9 | 2970 | 5643 | 3.1 | 2970 | 9207 | 2.9 | 2970 | 8613 | Material cost including GST and labour.
10 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 2 | 118.52 | 237.04 | 2 | 118.52 | 237.04 | 2 | 118.52 | 237.04
11 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 151.45 | 75.725 | 2 | 151.45 | 302.9 | 0.5 | 151.45 | 75.725
12 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 338.4 | 169.2 | 2 | 338.4 | 676.8 | 0.5 | 338.4 | 169.2
13 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073
14 | Danger Board | 7130880041 | No | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
15 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795 | 0.5 | 71.59 | 35.795 | 0.5 | 71.59 | 35.795
| 16x65 mm | 7130620614 | Kg | 0.5 | 70.4 | 35.2 | 0.5 | 70.4 | 35.2 | 0.5 | 70.4 | 35.2
| 16x90 mm | 7130620619 | Kg |  | 70.4 |  | 2.5 | 70.4 | 176 |  | 70.4
| 16x140 mm | 7130620625 | Kg | 2 | 69.2 | 138.4 |  |  |  | 2 | 69.2 | 138.4
| 16x200 mm | 7130620631 | Kg | 4 | 69.2 | 276.8 | 3.5 | 69.2 | 242.2 | 4 | 69.2 | 276.8
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 42711.1702 |  |  | 90508.3022 |  |  | 52086.2702
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 36195.9069 |  |  | 76701.951 |  |  | 44140.9069 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 3203.3378 |  |  | 6788.1227 |  | 0.075 | 3906.4703 | Earlier name was - Incidental Charges @ 9%
19 | Labour charges for concreting |  | Cmt | 1.9 | 609.1748 | 1157.4321 | 3.1 | 609.1748 | 1888.4419 | 2.9 | 609.1748 | 1766.6069
20 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 2 | 389.1481 | 778.2962
21 | Labour charges as per Schedule No.- AL-2 |  |  |  |  | 11109.83 |  |  | 11656.81 |  |  | 11908.53
22 | Transport charges upto 50 Kms average lead from Area Store to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 5363.8658 |  |  | 5363.8658 |  |  | 5363.8658
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 16, 18,19, 20, 21, 22 |  |  |  |  | 8040.4915 |  |  | 14525.6928 |  |  | 9378.9679
24 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22, 23) |  |  |  |  | 65849.1603 |  |  | 116924.8841 |  |  | 76465.3478
25 | Applicable CGST @ 9% on Row 24 |  |  |  | 0.09 | 5926.4244 |  | 0.09 | 10523.2396 |  | 0.09 | 6881.8813
26 | Applicable SGST @ 9% on Row 24 |  |  |  | 0.09 | 5926.4244 |  | 0.09 | 10523.2396 |  | 0.09 | 6881.8813
27 | Total Estimated Cost including GST (Row 24+25+26) |  |  |  |  | 77702.0092 |  |  | 137971.3633 |  |  | 90229.1104
28 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 77702 |  |  | 137971 |  |  | 90229
Note:
1 | This Schedule is to be supplemented with Schedule A-1 & A-3.
2 | All the rates are with considering price variation clause.
Note on B36: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D11: 89326879: Earlier unit was - No.
Note on D16: Barun Chakraborty: Earlier unit was - No.
Note on D20: Barun Chakraborty: Earlier unit was - No.

## A-3
COST SCHEDULE - A-3
1 KM OF 33 kV LINE ON PCC POLES / H-BEAM SUPPORT WITH MAXIMUM SPAN OF 100 METERS USING DOG CONDUCTOR
2019-20
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152 mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4402.65 | 44026.5
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 53.8792 | 259859.2851
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7605.2 | 76052
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2429.24 | 24292.4 | 10 | 2429.24 | 24292.4 | 10 | 2429.24 | 24292.4
5 | Back Clamp for Cross Arm
| (i) Stay Clamp For PCC Pole | 7130810193 | Pair | 10 | 300.41 | 3004.1 |  |  |  | 10 | 300.41 | 3004.1
| (ii) Stay Clamp For H-Beam Pole | 7130810692 | Pair |  |  |  | 10 | 333.29 | 3332.9
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 404.18 | 4041.8 | 10 | 404.18 | 4041.8 | 10 | 404.18 | 4041.8
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 118.52 | 1185.2 | 10 | 118.52 | 1185.2 | 10 | 118.52 | 1185.2
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 325.76 | 9772.8 | 30 | 325.76 | 9772.8 | 30 | 325.76 | 9772.8
9 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 3100 | 67.4322 | 209039.944 | 3100 | 67.4322 | 209039.944 | 3100 | 67.4322 | 209039.944
10 | Jointing Sleeves (suitable for 100 Sqmm, Al. Eq. ACSR cond.) | 7130830051 | No | 6 | 145.57 | 873.42 | 6 | 145.57 | 873.42 | 6 | 145.57 | 873.42
11 | Stay set 20 mm | 7130860033 | No | 3 | 829.62 | 2488.86 | 3 | 829.62 | 2488.86 | 3 | 829.62 | 2488.86
12 | Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 3 | 300.41 | 901.23 |  |  |  | 3 | 300.41 | 901.23
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 3 | 333.29 | 999.87
13 | Stay Wire 7/8 SWG @ 8.5 kg Per stay | 7130860076 | Kg | 25.5 | 71.9816 | 1835.5318 | 25.5 | 71.9816 | 1835.5318 | 25.5 | 71.9816 | 1835.5318
14 | Concreting of H-Beam supports @ 0.6 cmt. Per pole and @ 0.3 Cmt per stay and @ 0.05 cmt per pole for base padding for PCC / H- Beam pole (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Material cost including GST and labour.
15 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 151.45 | 212.03 | 6 | 151.45 | 908.7 | 1.4 | 151.45 | 212.03
16 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 338.4 | 507.6 | 6 | 338.4 | 2030.4 | 1.5 | 338.4 | 507.6
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 78.5018 | 1570.0366 | 20 | 78.5018 | 1570.0366 | 20 | 78.5018 | 1570.0366
18 | Danger Boards | 7130880041 | No | 10 | 92.6 | 926 | 10 | 92.6 | 926 | 10 | 92.6 | 926
19 | Binding wire and tape | 7130830006 | Kg | 3.5 | 160.41 | 561.435 | 3.5 | 160.41 | 561.435 | 3.5 | 160.41 | 561.435
20 | M.S. Nuts and Bolts |  | Kg | 18 |  |  | 18 |  |  | 18
| 16x40 mm | 7130620609 | Kg |  | 71.59 |  | 0.5 | 71.59 | 35.795 |  | 71.59
| 16x65 mm | 7130620614 | Kg |  | 70.4 |  | 7.5 | 70.4 | 528 |  | 70.4
| 16x90 mm | 7130620619 | Kg | 3.5 | 70.4 | 246.4 |  | 70.4 |  | 3.5 | 70.4 | 246.4
| 16x140 mm | 7130620625 | Kg |  | 69.2 |  | 10 | 69.2 | 692 |  | 69.2
| 16x160 mm | 7130620627 | Kg | 14.5 | 69.2 | 1003.4 |  | 69.2 |  | 14.5 | 69.2 | 1003.4
21 | Guarding |  |  |  | 12522.6544 |  |  | 12522.6544 |  |  | 12522.6544
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 65.0097 | 3185.4733 | 49 | 65.0097 | 3185.4733 | 49 | 65.0097 | 3185.4733
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 65.0097 | 1300.1932 | 20 | 65.0097 | 1300.1932 | 20 | 65.0097 | 1300.1932
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 1 | 3453.23 | 3453.23 | 1 | 3453.23 | 3453.23 | 1 | 3453.23 | 3453.23
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 333.29 | 999.87 | 3 | 333.29 | 999.87 | 3 | 333.29 | 999.87
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 69.2 | 83.04 | 1.2 | 69.2 | 83.04 | 1.2 | 69.2 | 83.04
| (vi) I-Bolt Big Size | 7130620013 | No | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 829.62 | 1659.24 | 2 | 829.62 | 1659.24 | 2 | 829.62 | 1659.24
| (viii) Stay wire 7/8 SWG & 8.5 Kg/ stay | 7130860076 | Kg | 17 | 71.9816 | 1223.6879 | 17 | 71.9816 | 1223.6879 | 17 | 71.9816 | 1223.6879
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 70.4 | 105.6 | 1.5 | 70.4 | 105.6 | 1.5 | 70.4 | 105.6
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 324951.3418 |  |  | 561257.032 |  |  | 371826.8418
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 275382.4931 |  |  | 475641.5525 |  |  | 315107.4931 | NEW ROW ADDED
24 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 24371.3506 |  | 0.075 | 42094.2774 |  | 0.075 | 27887.0131 | Earlier name was - Incidental Charges @ 9%
25 | Labour charges for concreting |  | Cmt | 2 | 609.1748 | 1218.3496 | 8 | 609.1748 | 4873.3984 | 7 | 609.1748 | 4264.2236
26 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 389.1481 | 3891.4812
27 | Labour charges as per Schedule No.- AL-3 |  |  |  |  | 49222.4 | -- | -- | 57281.22 |  |  | 53215.96
28 | Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 16900.0568 |  |  | 16900.0568 |  |  | 16900.0568
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 22, 24, 25, 26, 27, 28 |  |  |  |  | 52569.3725 |  |  | 85300.7481 |  |  | 59261.7619
30 | Total Estimated Cost excluding GST (Row 23, 24, 25, 26, 27, 28, 29) |  |  |  |  | 423555.5038 |  |  | 682091.2531 |  |  | 476636.5085
31 | Applicable CGST @ 9% on Row 30 |  |  |  | 0.09 | 38119.9953 |  | 0.09 | 61388.2128 |  | 0.09 | 42897.2858
32 | Applicable SGST @ 9% on Row 30 |  |  |  | 0.09 | 38119.9953 |  | 0.09 | 61388.2128 |  | 0.09 | 42897.2858
33 | Total Estimated Cost including GST (Row 30+31+32) |  |  |  |  | 499795.4945 |  |  | 804867.6787 |  |  | 562431.08
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 499795 |  |  | 804868 |  |  | 562431
Note:
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on B49: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D15: Barun Chakraborty: Earlier unit was - No.
Note on D24: Barun Chakraborty: Earlier unit was - No.

## A-3 (A)
COST SCHEDULE -- A-3 (A)
2019-20
SCHEDULE FOR AUGMENTATION OF 1 kM OF 33 kV LINE FROM RACCOON TO DOG CONDUCTOR
S.No. | Particulars | New SAP Bin Code | Unit | Qty | Cost per Unit | Cost
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | ACSR Dog Conductor 100 sq.mm | 7130830063 | Km | 3.1 | 67432.24 | 209039.944
2 | Jointing Sleeves suitable for Dog ACSR Conductor | 7130830051 | No | 6 | 145.57 | 873.42
3 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 6 | 325.76 | 1954.56
4 | Guarding
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 65.0097 | 3185.4733
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 65.0097 | 1300.1932
| (iii) 33 kV Guarding Channel (Set) | 7130897759 | Set | 1 | 3453.23 | 3453.23
| (iv) M.S Nut & Bolt 16x140 mm. | 7130620625 | Kg | 1.2 | 69.2 | 83.04
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 128.08 | 512.32
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 829.62 | 1659.24
| (vii) Stay Wire 7/8 SWG @ 8.5 Kg. Stay | 7130860076 | Kg | 17 | 71.9816 | 1223.6879
| (viii) MS Nut & Bolt 16x90 mm | 7130620619 | Kg | 1.5 | 70.4 | 105.6
5 | Concreting of Stay Set @ 0.3 Cmt per stay (1:3:6) | 7130200202 | Cmt | 0.6 | 2970 | 1782 | Material cost including GST and labour.
6 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 225172.7084
7 | Material cost excluding GST ( Sub Total-1/1.18 ) |  |  |  |  | 190824.3292 | NEW ROW ADDED
8 | Incidental Charges @ 7.5 % on Sub - Total-1 : - |  |  |  | 0.075 | 16887.9531 | Earlier name was - Incidental Charges @ 9%
9 | Labour charges for concreting |  | Cmt | 0.6 | 609.1748 | 365.5049
10 | Labour Charges |  |  |  |  | 23520.29
| Stay erection |  | No | 2 | 212.72 | 425.44
| Stringing of Dog Conductor |  | Ckt Km | 1 | 13674.58 | 13674.58
| Labour Charge for Carpet Guarding |  | Span | 1 | 2582.98 | 2582.98
| Dismantling Charges |  | Ckt Km | 1 | 6837.29 | 6837.29
11 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 6, 8, 9, 10 |  |  |  |  | 33243.3071
12 | Total Estimated Cost excluding GST (Row 7, 8, 9, 10, 11) |  |  |  |  | 264841.3842
13 | Applicable CGST @ 9% on Row 12 |  |  |  | 0.09 | 23835.7246
14 | Applicable SGST @ 9% on Row 12 |  |  |  | 0.09 | 23835.7246
15 | Returnable cost of old conductor assuming 25 years of life & 20 years in service |  |  | 3.1 | 5229.36 | 16211.016
16 | Total Estimated Cost including GST (Row 12+13+14-15) |  |  |  |  | 296301.8174
17 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 296302
Note on B20: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## A-3 (B)
COST SCHEDULE -- A-3 (B)
2019-20
COST SCHEDULE FOR ADDITIONAL (MID SPAN) POLE FOR 33 kV LINE USING 37.1 KG / MTR 13 M. LONG H-BEAM SUPPORT
S. No. | PARTICULARS | New SAP Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) H-Beam
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 482.3 | 53.8792 | 25985.9285
2 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 1 | 2429.24 | 2429.24
3 | Cross Arm Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 1 | 333.29 | 333.29
4 | 33 kV Top Clamp | 7130810676 | No | 1 | 404.18 | 404.18
5 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 1 | 118.52 | 118.52
6 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 325.76 | 977.28
7 | Concreting of H-Beam support @ 0.6 Cmt. per pole and @ 0.05 Cmt per pole for base padding of H-Beam pole (1:3:6). | 7130200202 | Cmt | 0.65 | 2970 | 1930.5 | Material cost including GST and labour.
8 | Red Oxide Paint | 7130211158 | Ltr | 1 | 151.45 | 151.45
9 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4
10 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 2 | 78.5018 | 157.0037
11 | Danger Boards | 7130880041 | No | 1 | 92.6 | 92.6
12 | Binding wire and tape | 7130830006 | Kg | 0.5 | 160.41 | 80.205
13 | M.S. Nuts and Bolts |  | Kg | 2.5
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795
| 16x65 mm | 7130620614 | Kg | 1 | 70.4 | 70.4
| 16x90 mm | 7130620619 | Kg |  | 70.4
| 16x140 mm | 7130620625 | Kg | 1 | 69.2 | 69.2
| 16x160 mm | 7130620627 | Kg |  | 69.2
14 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 33173.9922
15 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 28113.5527 | NEW ROW ADDED
16 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 2488.0494 | Earlier name was - Incidental Charges @ 9%
17 | Labour charges for concreting |  | Cmt | 0.65 | 609.1748 | 395.9636
18 | Labour charges as per Schedule No.- AL-3 (B) (Revised for one Pole) |  |  |  |  | 3344.98
19 | Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 1690.0067
20 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 14, 16, 17, 18, 19 |  |  |  |  | 5136.624
21 | Total Estimated Cost excluding GST (Row 15, 16, 17, 18, 19, 20) |  |  |  |  | 41169.1764
22 | Applicable CGST @ 9% on Row 21 |  |  |  | 0.09 | 3705.2259
23 | Applicable SGST @ 9% on Row 21 |  |  |  | 0.09 | 3705.2259
24 | Total Estimated Cost including GST (Row 21+22+23) |  |  |  |  | 48579.6282
25 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 48580
Note on B27: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## A-4
COST SCHEDULE A-4
1 KM OF 33 kV LINE ON 37.1 KG / MTR 13 M. LONG H-BEAM SUSPENSION TYPE WITH PANTHER CONDUCTOR (WITH MAXIMUM SPAN OF 50 METERS)
2019-20
S. No. | PARTICULARS | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M long (482.30 Kg) x 20 No = 9646 Kgs | 7130601958 | Kg | 9646 | 53.8792 | 519718.5703
2 | DC Cross arm (100x50 mm) Channel 2.4 Mtr. (1.5 X 20 = 30) | 7130810512 | Set | 30 | 4104.29 | 123128.7
3 | 33 kV Suspension Hardware suitable for Panther Conductor (3x20=60) | 7130820312 | Set | 60 | 2197.28 | 131836.8
4 | 33 kV Polymer Disc Insulator (9x20=180) | 7130820013 | No. | 180 | 219.41 | 39493.8
5 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 20 | 118.52 | 2370.4
6 | ACSR Panther Conductor with 5% sag | 7130830070 | Mtr. | 3150 | 151.6531 | 477707.202
7 | Jointing Sleeves suitable for Panther conductor | 7130830971 | No. | 6 | 224.97 | 1349.82
8 | Stay Set 20 mm Complete | 7130860033 | Set. | 12 | 829.62 | 9955.44
9 | Stay Clamp for "H" Beam | 7130810692 | Pair | 100 | 333.29 | 33329
10 | Stay Wire 7/8 SWG @ 8.5 Kg/Stay | 7130860076 | Kg. | 170 | 71.9816 | 12236.8788
11 | Concreting of H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt. per Pole for base Padding & @ 0.3 Cmt. Per stay (1:3:6) | 7130200202 | Cmt. | 17.2 | 2970 | 51084 | Material cost including GST and labour.
12 | Red Oxide Paint | 7130211158 | Ltr. | 26 | 151.45 | 3937.7
13 | Aluminium Paint | 7130210809 | Ltr. | 26 | 338.4 | 8798.4
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg. | 40 | 78.5018 | 3140.0732
15 | Danger Boards | 7130880041 | No. | 20 | 92.6 | 1852
16 | Binding Wire & Tape | 7130830006 | Kg. | 8 | 160.41 | 1283.28
17 | MS Nut & Bolts |  | Kg. | 123
| 16x40 mm | 7130620609 | Kg. | 2 | 71.59 | 143.18
| 16x65 mm | 7130620614 | Kg. | 30 | 70.4 | 2112
| 16x90 mm | 7130620619 | Kg. | 20 | 70.4 | 1408
| 16x140 mm | 7130620625 | Kg. |  | 69.2
| 16x160 mm | 7130620627 | Kg. | 1 | 69.2 | 69.2
| 16x200 mm | 7130620631 | Kg. |  | 69.2
| 16x250 mm | 7130620637 | Kg. | 70 | 69.2 | 4844
18 | MS Angle 65x65x6 for Tie | 7130600032 | Kg. | 435 | 43.1218 | 18757.9917
19 | Strain Plate (65x8 mm) | 7130810624 | No. | 120 | 96.9 | 11628
20 | Guarding 33 kV for single span
| (i) G.I. Wire 6 SWG | 7130870045 | Kg. | 40 | 65.0097 | 2600.3864
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg. | 20 | 65.0097 | 1300.1932
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 2 | 3453.23 | 6906.46
| (iv) M.S Nut & Bolt 16x250 mm. | 7130620637 | Kg. | 5 | 69.2 | 346
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 128.08 | 512.32
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 829.62 | 1659.24
| (vii) Stay Wire 7/8 SWG & 8.5 Kg. Stay | 7130860076 | Kg. | 17 | 71.9816 | 1223.6879
| (viii) Stay Clamp for "H" Beam | 7130810692 | Pair | 2 | 333.29 | 666.58
| (ix) MS Nut & Bolt 16x90 mm | 7130620619 | Kg. | 1 | 70.4 | 70.4
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1475469.7035
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1250398.0538 | NEW ROW ADDED
23 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 110660.2278 | Earlier name was - Incidental Charges @ 9%
24 | Labour charges for concreting |  | Cmt | 17.2 | 609.1748 | 10477.8065
25 | Labour Charges per Km as per Schedule - AL-4 |  | Km | 1 |  | 158248.27
26 | Transport Charges up to 50 km average lead from area Stores to Construction Camp Including Side Transport |  | LS | LS |  | 31954.428
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 21, 23, 24, 25, 26 |  |  |  |  | 223351.3045
28 | Total Estimated Cost excluding GST (Row 22, 23, 24, 25, 26, 27) |  |  |  |  | 1785090.0905
29 | Applicable CGST @ 9% on Row 28 |  |  |  | 0.09 | 160658.1081
30 | Applicable SGST @ 9% on Row 28 |  |  |  | 0.09 | 160658.1081
31 | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 2106406.3067
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 2106406
Note on B45: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D10: Barun Chakraborty: Earlier unit was - No.

## A-5
COST SCHEDULE A-5
33 kV D.P. STRUCTURE ON 13 M. LONG H-BEAM POLE FOR PANTHER CONDUCTOR (TO BE SUPPLEMENTED WITH EVERY 0.3 kM OF SUSPENSION LINE)
2019-20
S. No. | Particulars | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg. | 964.6 | 53.8792 | 51971.857
2 | DC Cross arm (100x50 mm) Channel 5' Center | 7130810608 | Set | 1 | 5601.21 | 5601.21
3 | 33 kV Tension Hardware suitable for Panther Conductor | 7130870318 | Set | 6 | 1009.78 | 6058.68
4 | 33 kV Suspension Hardware suitable for Panther Conductor | 7130820312 | Set | 3 | 2197.28 | 6591.84
5 | 33 kV Polymer Disc Insulator | 7130820013 | No. | 27 | 219.41 | 5924.07
6 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 2 | 118.52 | 237.04
7 | Horizontal & Cross bracing |  | No. | 1
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 333.29 | 1333.16
| (ii) M.S. Angle 65X65x6 mm | 7130600032 | Kg | 60 | 43.1218 | 2587.3092
8 | Stay Set 20 mm complete | 7130860033 | Set. | 6 | 829.62 | 4977.72
9 | Stay Clamp for "H" Beam | 7130810692 | Pair | 9 | 333.29 | 2999.61
10 | Stay Wire 7/8 SWG @ 8.5 Kg./pole | 7130860076 | Kg. | 51 | 71.9816 | 3671.0636
11 | Concreting of H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt per Pole for base Padding & @ 0.3 Cmt. Per stay (1:3:6) | 7130200202 | Cmt. | 3.1 | 2970 | 9207 | Material cost including GST and labour.
12 | Red Oxide Paint | 7130211158 | Ltr. | 2 | 151.45 | 302.9
13 | Aluminium Paint | 7130210809 | Ltr. | 2 | 338.4 | 676.8
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 78.5018 | 314.0073
15 | Danger Board | 7130880041 | No | 2 | 92.6 | 185.2
16 | Strain Plate (65x8 mm) | 7130810624 | No. | 4 | 96.9 | 387.6
17 | MS Nut & Bolts |  | Kg. | 15
| 16x40 mm | 7130620609 | Kg. | 1 | 71.59 | 71.59
| 16x65 mm | 7130620614 | Kg. | 3 | 70.4 | 211.2
| 16x90 mm | 7130620619 | Kg. | 1 | 70.4 | 70.4
| 16x140 mm | 7130620625 | Kg. | 2 | 69.2 | 138.4
| 16x160 mm | 7130620627 | Kg. | 2 | 69.2 | 138.4
| 16x200 mm | 7130620631 | Kg. | 2 | 69.2 | 138.4
| 16x250 mm | 7130620637 | Kg. | 4 | 69.2 | 276.8
18 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 104072.2572
19 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 88196.8281 | NEW ROW ADDED
20 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 7805.4193 | Earlier name was - Incidental Charges @ 9%
21 | Labour charges for concreting |  | Cmt | 3.1 | 609.1748 | 1888.4419
22 | Labour Charges as per Schedule AL-2 |  |  |  |  | 11656.81
23 | Transport Charges up to 50 km. average lead from area Stores to Construction Camp including Side Transport (Transport Schedule T-1) |  |  |  |  | 5363.8658
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 18, 20, 21, 22, 23 |  |  |  |  | 16348.3493
25 | Total Estimated Cost excluding GST (Row 19, 20, 21, 22, 23, 24) |  |  |  |  | 131259.7143
26 | Applicable CGST @ 9% on Row 25 |  |  |  | 0.09 | 11813.3743
27 | Applicable SGST @ 9% on Row 25 |  |  |  | 0.09 | 11813.3743
28 | Total Estimated Cost including GST (Row 25+26+27) |  |  |  |  | 154886.4629
29 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 154886
Note on B36: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D12: Barun Chakraborty: Earlier unit was - No.
Note on D13: Barun Chakraborty: Earlier unit was - No.

## A-6
COST SCHEDULE A-6
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER EXISTING RAILWAY TRACK / ROAD FOR 60 MTR. LONG RAIL / ROAD CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | Using HDD Technique (for Railway works) on 3x400 sq.mm AB XLPE Cable | Using HDD Technique (for Road crossing works) on 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD; 6 Mtr long | 7132461004 | Mtr | 1183.33 | 120 | 141999.6 | 141999.6
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 430.3 | 18 | 7745.4 | 7745.4
3 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2219.2291 | 190 | 421653.5347 | 421653.5347
4 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 35218.1 | 4 | 140872.4 | 140872.4
5 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1113.58 | 24 | 26725.92 | 26725.92
6 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
7 | M.S.Flat (50x6) mm | 7130600173 | kg | 46.9271 | 100 | 4692.714 | 4692.714
8 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 4 | 2224 | 2224
9 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 80 | 2640 | 2640
10 | Sand | 7132498006 | Cmt | 892.5 | 1.2 | 1071 | 1071
11 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3221.41 | 6 | 19328.46 | 19328.46
12 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 51.3096 | 18 | 923.5723 | 923.5723
13 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 275.5 | 6 | 1653 | 1653
14 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 876.17 | 10 | 8761.7 | 8761.7
15 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway authorities including liaisoning work etc. |  | LS | LS | LS | 25000
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 811291.301 | 786291.301
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 687535.0008 | 666348.5601 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 60846.8476 | 58971.8476 | Earlier name was - Incidental Charges @ 9%
19 | Service in lieu of Earthing Coal & Sand etc |  | No | 2765.8829 | 10 | 27658.8289 | 27658.8289
20 | Labour Charges for laying of HDPE Pipe (using HDD Technique ** ) as per Schedule AL-5 |  |  |  |  | 362831 | 362831
21 | Labour Charges for excavation of cable trench beyond the length of HDPE Pipe upto DP Structure |  | CMT | 267.4136 | 12 | 3208.9636 | 3208.9636
22 | Transportation Charges |  |  |  |  | 80692.9991 | 80692.9991
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 16, 18, 19, 20, 21, 22 |  |  |  |  | 168316.2425 | 164956.8675
24 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22, 23) |  |  |  |  | 1391089.8826 | 1364669.0669
25 | Applicable CGST @ 9% on Row 24 |  |  | 0.09 |  | 125198.0894 | 122820.216
26 | Applicable SGST @ 9% on Row 24 |  |  | 0.09 |  | 125198.0894 | 122820.216
27 | Charges payable to Railway including supervision charges etc. [15% of Col. 24] |  |  |  |  | 208663.4824
28 | Municipality Charges payable to Local bodies as per Demand note |  | LS
29 | Total Estimated Cost including GST [for Col. 07 = Row 24+25+26+27] & [for Col. 08 = Row 24+25+26+28] |  |  |  |  | 1850149.5438 | 1610309.4989
30 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1850150 | 1610309
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
** | Horizontal Directional Drilling (HDD) Technique
This schedule is prepared for 60 Mtr Corridor of Railway / Road crossing. Estimate may be framed as per actual site conditions and actual width of the rail / road corridor.
*** | The charges to be paid for according railway permission shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note on B25: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on E15: 89326879: Assuming 2 kg M-seal @ Rs 450/- per kg + PVC Plate 10 mm thick
Note on G29: 89326879: ***
Note on H37: 89326879: Fill appropriate cost here
*
***
Fill appropriate cost

## A-7
COST SCHEDULE A-7
2019-20
SCHEDULE FOR LAST SPAN CABLING OF 33 kV H.T. CONNECTION
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 3x185 sq.mm AB XLPE Cable | 3x240 sq.mm AB XLPE Cable
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 53.8792 | 482.3 | 25985.9285 | 25985.9285
2 | 3x185 sq.mm 33 kV AB XLPE Cable | 7130310053 | Mtr. | 1333.2897 | 50 | 66664.4865
3 | 3x240 sq.mm 33 kV AB XLPE Cable | 7130310054 | Mtr. | 1695.4156 | 50 |  | 84770.7825
4 | 33 kV Termination Kit for 3x185 sqmm AB XLPE Cable * | 7130320039 | Set | 15767.29 | 2 | 31534.58
5 | 33 kV Termination Kit for 3x240 sqmm AB XLPE Cable * | 7130320040 | Set | 18395.19 | 2 |  | 36790.38
6 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 118.52 | 1 | 118.52 | 118.52
7 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | Set | 3361.56 | 2 | 6723.12 | 6723.12
8 | Stay Set 20 mm | 7130860033 | No | 829.62 | 2 | 1659.24 | 1659.24
9 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 71.9816 | 17 | 1223.6879 | 1223.6879
10 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay (1:3:6) | 7130200202 | Cmt | 2970 | 1.25 | 3712.5 | 3712.5 | Material cost including GST and labour.
11 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 1 | 151.45 | 151.45
12 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 1 | 338.4 | 338.4
13 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 78.5018 | 2 | 157.0037 | 157.0037
14 | Danger Board | 7130880041 | No | 92.6 | 1 | 92.6 | 92.6
15 | Stay Clamp for "H" Beam | 7130810692 | Pair | 333.29 | 4 | 1333.16 | 1333.16
16 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 71.59 | 5 | 357.95 | 357.95
17 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 70.4 | 1 | 70.4 | 70.4
18 | Dead end Assembly (Suitable for all size cable) | 7130320044 | No. | 893.65 | 2 | 1787.3 | 1787.3
19 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 876.17 | 2 | 1752.34 | 1752.34
20 | Cable tie for AB Cable | 7130320045 | No | 26.54 | 25 | 663.5 | 663.5
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 144326.1666 | 167688.2626
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 122310.3106 | 142108.6971 | NEW ROW ADDED
23 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 10824.4625 | 12576.6197 | Earlier name was - Incidental Charges @ 9%
24 | Labour Charges |  |  | 48773.0895 | 1 | 48773.0895 | 48773.0895
25 | Transport Charges |  |  | 14671.4506 | 1 | 14671.4506 | 14671.4506
26 | Labour charges for concreting |  | Cmt | 609.1748 | 1.25 | 761.4685 | 761.4685
27 | Service in lieu of Earthing Coal & Sand etc |  | No | 2765.8829 | 2 | 5531.7658 | 5531.7658
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 21, 23, 24, 25, 26, 27 |  |  |  |  | 28111.0504 | 31250.3321
29 | Total Estimated Cost excluding GST (Row 22, 23, 24, 25, 26, 27, 28) |  |  |  |  | 230983.598 | 255673.4233
30 | Applicable CGST @ 9% on Row 29 |  |  | 0.09 |  | 20788.5238 | 23010.6081
31 | Applicable SGST @ 9% on Row 29 |  |  | 0.09 |  | 20788.5238 | 23010.6081
32 | Total Estimated Cost including GST (Row 29+30+31) |  |  |  |  | 272560.6456 | 301694.6395
33 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 272561 | 301695
* | Note -- Appropriate size of termination kit and 33 kV AB XLPE Cable may be used for S.No 04 and 05 acccording to the load of HT connection.
Note on B28: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## A-8
COST SCHEDULE A-8
33 kV MEDP STRUCTURE ON PCC POLE / H-BEAM POLE (TO BE SUPPLEMENTED FOR H.T. CONNECTION)
2019-20
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg / Mtr 13.0 Mtr long H-Beam
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 4402.65 | 8805.3
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr; 13 Mtr long (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 53.8792 | 51971.857
2 | DC cross arm of 100x50 mm Channel (3.8 Mtr. Long) | 7130810608 | Set | 2 | 5601.21 | 11202.42 | 2 | 5601.21 | 11202.42
3 | 33 kV Polymer Disc Insulator | 7130820013 | No | 18 | 219.41 | 3949.38 | 18 | 219.41 | 3949.38
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 6 | 256.44 | 1538.64 | 6 | 256.44 | 1538.64
5 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 325.76 | 977.28 | 3 | 325.76 | 977.28
6 | (i) Stay set 20 mm | 7130860033 | No | 6 | 829.62 | 4977.72 | 4 | 829.62 | 3318.48
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair | 6 | 300.41 | 1802.46
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 4 | 333.29 | 1333.16
| (iv) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 51 | 71.9816 | 3671.0636 | 34 | 71.9816 | 2447.3758
7 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 96.9 | 581.4 | 6 | 96.9 | 581.4
8 | Concreting of H-Beam supports @ 0.6 Cmt per pole ; @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole (1:3:6) | 7130200202 | Cmt | 1.9 | 2970 | 5643 | 2.5 | 2970 | 7425 | Material cost including GST and labour.
9 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 2 | 118.52 | 237.04 | 2 | 118.52 | 237.04
10 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 151.45 | 75.725 | 2 | 151.45 | 302.9
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 338.4 | 169.2 | 2 | 338.4 | 676.8
12 | Barbed wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073
13 | Danger Board | 7130880041 | No | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
14 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795 | 0.5 | 71.59 | 35.795
| 16x65 mm | 7130620614 | Kg | 0.5 | 70.4 | 35.2 | 0.5 | 70.4 | 35.2
| 16x90 mm | 7130620619 | Kg |  | 70.4 |  | 2.5 | 70.4 | 176
| 16x140 mm | 7130620625 | Kg | 2 | 69.2 | 138.4 |  | 69.2
| 16x200 mm | 7130620631 | Kg | 4 | 69.2 | 276.8 | 3.5 | 69.2 | 242.2
15 | GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 2 | 876.17 | 1752.34 | 2 | 876.17 | 1752.34
16 | G.I.Bend of 40 mm dia. | 7130640171 | Each | 1 | 107.48 | 107.48 | 1 | 107.48 | 107.48
17 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3 | 3221.41 | 9664.23 | 3 | 3221.41 | 9664.23
18 | 33 kV CTPT unit of appropriate capacity |  | No
19 | Copper control cable 10 Core 2.5 Sqmm. (armoured) | 7130310660 | Mtr | 10 | 200.541 | 2005.41 | 10 | 200.541 | 2005.41
20 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 1 | 3611.89 | 3611.89 | 1 | 3611.89 | 3611.89 | Name changed
21 | Universal Meter Box for HT meters. | 7132406425 | Each | 1 | 3232.14 | 3232.14 | 1 | 3232.14 | 3232.14
22 | Test terminal Box (TTB) | 7131310037 | Each | 1 | 923.52 | 923.52 | 1 | 923.52 | 923.52
23 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 65820.441 |  |  | 108154.5451
24 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 55780.0347 |  |  | 91656.3942 | NEW ROW ADDED
25 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 4936.5331 |  | 0.075 | 8111.5909 | Earlier name was - Incidental Charges @ 9%
26 | Labour charges for concreting |  | Cmt | 1.9 | 609.1748 | 1157.4321 | 2.5 | 609.1748 | 1522.937
27 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 2 | 389.1481 | 778.2962
28 | Labour charges as per Schedule No.- AL-2 |  |  |  |  | 11109.83 |  |  | 11656.81
29 | Transport charges upto 50 Kms average lead from Area Store to construction camp including site Transport (Trans. Schedule T-1) |  |  |  |  | 5363.8658 |  |  | 5363.8658
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 23, 25, 26, 27, 28, 29 |  |  |  |  | 11145.7998 |  |  | 16851.2186
31 | Total Estimated Cost excluding GST (Row 24, 25, 26, 27, 28, 29, 30) |  |  |  |  | 90271.7917 |  |  | 135162.8164
32 | Applicable CGST @ 9% on Row 31 |  |  |  | 0.09 | 8124.4613 |  | 0.09 | 12164.6535
33 | Applicable SGST @ 9% on Row 31 |  |  |  | 0.09 | 8124.4613 |  | 0.09 | 12164.6535
34 | Total Estimated Cost including GST (Row 31+32+33) |  |  |  |  | 106520.7142 |  |  | 159492.1234
35 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 106521 |  |  | 159492
Note:- 1. This Schedule is to be supplemented with Schedule A-1 & A-3.
2. All the rates are with considering price variation clause.
Note on B37: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category A
Note on B40: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D16: Barun Chakraborty: Earlier unit was - No.

## A-9
COST SCHEDULE A-9
2019-20
SCHEDULE FOR LAST SPAN CABLING OF 33 kV LINE USING COVERED CONDUCTOR OF 70 & 99 SQ.MM SIZE
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 70 sq.mm Covered Conductor | 99 sq.mm Covered Conductor
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 53.8792 | 482.3 | 25985.9285 | 25985.9285
2 | 33 kV Covered conductor 70 sq.mm (207 Amp) (with 3% sag) | 7130310045 | Mtr. | 716.9 | 50 | 35845
3 | 33 kV Covered conductor 99 sq.mm (258 Amp) (with 3% sag) | 7130310046 | Mtr. | 815.32 | 50 |  | 40766
4 | 33 kV Polymer Disc Insulator | 7130820013 | Set | 219.41 | 3 | 658.23 | 658.23
5 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 118.52 | 1 | 118.52 | 118.52
6 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | Set | 3361.56 | 2 | 6723.12 | 6723.12
7 | Stay Set 20 mm | 7130860033 | No | 829.62 | 2 | 1659.24 | 1659.24
8 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 71.9816 | 17 | 1223.6879 | 1223.6879
9 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay (1:3:6) | 7130200202 | Cmt | 2970 | 1.25 | 3712.5 | 3712.5 | Material cost including GST and labour.
10 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 1 | 151.45 | 151.45
11 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 1 | 338.4 | 338.4
12 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 78.5018 | 2 | 157.0037 | 157.0037
13 | Danger Board | 7130880041 | No | 92.6 | 1 | 92.6 | 92.6
14 | Stay Clamp for "H" Beam | 7130810692 | Pair | 333.29 | 4 | 1333.16 | 1333.16
15 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 71.59 | 5 | 357.95 | 357.95
16 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 70.4 | 1 | 70.4 | 70.4
17 | Dead end Assembly (Suitable for all size cable) | 7130320044 | No. | 893.65 | 2 | 1787.3 | 1787.3
18 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 876.17 | 3 | 2628.51 | 2628.51
19 | Cable tie for AB Cable | 7130320045 | No | 26.54 | 25 | 663.5 | 663.5
20 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 83506.5001 | 88427.5001
21 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 70768.2204 | 74938.5594 | NEW ROW ADDED
22 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 6262.9875 | 6632.0625 | Earlier name was - Incidental Charges @ 9%
23 | Labour Charges as per labour schedule AL-9 |  |  | 7244.48 | 1 | 7244.48 | 7244.48 | New schedule added
24 | Transport Charges |  |  | 14671.4506 | 1 | 14671.4506 | 14671.4506
25 | Labour charges for concreting |  | Cmt | 609.1748 | 1.25 | 761.4685 | 761.4685
26 | Service in lieu of Earthing Coal & Sand etc |  | No | 2765.8829 | 2 | 5531.7658 | 5531.7658
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 20, 22, 23, 24, 25, 26 |  |  |  |  | 14747.3316 | 15408.5909
28 | Total Estimated Cost excluding GST (Row 21, 22, 23, 24, 25, 26, 27) |  |  |  |  | 119987.7043 | 125188.3777
29 | Applicable CGST @ 9% on Row 28 |  |  | 0.09 |  | 10798.8934 | 11266.954
30 | Applicable SGST @ 9% on Row 28 |  |  | 0.09 |  | 10798.8934 | 11266.954
31 | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 141585.4911 | 147722.2857
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 141585 | 147722
Note on B27: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on B30: Barun Chakraborty: Earlier name - Labour Charges

## A-10
COST SCHEDULE A-10
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER RAILWAY TRACK / ROAD FOR 60 MTR. LONG CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE USING OPEN TRENCH METHOD.
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD; 6 Mtr long | 7132461004 | Mtr | 1183.33 | 120 | 141999.6 | 141999.6
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 430.3 | 18 | 7745.4 | 7745.4
3 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 2030.7475 | 180 | 365534.5446
4 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2219.2291 | 190 |  | 421653.5347
5 | End terminating jointing kit upto 240 sqmm XLPE cable | 7130352037 | Set | 23743.04 | 4 | 94972.16
6 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 35218.1 | 4 |  | 140872.4
7 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1113.58 | 24 | 26725.92 | 26725.92
8 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
9 | M.S.Flat (50x6) mm | 7130600173 | kg | 46.9271 | 100 | 4692.714 | 4692.714
10 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 4 | 2224 | 2224
11 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 80 | 2640 | 2640
12 | Sand | 7132498006 | Cmt | 892.5 | 1.2 | 1071 | 1071
13 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3221.41 | 6 | 19328.46 | 19328.46
14 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 51.3096 | 18 | 923.5723 | 923.5723
15 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 275.5 | 6 | 1653 | 1653
16 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 876.17 | 10 | 8761.7 | 8761.7
17 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway / Road constructing authorities including liaisoning work etc. |  | LS | LS | LS | 25000 | 25000
18 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 709272.0709 | 811291.301
19 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 601078.0262 | 687535.0008 | NEW ROW ADDED
20 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 53195.4053 | 60846.8476 | Earlier name was - Incidental Charges @ 9%
21 | Service in lieu of Earthing Coal & Sand etc |  | No | 2765.8829 | 10 | 27658.8289 | 27658.8289
22 | Labour Charges for excavation of cable trench using open trench method as per Schedule - AL-6 |  | Mtr |  | 60 | 175053 | 179931
23 | Transportation Charges |  |  |  |  | 80692.994 | 80692.994
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 18, 20, 21, 22, 23 |  |  |  |  | 130734.0374 | 145052.6214
25 | Total Estimated Cost excluding GST (Row 19, 20, 21, 22, 23, 24) |  |  |  |  | 1068412.2917 | 1181717.2927
26 | Applicable CGST @ 9% on Row 25 |  |  | 0.09 |  | 96157.1063 | 106354.5563
27 | Applicable SGST @ 9% on Row 25 |  |  | 0.09 |  | 96157.1063 | 106354.5563
28 | Charges payable to Railway including supervision charges etc. | 15% |  |  |  | 160261.8438 | 177257.5939
29 | Total Estimated Cost including GST (Row 25+26+27+28) |  |  |  |  | 1420988.348 | 1571683.9992
30 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1420988 | 1571684
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
The rates mentioned at S.No.1, 2, 3 & 4 are applicable for 60 Mtr Corridor of Railway crossing. Estimate may be prepared based on actual length of corridor.
** | The charges to be paid for according railway permisssion shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note on B14: 89326879: Earlier name was -- End terminating jointing kit for 240 sqmm XLPE cable
Note on B27: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on E17: Barun Chakraborty: Assuming 2 kg M-seal @ Rs 450/- per kg + PVC Plate 10 mm thick
*
**

## A-11
COST SCHEDULE A-11
SCHEDULE FOR LAYING OF 1 kM 33 kV CABLE DIRECT IN GROUND SINGLE CABLE LINE USING OPEN TRENCH METHOD
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 2030.7475 | 1040 | 2111977.3688
2 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 2219.2291 | 1040 |  | 2307998.2952
3 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 120- 240 sq mm Underground XLPE cable | 7130310089 | Set | 58922.67 | 2 | 117845.34 |  | New Bin Code alloted
4 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 300- 400 sq mm Underground XLPE cable | 7130310090 | No | 65983.05 | 2 |  | 131966.1 | New Bin Code alloted
5 | End terminating jointing kit upto 240 sqmm XLPE cable | 7130352037 | Set | 23743.04 | 2 | 47486.08
6 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 35218.1 | 2 |  | 70436.2
7 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 1113.58 | 10 | 11135.8 | 11135.8
8 | G.I. Wire 8 SWG (for earthing connect to LA & cable) | 7130870043 | Kg | 65.0097 | 5 | 325.0483 | 325.0483
9 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 20 | 11120 | 11120
10 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 4000 | 132000 | 132000
11 | River Sand (For 10 cm. base & 10 cm. filling of trench above cable & then cable covering tiles over complete length of trench) | 7132498006 | Cmt | 892.5 | 150 | 133875 | 133875
12 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3221.41 | 6 | 19328.46 | 19328.46
13 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 51.3096 | 18 | 923.5723 | 923.5723
14 | Aluminium T-clamp suitable for Dog / Raccoon conductor for connecting L.A. | 7130830585 | No. | 275.5 | 6 | 1653 | 1653
15 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. | 7130642039 | No | 876.17 | 2 | 1752.34 | 1752.34
16 | M.S. Nuts & Bolts | Fill the appropriate Bin Code | Kg | 72.78 | 3 | 218.34 | 218.34
17 | Bhatta brick | 7132498054 | No | 6.09 | 4400 | 26796 | 26796 | New Bin Code alloted
18 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Road constructing authorities including liaisoning work etc. [ To be provisioned as per actual requirement ] |  | LS | LS | LS | 25000 | 25000
19 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 2641436.3494 | 2874528.1558
20 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 2238505.3808 | 2436040.81 | NEW ROW ADDED
21 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 198107.7262 | 215589.6117 | Earlier name was - Incidental Charges @ 9%
22 | Service in lieu of Earthing Coal & Sand etc |  | No | 2765.8822 | 10 | 27658.8217 | 27658.8217
23 | Labour Charges - |  |  |  |  | 833431.7 | 833431.7
i | Cable trench excavation [(1.0 Mx0.75 Mx1.5 M) LxWxD] |  | Cmt | 251.76 | 1125 | 283230 | 283230
ii | Spreading of sand for base pad of cable (10 cm thick & 10 cm. above cable) |  | Mtr | 14.11 | 1000 | 14110 | 14110
iii | Laying of XLPE Cable in open trench & rising on pole through GI pipe & back filling of cable trench with excavated soil |  | Mtr | 487.8 | 1040 | 507312 | 507312
iv | Laying of GI pipe |  | Mtr | 69.89 | 10 | 698.9 | 698.9
v | Fixing of rising pipe with clamps |  | Mtr | 390.24 | 10 | 3902.4 | 3902.4
vi | Fixing of 33 kV lightning arrestor including earthing, jumpering and fixing of aluminium clamp |  | Set | 610.42 | 2 | 1220.84 | 1220.84
vii | Providing earthing (earthing pit digging and laying of earthing pipe complete) |  | Set | 1063.58 | 2 | 2127.16 | 2127.16
viii | Covering of cable with tiles |  | Mtr | 3.88 | 1000 | 3880 | 3880
ix | Making of Straight jointing of XLPE Cable |  | Set | 4591.62 | 2 | 9183.24 | 9183.24
x | Making of End jointing of XLPE Cable |  | Set | 3883.58 | 2 | 7767.16 | 7767.16
24 | Transportation Charges |  |  |  |  | 80692.994 | 80692.994
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 19, 21, 22, 23, 24 |  |  |  |  | 472665.9489 | 503987.6604
26 | Total Estimated Cost excluding GST (Row 20, 21, 22, 23, 24, 25) |  |  |  |  | 3851062.5716 | 4097401.5977
27 | Applicable CGST @ 9% on Row 26 |  |  | 0.09 |  | 346595.6314 | 368766.1438
28 | Applicable SGST @ 9% on Row 26 |  |  | 0.09 |  | 346595.6314 | 368766.1438
29 | Charges payable to Nagar Nigam / Nagar Palika / Nagar Panchayat / Gram Panchayat including supervision charges etc.
30 | Total Estimated Cost including GST (Row 26+27+28+29) |  |  |  |  | 4544253.8345 | 4834933.8853
31 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 4544254 | 4834934
(a) | Cable and accessories size can be replaced as per actual requirement
(b) | When multiple cables have to be laid in the common trench, the following excavation is to be followed-- (i) 1.0 Mtr width x 1.5 Mtr depth for laying of 02 cables; (ii) 1.25 Mtr width x 1.5 Mtr depth for laying of 03 cables; (iii) 1.5 Mtr width x 1.5 Mtr depth for laying of 04 cables and so on.
(c) | Between two cables, fly ash brick is to be provided as separator
(d) | All other items are to be changed as per size of trench and number of cables in a trench.
ACTIVITY OF Col. 21 (xi) INCLUDED in (vi)
xi | Jumpering of Lightning arrestor and fixing of aluminium clamps |  | Set | 291.28 | 2 | 582.56 | 582.56
Note on B28: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on E33: 89326879: As per AL-6
Note on E34: 89326879: As per AL-6
Note on E35: 89326879: As per AL-6
Note on E36: 89326879: As per AL-6
Note on E37: 89326879: As per AL-6
Note on E38: 89326879: As per AL-6 -- Total of S.No. 10 & 11
Note on E39: 89326879: As per AL-6
Note on E40: 89326879: As per AL-6
Note on E41: Barun Chakraborty: Refer to Sch. CL-10, S.No. 3
Note on E42: Barun Chakraborty: Refer to Sch. CL-10, S.No. 4

## B-1
COST SCHEDULE B -1
SCHEDULE FOR 33/11 kV, 3.15 MVA, 1.6 MVA SUB-STATION WITH TWO BAYS FOR OUTGOING FEEDERS AND 5 MVA SUB-STATION WITH THREE BAYS FOR OUTGOING FEEDERS AT NEW SITE
2019-20
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Proposed 33/11 kV S/s expandable to 2x1.6 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x3.15 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x5 MVA with control room
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 |  | LAND AND CIVIL WORKS (Rate as per SoR PWD)
| i | Construction of 1.5 Mtr high barbed wire fencing in angle iron post as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Mtr | 406 | 400 | 162400 | 400 | 162400 | 400 | 162400
| ii | Drilling of 150 mm dia bore well (upto 100 Mtr depth) with 1.5 HP Submersible motor pump and water supply line for switch yard including all taxes, T&P, materials, labours, transportation etc complete. |  | Job | 170146 | 1 | 170146 | 1 | 170146 | 1 | 170146
| iii | Construction of A1 type Control Room with toilet as per Drg. No. 04-01/AR/24-R2 date 13.06.2007 including all taxes royalty, T&P, materials, labours, transportation etc. complete. |  | Job | 906710 | 1 | 906710 | 1 | 906710 | 1 | 906710
| iv (a) | Construction of 2.4 Mtr high Chain link wire mesh fencing on Hard Soil or Hard Moorum as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | M | 2494 | 125 | 311750 | 125 | 311750 | 125 | 311750
| iv (b) | Construction of 2.4 Mtr high Chain link wire mesh fencing on Black Cotton Soil as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | M | 2860 | 125 | 357500 | 125 | 357500 | 125 | 357500
| v | Construction of 4.50 m x 2.15 m size yard / area gate as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Each | 35276 | 2 | 70552 | 2 | 70552 | 2 | 70552
| vi | Providing and filling in plinth with sand / crusher dust and hard moorum under floor in layers not exceeding 20 cm in depth consolidating each deposited layer by ramming and watering with a lead upto 50 M and lift upto 1.5 M. (Moorum measured in stacks will be reduced by 16% for voids). |  | Cmt | 371 | 300 | 111300 | 300 | 111300 | 300 | 111300 | NAME CHANGED
| vii | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete (Metal measured in stacks will be reduced by 8% for voids). |  | Cu. M | 1140 | 180 | 205200 | 180 | 205200 | 180 | 205200 | NAME CHANGED
| viii (a) | Construction of 4.0 Mtr wide Cement Concrete Road on hard soil or hard moorum as per given drawing including cost of mixture machine, vibrator, curing all materials, T&P, labour, transportation, loading, unloading, royalty taxes etc. complete. |  | Mtr | 4328 | 120 | 519360 | 120 | 519360 | 120 | 519360
| viii (b) | Construction of 4.0 Mtr wide Cement Concrete Road on black cotton soil as per given drawing including cost of mixture machine, vibrator, curing all materials, T&P, labour, transportation, loading, unloading, royalty taxes etc. complete. |  | Mtr | 4845 | 120 | 581400 | 120 | 581400 | 120 | 581400
| ix | Construction of 7.50 M long 600 mm internal dia. NP-3 Hume pipe culvert as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty taxes etc. complete. |  | No. | 33635 | 1 | 33635 | 1 | 33635 | 1 | 33635
| x | Construction of 1.0 M high (from G.L.) brick masonary retaining wall as per given drawing including all labour, material, T&P, curing, transportation, loading, unloading, royalty taxes etc. complete. |  | RM | 3952 | 130 | 513760 | 130 | 513760 | 130 | 513760 | Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
| xi | Providing filling and compacting local earth (from approved source pit) in layers not exceeding 20 cm in depth consolidating each deposited layer by ramming and watering, including dressing etc. complete |  | Cu. M | 242 | 600 | 145200 | 600 | 145200 | 600 | 145200 | NEW ROW ADDED
| xii | Sub total-1 | 7: 3150013; 9: 3150013; 11: 3150013
2 |  | EQUIPMENTS
| i | 33/11 kV transformer 1.60 MVA | 7132220091 | No | 805738.17 | 1 | 805738.17 | -- | -- | -- | --
|  | 33/11 kV transformer 3.15 MVA | 7132220095 | No | 2393149.15 | -- |  | 1 | 2393149.15 | -- | --
|  | 33/11 kV transformer 5.00 MVA | 7132220097 | No | 3379006.13 | -- |  | -- |  | 1 | 3379006.13
| ii | 33 kV VCB (With CT's & panel) | 4: No; 5: 343410.11; 6: --; 8: 1
|  | (i) 33 kV VCB (Without CT's & Panel) | 7131943380 | No | 244236.87 | -- |  | 1 | 244236.87 | 1 | 244236.87
|  | (ii) 33 kV Control Panel | 7131960524 | No | 40103.54 | -- |  | 1 | 40103.54 | 1 | 40103.54
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 19689.9 | -- |  | 3 | 59069.7 | 3 | 59069.7
| iii | 11 kV VCB for X'mer protection (With CTs & panel) | 4: No; 5: 199948.36; 6: 1; 8: 1; 10: 1
|  | (i) 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 119502.62 | 1 | 119502.62 | 1 | 119502.62 | 1 | 119502.62
|  | (ii) 11 kV Control Panel for Transformer Protection | 7131960522 | Each | 40103.54 | 1 | 40103.54 | 1 | 40103.54 | 1 | 40103.54
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | No | 13447.4 | 3 | 40342.2 | 3 | 40342.2 | 3 | 40342.2
| iv | 11 kV VCB for feeder protection with CTs & panel. | 4: No; 5: 374819.96; 6: 2; 8: 2; 10: 3
|  | (i) 11 kV VCB with Relay & Control Panel | 7131960497 | No | 146280.49 | 2 | 292560.98 | 2 | 292560.98 | 3 | 438841.47 | 7131941762+7131960008=7131960497
|  | (ii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 13709.83 | 6 | 82258.98 | 6 | 82258.98 | 9 | 123388.47
| v | 33 kV Isolator (600 A.) Set without earth switch | 7131930752 | No | 40401.22 | 2 | 80802.44 | 2 | 80802.44 | 2 | 80802.44
| vi | 11 kV Isolator (600 A.) (including 2 Nos. for capacitor bank) Set | 7131930663 | No | 23345.09 | 6 | 140070.54 | 6 | 140070.54 | 8 | 186760.72
| vii | 33 kV DO Fuse unit | 7131930415 | Each | 2886.87 | 3 | 8660.61 | 3 | 8660.61 | 9 | 25981.83
| viii | 11 kV DO Fuse unit | 7131930412 | Each | 1177.88 | 3 | 3533.64 | 3 | 3533.64 | 6 | 7067.28
| ix | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 3221.41 | 3 | 9664.23 | 3 | 9664.23 | 3 | 9664.23
| x | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 328.57 | 12 | 3942.84 | 12 | 3942.84 | 15 | 4928.55
| xi | 33 kV AB Switch | 7131930321 | Each | 18863.48 | 1 | 18863.48 | 1 | 18863.48 | 1 | 18863.48
| xii | 11 kV AB Switch | 7131930221 | Each | 8496 | 3 | 25488 | 3 | 25488 | 4 | 33984
| xiii | Single phase 33 kV PT | 7132230057 | Each | 16566.35 | 3 | 49699.05 | 3 | 49699.05 | 3 | 49699.05
| xiv | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 83038.2 | 1 | 83038.2 | 1 | 83038.2 | 1 | 83038.2
| xv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 37649.28 | 2 | 75298.56 | 2 | 75298.56 | 3 | 112947.84
| xvi | Single phase 11 kV PT's | 7132230056 | Each | 10323.86 | 3 | 30971.58 | 3 | 30971.58 | 3 | 30971.58
| xvii | LT Meter (CT Operated) 100/5 A with CT's | 4: No; 5: 2873.24; 6: 1; 8: 1; 10: 1
|  | (i) LT Meter (CT Operated) 100/5 A | 7131310997 | No | 1805 | 1 | 1805 | 1 | 1805 | 1 | 1805
|  | (ii) LT CT 100/5 A | 7132230016 | No | 356.08 | 3 | 1068.24 | 3 | 1068.24 | 3 | 1068.24
| xviii | H.T. STATIC TRIVECTOR METERS | 4: No; 5: 10835.67; 6: 3; 8: 3; 10: 4
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 3611.89 | 3 | 10835.67 | 3 | 10835.67 | 4 | 14447.56
| xix | Lead Acid Battery with automatic charger | 4: No; 5: 66160.15; 6: 1; 8: 1; 10: 1
|  | (i) Battery | 7132404366 | No | 55627.8 | 1 | 55627.8 | 1 | 55627.8 | 1 | 55627.8
| 1 | (ii) Battery Charger | 7132468558 | No | 10532.35 | 1 | 10532.35 | 1 | 10532.35 | 1 | 10532.35
| xx | 33/0.4 kV station transformer (50 kVA) | 7132210215 | Each | 136597.53 | 0 | 0 | 0 | 0 | 2 | 273195.06
| xxi | Energy efficient 11/0.4 kV station transformer (100 kVA) [LEVEL-2] * | 7132210020 | Each | 129355.28 | 1 | 129355.28 | 1 | 129355.28
| xxii | LT Distribution box for 63 kVA X'mer | 7131950065 | Each | 15779.98 | 0 | 0 | 0 | 0 | 2 | 31559.96
| xxiii | LT Distribution box for 100 kVA X'mer | 7131950105 | Each | 19725.8 | 1 | 19725.8 | 1 | 19725.8
| xxiv | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 6 Nos = 2448.6 Kgs | 7130601958 | Kg | 53.8792 | 2448.6 | 131928.5601 | 2448.6 | 131928.5601 | 2448.6 | 131928.5601
| xxv | Control cable
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr. | 129.5439 | 360 | 46635.8148 | 360 | 46635.8148 | 480 | 62181.0864
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr. | 68.1431 | 360 | 24531.5016 | 360 | 24531.5016 | 510 | 34752.9606
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr. | 39.1091 | 180 | 7039.6326 | 240 | 9386.1768 | 300 | 11732.721
| xxvi | Tee Clamp for Dog Conductor | 7130830585 | No | 275.5 | 96 | 26448 | 96 | 26448 | 108 | 29754
| xxvii | Danger Board for 33 kV & 11 kV equipment / supply pole | 7130880041 | No | 92.6 | 10 | 926 | 10 | 926 | 10 | 926
| xxviii | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 52.2909 | 300 | 15687.273 | 300 | 15687.273 | 300 | 15687.273
| xxix | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3133.19 | 5 | 15665.95 | 5 | 15665.95 | 6 | 18799.14
| xxx | Sub-total - 2 | 7: 2408352.5321; 9: 4341520.1663; 11: 5823301.4511
3 |  | STRUCTURE AND BUS BAR ARRANGEMENTS: -
| i | 8 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x8 mtr =296.8 kg/pole x 10 Nos = 2968 Kgs. | 7130601958 | Kg | 53.8792 | 2968 | 159913.4062 | 2968 | 159913.4062 | 3561.6 | 191896.0875
| ii | 7 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x7mtr = 259.7 Kg/pole x 4 Nos = 1038.8 Kgs. | 7130601958 | Kg | 53.8792 | 1038.8 | 55969.6922 | 1038.8 | 55969.6922 | 1038.8 | 55969.6922
| iii | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 8 Nos = 3264.8 Kgs | 7130601958 | Kg | 53.8792 | 3264.8 | 175904.7469 | 3264.8 | 175904.7469 | 4081 | 219880.9336
| iv | MS DC Cross arm (100 x 50 x 6 mm Channel) 5.2 Mtr long Set | 7130810684 | No | 8809.64 | 22 | 193812.08 | 22 | 193812.08 | 28 | 246669.92
| v | MS DC Cross arm (100 x 50 x 6 mm Channel) 3.8 Mtr long Set | 7130810006 | Set | 7091.89 | 2 | 14183.78 | 2 | 14183.78 | 9 | 63827.01
| vi | MS DC Cross arm (100 x 50 x 6 mm Channel) 2.7 Mtr long Set | 7130810608 | Set | 5601.21 | 9 | 50410.89 | 9 | 50410.89 | 11 | 61613.31
| vii | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1730.26 | 1 | 1730.26 | 1 | 1730.26 | 2 | 3460.52
| viii | R.S. Joist (175x85 mm) | 7130600675 | Kg | 44.9155 | 468 | 21020.4634 | 468 | 21020.4634 | 546 | 24523.8739
| ix | ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr | 67.4322 | 500 | 33716.12 | 500 | 33716.12 | 600 | 40459.344
| x | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 325.76 | 6 | 1954.56 | 6 | 1954.56 | 9 | 2931.84
| xi | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 132.09 | 9 | 1188.81 | 12 | 1585.08 | 12 | 1585.08
| xii | Polymer Disc Insulator for 33 kV Side | 7130820013 | Each | 219.41 | 81 | 17772.21 | 81 | 17772.21 | 81 | 17772.21
| xiii | 33 kV Strain Hardware fitting | 7130820248 | Each | 256.44 | 81 | 20771.64 | 81 | 20771.64 | 102 | 26156.88
| xiv | Polymer Disc insulator for 11 kV side (double disc) | 7130820010 | Each | 119.1 | 108 | 12862.8 | 108 | 12862.8 | 150 | 17865
| xv | 33 kV Strain Plate 8 mm thick | 7130810624 | Each | 96.9 | 198 | 19186.2 | 198 | 19186.2 | 246 | 23837.4
| xvi | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 40 | 6058 | 40 | 6058 | 45 | 6815.25
| xvii | Aluminium Paint | 7130210809 | Ltr | 338.4 | 40 | 13536 | 40 | 13536 | 45 | 15228
| xviii | Sub-total - 3 | 7: 799991.6586; 9: 800387.9286; 11: 1020492.3512
4 |  | OTHER MISCELLANEOUS ITEMS: -
| i | Concreting of structures & foundation (1:3:6) | 7130200202 | Cmt | 2970 | 51.6 | 153252 | 60.6 | 179982 | 67.2 | 199584 | Material cost including GST and labour.
| ii | PVC insulated Single Core 70 Sqmm Armoured cable. | 7130311010 | Mtr. | 51.4677 | 10 | 514.6772 | 10 | 514.6772 | 10 | 514.6772
| iii | 16 Sqmm 4-core Cable for Switch yard lighting, tripping arrangement & system control (armoured) | 7130311084 | Mtr. | 60.69 | 300 | 18207.012 | 300 | 18207.012 | 300 | 18207.012
| iv | 18 W LED Street Light complete set | 7131210030 | Set | 2336.88 | 4 | 9347.52 | 4 | 9347.52 | 4 | 9347.52
| v | 70 W LED Street Light complete set | 7131210032 | Set | 4270.41 | 6 | 25622.46 | 6 | 25622.46 | 6 | 25622.46
| vi | AC Distribution board for AC/DC Supply | 7131920028 | No | 11255.65 | 1 | 11255.65 | 1 | 11255.65 | 1 | 11255.65
| vii | Fixing of 33/11 kV S/S (Name Plate) Board made up of 2 mm thick MS Sheet of size 5'x8' as per approved drawing. | 7132406800 | Job | 9713.03 | 1 | 9713.03 | 1 | 9713.03 | 1 | 9713.03
| viii | Earthing of Sub-station including Distribution Transformer earthing. | bar: 4; 6; 8; 10
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4453.22 | 21 | 93517.62 | 21 | 93517.62 | 21 | 93517.62
|  | (ii) GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 876.17 | 40 | 35046.8 | 40 | 35046.8 | 40 | 35046.8
|  | (iii) MS flat 50x6 mm size (2.5 kg per meter) | 7130600173 | Kg | 46.9271 | 1000 | 46927.14 | 1000 | 46927.14 | 1000 | 46927.14
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 65.0097 | 31 | 2015.2995 | 31 | 2015.2995 | 31 | 2015.2995
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 99.03 | 25 | 2475.75 | 25 | 2475.75 | 25 | 2475.75
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 99.03 | 10 | 990.3 | 10 | 990.3 | 10 | 990.3
|  | (vii) GI Spring washers | 7130622922 | Kg | 153.83 | 5 | 769.15 | 5 | 769.15 | 5 | 769.15
|  | MS Nuts & Bolts | 4: Kg; 6: 186; 8: 270; 10: 270
|  | (i) MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 71.59 | 10 | 715.9 | 15 | 1073.85 | 15 | 1073.85
|  | (ii) MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 70.4 | 5 | 352 | 10 | 704 | 10 | 704
|  | (iii) MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 70.4 | 15 | 1056 | 25 | 1760 | 25 | 1760
|  | (iv) MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 69.2 | 66 | 4567.2 | 85 | 5882 | 85 | 5882
|  | (v) MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 69.2 | 80 | 5536 | 110 | 7612 | 110 | 7612
|  | (vi) MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 69.2 | 10 | 692 | 25 | 1730 | 25 | 1730
| ix | Furniture
|  | (i) Table 4'x2.5' |  | No | 4982.9 | 1 | 4982.9 | 1 | 4982.9 | 1 | 4982.9
|  | (ii) Chair | 7132409830 | No | 3776 | 2 | 7552 | 2 | 7552 | 2 | 7552
|  | (iii) Small Steel Almirah 50'' | 7132401672 | No | 10030 | 1 | 10030 | 1 | 10030 | 1 | 10030
| x | Fire fighting equipments | bar: 4
|  | (i) Fire fighting equipments (dry chemical powder type 5 Kg capacity) | 7132490006 | No | 5357.02 | 2 | 10714.04 | 2 | 10714.04 | 2 | 10714.04
|  | (ii) Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | 7132421002 | No | 5990.38 | 2 | 11980.76 | 2 | 11980.76 | 2 | 11980.76
| xi | Electrically insulated 11 kV mats infront of electrical control panel | 7132448003 | No | 4769.91 | 3 | 14309.73 | 3 | 14309.73 | 3 | 14309.73
| xii | Sub-total - 4 | 7: 482142.9387; 9: 514715.6887; 11: 534317.6887
5 |  | Total material cost including Civil works & GST both | 7: 6840500.1295; 9: 8806636.7837; 11: 10528124.491
6 |  | Total material cost including Civil works but excluding GST (Row 5 / 1.18) | 7: 5797034.008; 9: 7463251.5116; 11: 8922139.3991 | NEW ROW ADDED
7 |  | Incidental Charges @ 7.5 % on " Row-5 " above (Row 5 * 0.075) | 5: 0.075; 7: 513037.5097; 9: 660497.7588; 11: 789609.3368 | Earlier name was - Incidental Charges @ 9%
8 | (i) | Services on S/s earthing |  | No | 27670.3866 | 1 | 27670.3866 | 1 | 27670.3866 | 1 | 27670.3866
| (ii) | Services on Cable trench (separate trench for power cable & control cable). |  | RM | 2151.893 | 70 | 150632.51 | 70 | 150632.51 | 80 | 172151.44 | Based on calculations provided by SE(Civil) in SoR 2017-18 for Construction of brick masonry cable trench with cover @ Rs 21518.93 for 10 Mtr length
| (iii) | Services on Painting of structures |  | No | 17809.6618 | 1 | 17809.6618 | 1 | 17809.6618 | 1 | 17809.6618
| (iv) | Services on Labelling of equipments |  | No | 14841.3848 | 1 | 14841.3848 | 1 | 14841.3848 | 1 | 14841.3848
9 |  | Labour charges as per sch. (BL-1+BL-3) | 7: 223822.37; 9: 238075.29; 11: 271577.79
10 |  | Labour charges for concreting |  | Cmt | 609.1748 | 51.6 | 31433.4194 | 60.6 | 36915.9925 | 67.2 | 40936.5462
11 |  | Transport charges | 7: 38345.3115; 9: 38345.3115; 11: 42605.8971
12 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 5, 7, 8 [(i), (ii), (iii), (iv)], 9, 10, 11, | 7: 982261.5854; 9: 1248928.135; 11: 1488165.8668
13 |  | Total estimated cost of Sub-station (Including Civil works but excluding GST) [Row = 6, 7, 8 [(i), (ii), (iii), (iv)], 9, 10, 11, 12, | 7: 7796888.1473; 9: 9896967.9427; 11: 11787507.7093
14 |  | Total Cost (Rs In lakhs) | 7: 77.9689; 9: 98.9697; 11: 117.8751
15 |  | Applicable CGST @ 9% on Row 13 | 5: 0.09; 7: 701719.9333; 9: 890727.1148; 11: 1060875.6938
16 |  | Applicable SGST @ 9% on Row 13 | 5: 0.09; 7: 701719.9333; 9: 890727.1148; 11: 1060875.6938
17 |  | Grand Total estimated cost of S/s including GST (Row 13+15+16). | 7: 9200328.0139; 9: 11678422.1724; 11: 13909259.097
18 |  | Grand Total estimated cost including GST (Rounded off) | 7: 9200328; 9: 11678422; 11: 13909259
19 |  | Grand Total cost (Rs in LAKHS) | 7: 92.0033; 9: 116.7842; 11: 139.0926
Note:
| (1) | All the rates are with considering price variation clause.
| (2) | In case of non-availability of H-Beam for structure double welded RS Joist may be used (1) 8 meter long double welded RS Joist and cost of it shall be taken in place of cost of item No.3 (i) unit rate as Rs 10640.00 & quantity should be 10 Nos for 3.15 & 1.6 MVA and 12 Nos for 5 MVA (2) 7 meter long double welded RS Joist and cost of it shall be taken as in place of cost of item No.3 (ii) unit rate as Rs 9372.00 & quantity should be 04 Nos each for 3.15 & 1.6 MVA and 5 MVA
| (3) | The cost of land is not taken in to account since normally CSPDCL acquires Govt. land at negligible cost. How ever needs to be procure other than Govt. land then should be added actual cost.
| * | ISI Marked Energy Efficiency level-2 transformer
[7 empty] | 6840500.13 |  | 8806636.79 |  | 10528124.49
Note on C18: 89326879: Earlier name was - Supply and filling of good quality hard moorum including stacking at site and spreading in layers of 150 mm thickness including watering and ramming including all leads & lifts, labour, T&P, transportation, loading unloading, royalty, taxes etc. complete (Moorum measured in stacks will be reduced by 16% for voids).
Note on C19: 89326879: Earlier name was - Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete and including spreading in 100 mm thick layers complete (Metal measured in stacks will be reduced by 8% for voids).
Note on C57: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category A
Note on C59: Author: Earlier name was - Battery (Low Maintenance SAN container)
Note on C126: Barun Chakraborty: Earlier name was - Total including Civil works
Note on C137: Barun Chakraborty: Earlier name was - Total cost of Sub-station (Including Civil works)
Note on D98: Barun Chakraborty: NEW BIN CODE ALLOTED
Note on D99: Barun Chakraborty: NEW BIN CODE ALLOTED
Note on E22: 89326879: Earlier unit was - Each
Note on E130: 89326879: Earlier unit taken as Mtr
Note on H25: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
Note on J25: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.
Note on L25: 89326879: Please select appropriate row for S.No. 1 [(iv-a) or (iv-b) & (viii-a) or (viii-b)] according to actual field condition as per type of soil.

## B-2
COST SCHEDULE B-2
2019-20
( 33 kV SUB-STATION )
POWER TRANSFORMERS
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | 1600 kVA | 3150 kVA | 5000 kVA
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Cost of Transformer as per Schedule of rates
| Power Transformer 1600 kVA | 7132220091 | No | 805738.17 | 1 | 805738.17
| Power Transformer 3150 kVA | 7132220095 | No | 2393149.15 | 1 |  | 2393149.15
| Power Transformer 5000 kVA | 7132220097 | No | 3379006.13 | 1 |  |  | 3379006.13
2 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 805738.17 | 2393149.15 | 3379006.13
3 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 682828.9576 | 2028092.5 | 2863564.5169 | NEW ROW ADDED
4 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 60430.3628 | 179486.1862 | 253425.4598 | Earlier name was - Incidental Charges @ 9%
5 | Services for Painting |  |  |  |  | 5843.0649 | 9348.9038 | 9348.9038
6 | Labour charges as per Schedule BL-3 |  |  |  |  | 62048.37 | 73754.29 | 85851.79
7 | Transport charges upto 50 Km average lead from Area Store to construction camp including site transport (Transport Sch T-2) |  |  |  |  | 3967.2483 | 11435.424 | 17839.7321
8 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 2, 4, 5, 6, 7 |  |  |  |  | 117253.402 | 333396.7443 | 468184.002
9 | Total Estimated Cost excluding GST (Row 3, 4, 5, 6, 7, 8) |  |  |  |  | 932371.4055 | 2635514.0484 | 3698214.4046
10 | Applicable CGST @ 9% on Row 9 |  |  | 0.09 |  | 83913.4265 | 237196.2644 | 332839.2964
11 | Applicable SGST @ 9% on Row 9 |  |  | 0.09 |  | 83913.4265 | 237196.2644 | 332839.2964
12 | Total Estimated Cost including GST (Row 9+10+11) |  |  |  |  | 1100198.2585 | 3109906.5771 | 4363892.9974
13 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1100198 | 3109907 | 4363893
Note: | All the rates are with considering price variation clause.
Note on B14: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## B-3
COST SCHEDULE B-3
|  |  | ( 33 kV SUB-STATIONS ) |  |  |  |  | 2019-20
SCHEDULE FOR INSTALLATION OF ADDITIONAL TRANSFORMER FOR PARALLEL OPERATION WITH TWO ADDITIONAL BAY ON 11 kV SIDE
S. No. | S.No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | Sub-station capacity |  |  | Reason
[7 empty] | 1.6 MVA | 3.15 MVA | 5.0 MVA
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 |  | EQUIPMENTS
| i | Power Transformer 33/11 kV
|  | Power Transformer 1.6 MVA | 7132220091 | No | 805738.17 | 1 | 805738.17
|  | Power Transformer 3.15 MVA | 7132220095 | No | 2393149.15 | 1 |  | 2393149.15
|  | Power Transformer 5 MVA | 7132220097 | No | 3379006.13 | 1 |  |  | 3379006.13
| ii | 33 kV VCB with CT's and panels. |  | No | 343410.11
|  | (i) 33 kV VCB ( without CT's and panels) | 7131943380 | No | 244236.87 | 1 |  | 244236.87 | 244236.87
|  | (ii) 33 kV Control Panel | 7131960524 | No | 40103.54 | 1 |  | 40103.54 | 40103.54
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 19689.9 | 3 |  | 59069.7 | 59069.7
| iii | 11 kV VCB for X'mer protection with CT's and panels. |  | No | 199948.36 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | Each | 119502.62 | 1 | 119502.62 | 119502.62 | 119502.62
|  | (ii) 11 kV Control Panel for X-mer Protection | 7131960522 | Each | 40103.54 | 1 | 40103.54 | 40103.54 | 40103.54
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | Each | 13447.4 | 3 | 40342.2 | 40342.2 | 40342.2
| iv | 11 kV VCB for feeder protection with CT's and panels. |  | No | 374819.96 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | No | 119502.62 | 2 | 239005.24 | 239005.24 | 239005.24
|  | (ii) 11 kV Control Panel for feeder protection | 7131960008 | Each | 26777.87 | 2 | 53555.74 | 53555.74 | 53555.74
|  | (iii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 13709.83 | 6 | 82258.98 | 82258.98 | 82258.98
| v | 33 kV DO Fuse Unit | 7131930415 | Each | 2886.87 | 3 | 8660.61
| vi | 33 kV isolator, 600 A. Without earth switch | 7131930752 | No | 40401.22 | 3 | 121203.66 | 121203.66 | 121203.66
| vii | 11 kV isolator, 600 A | 7131930663 | No | 23345.09 | 5 | 116725.45 | 116725.45 | 116725.45
| viii | 33 kV Polymer Lightning Arrestor | 7130840021 | Each | 3221.41 | 3 | 9664.23 | 9664.23 | 9664.23
| ix | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 328.57 | 9 | 2957.13 | 2957.13 | 2957.13
| x | H.T. STATIC TRIVECTOR METERS |  | No | 10835.67
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 3611.89 | 3 | 10835.67 | 10835.67 | 10835.67
| xi | 33 kV Single Phase PT | 7132230057 | Each | 16566.35 | 3 | 49699.05 | 49699.05 | 49699.05
| xii | 11 kV Single Phase PT | 7132230056 | Each | 10323.86 | 3 | 30971.58 | 30971.58 | 30971.58
| xiii | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 83038.2 | 1 | 83038.2 | 83038.2 | 83038.2
| xiv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 37649.28 | 2 | 75298.56 | 75298.56 | 75298.56
| xv | 33 kV AB switch | 7131930321 | Each | 18863.48 | 0 | 0 | 0 | 0
| xvi | 11 kV AB switch | 7131930221 | Each | 8496 | 2 | 16992 | 16992 | 16992
| xvii | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3133.19 | 5 | 15665.95 | 15665.95 | 15665.95
2 |  | STRUCTURE AND BUS BAR ARRANGEMENT
| (i) | DO fuse supporting structure set on 7 Mtr long H- Beam 37.1 kg/mtr 33 kV & 11 kV side (2 No. each side) i.e. 37.1 kg x 7 = 259.7 kg/pole x 4 Nos = 1038.8 Kgs | 7130601958 | Kg | 53.8792 | 1038.8 | 55969.6922 | 55969.6922 | 55969.6922
| (ii) | 33 kV additional bay ( 02 No H-Beam 152x152 mm 08 mtr long) with 6 Nos, 5.2 Mtr channel |  | Set | 134442.4825 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.20 Kgs | 7130601958 | Kg | 53.8792 | 1187.2 | 63965.3625 | 63965.3625 | 63965.3625
|  | (ii) D.C.Cross arm Channel 5.2 mtr 100x50 mm | 7130810684 | No | 8809.64 | 8 | 70477.12 | 70477.12 | 70477.12
| (iii) | 11 kV, 2 Addl. bus bar structure 08 mtr long H- Beam 37.1 Kg/mtr with 4 Nos, 5.2 Mtr long DC cross arm (100 x 50 mm) |  | Set | 413090.3029 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.2 Kgs. | 7130601958 | Kg | 53.8792 | 1187.2 | 63965.3625 | 63965.3625 | 63965.3625
|  | (ii) H-Beam 152x152 mm 11 mtr long 37.1 kg/mtr i.e.= 408.1 kg/pole x 4 No = 1632.40 Kgs | 7130601958 | Kg | 53.8792 | 1632.4 | 87952.3734 | 87952.3734 | 87952.3734
|  | (iii) R.S. Joist (175x85 mm) [ 8x2 Mtr ] | 7130600675 | Kg | 44.9155 | 273 | 12261.937 | 12261.937 | 12261.937
|  | (iv) D.C.Cross arm Channel 5.2 mtr 100x50 mm (set) | 7130810684 | No | 8809.64 | 24 | 211431.36 | 211431.36 | 211431.36
|  | (v) D.C.Cross arm 5 ft. Centre 100x50 mm Channel | 7130810608 | Set | 5601.21 | 5 | 28006.05 | 28006.05 | 28006.05
|  | (vi) D.C.Cross arm 8 ft. Centre 100x50 mm Channel | 7130810517 | Set | 4736.61 | 2 | 9473.22 | 9473.22 | 9473.22
| (iv) | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 52.2909 | 300 | 15687.273 | 15687.273 | 15687.273
| (v) | ACSR Dog conductor | 7130830063 | Mtr | 67.4322 | 300 | 20229.672 | 20229.672 | 20229.672
| (vi) | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 325.76 | 3 | 977.28 | 977.28 | 977.28
| (vii) | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 132.09 | 6 | 792.54 | 792.54 | 792.54
| (viii) | Strain hardware with strain set suitable for Dog conductor: -
|  | (a) 33 kV side with 3 disc insulator per phase. |  | Set | 34261.2 | 18
|  | (i) 33 kV Polymer Disc insulator . | 7130820013 | No | 219.41 | 72 | 15797.52 | 15797.52 | 15797.52
|  | (ii) 33 kV Strain Hardware | 7130820248 | Each | 256.44 | 72 | 18463.68 | 18463.68 | 18463.68
|  | (b) 11 kV side with 2 disc insulator per phase. |  | Set | 9887.16
|  | (i) 11 kV Polymer Disc insulator | 7130820010 | No | 119.1 | 12 | 1429.2 | 1429.2 | 1429.2
|  | (ii) 11 kV Hardware | 7130820241 | No | 123.43 | 12 | 1481.16 | 1481.16 | 1481.16
|  | (iii) Strain plate 8 mm thick | 7130810624 | No | 96.9 | 72 | 6976.8 | 6976.8 | 6976.8
| (ix) | T-clamp for jumper connection with AB Switches & DO fuses / Isolator. | 7130830585 | No | 275.5 | 96 | 26448 | 26448 | 26448
| (x) | Stay Clamp for "H" Beam | 7130810692 | Pair | 333.29 | 42 | 13998.18 | 13998.18 | 13998.18
| (xi) | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 6 | 908.7 | 908.7 | 908.7
| (xii) | Aluminium Paint | 7130210809 | Ltr | 338.4 | 6 | 2030.4 | 2030.4 | 2030.4
3 |  | OTHER MISCELLANEOUS ITEMS
| i | Concreting of structure @ 0.45 Cmt. per bus structure (1:3:6) = 7.2 Cmt for 16 Nos structure. | 7130200202 | Kg | 2970 | 8.6 | 25542 | 25542 | 25542 | Material cost including GST and labour.
| ii | Concreting of Transformer foundation (1:3:6) = 15 cmt | 7130200202 | Kg | 2970 | 15 | 44550 | 44550 | 44550 | Material cost including GST and labour.
| iii | Concreting of 11 kV VCB foundation (1:3:6) = 18 cmt. | 7130200202 | Kg | 2970 | 18 | 53460 | 53460 | 53460 | Material cost including GST and labour.
| iv | Concreting of 33 kV VCB foundation (1:3:6) = 7 cmt. | 7130200202 | Kg | 2970 | 7 | 20790 | 20790 | 20790 | Material cost including GST and labour.
| v | Control cable for Xmer & VCB
|  | a) 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 129.5439 | 180 | 23317.9074 | 23317.9074 | 23317.9074
|  | b) 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 68.1431 | 720 | 49063.0032 | 49063.0032 | 49063.0032
|  | c) 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.1091 | 180 | 7039.6326 | 7039.6326 | 7039.6326
| vi | Earthing for addl X'mer & VCB
Document – As per W/o of G.S. Flat mesh earthing of 33/11 kV S/s as per No. CE/RR/TR/4328/9029 Raipur, Dt. 05/03/2007 (Rate taken from Sch.- III)
|  | (i) 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4453.22 | 9 | 40078.98 | 40078.98 | 40078.98
|  | (ii) GI Pipe of 40 mm dia 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 876.17 | 24 | 21028.08 | 21028.08 | 21028.08
|  | (iii) MS flat 50x6 mm size | 7130600173 | Kg | 46.9271 | 400 | 18770.856 | 18770.856 | 18770.856
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 65.0097 | 31 | 2015.2995 | 2015.2995 | 2015.2995
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 99.03 | 25 | 2475.75 | 2475.75 | 2475.75
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 99.03 | 10 | 990.3 | 990.3 | 990.3
|  | (vii) GI Spring washers | 7130622922 | Kg | 153.83 | 5 | 769.15 | 769.15 | 769.15
| vii | M.S. Nut- Bolts |  | Kg |  | 213
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 71.59 | 10 | 715.9 | 715.9 | 715.9
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 70.4 | 8 | 563.2 | 563.2 | 563.2
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 70.4 | 25 | 1760 | 1760 | 1760
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 69.2 | 70 | 4844 | 4844 | 4844
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 69.2 | 80 | 5536 | 5536 | 5536
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 69.2 | 20 | 1384 | 1384 | 1384
4 |  | SUB TOTAL - A (1+2+3) [Material cost including GST] |  |  |  |  | 2975635.5212 | 4897796.0012 | 5883652.9812
5 |  | Material cost excluding GST (Sub Total- A / 1.18) |  |  |  |  | 2521725.018 | 4150674.5773 | 4986146.5943 | NEW ROW ADDED
6 |  | Incidental Charges @ 7.5% on Sub-Total - A : - |  |  | 0.075 |  | 223172.6641 | 367334.7001 | 441273.9736 | Earlier name was - Incidental Charges @ 9%
7 |  | (i) Services on Earthing |  | No. | 12268.8792 | 1 | 12268.8792 | 12268.8792 | 12268.8792 | No. of earthing = 6; services on 6 earthing =6x1943=11658/-
|  | (ii) Services on Painting |  | No. | 17809.6618 | 1 | 17809.6618 | 17809.6618 | 17809.6618
|  | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete (Metal measured in stacks will be reduced by 8% for voids). |  | Cmt | 1140 | 45 | 51300 | 51300 | 51300 | NAME CHANGED
|  | Services on Labelling of equipments |  | No | 14841.3847 | 1 | 14841.3847 | 14841.3847 | 14841.3847
|  | Services on X'mer foundation [2.5(L)*2(W)*3(H)] |  | Cmt | 4490.1935 | 15 | 67352.9028 | 67352.9028 | 67352.9028
|  | Services on foundation of 11 kV VCB [2(L)*2(W)*1.5(H)] |  | Cmt | 4490.1935 | 18 | 80823.4834 | 80823.4834 | 80823.4834
|  | Services on foundation of 33 kV VCB [2(L)*2(W)*1.75(H)] |  | Cmt | 4490.1935 | 7 | 31431.3546 | 31431.3546 | 31431.3546
|  | Construction of brick masonry cable trench with cover |  | RM | 2151.893 | 45 | 96835.185 | 96835.185 | 96835.185
8 |  | Labour charges: - |  |  |  |  | 241838.065 | 253543.985 | 265641.485
| i | X'mer erection (Labour sch BL-3) |  |  |  |  | 62048.37 | 73754.29 | 85851.79
| ii | Other items as per schedule [Labour Schedule BL-2+(4*BL-4)] |  |  |  |  | 150183.8 | 150183.8 | 150183.8
| iii | Labour charges for concreting |  | Cmt | 609.1748 | 48.6 | 29605.895 | 29605.895 | 29605.895
9 |  | Transport charges upto 50 Km lead from area stores to construction site for addl. lead refer Schedule T-2
| i | For Transformer only |  |  |  |  | 3850.0793 | 11044.0898 | 15719.4455
| ii | For other material (Excluding Power Transformer) |  |  |  |  | 9003.0535 | 11247.9579 | 12779.6403
10 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 4, 6, 7, 8, 9 |  |  |  |  | 478270.2793 | 739203.6982 | 873966.2971
11 |  | Total Estimated Cost excluding GST (Row 5, 6, 7, 8, 9, 10) |  |  |  |  | 3850522.0107 | 5905711.8598 | 6968190.2872
12 |  | Applicable CGST @ 9% on Row 11 |  |  | 0.09 |  | 346546.981 | 531514.0674 | 627137.1259
13 |  | Applicable SGST @ 9% on Row 11 |  |  | 0.09 |  | 346546.981 | 531514.0674 | 627137.1259
14 |  | Total estimated cost of S/s including GST (Row 11+12+13). |  |  |  |  | 4543615.9727 | 6968739.9945 | 8222464.5389
15 |  | Total estimated cost of S/s including GST (Rounded off) |  |  |  |  | 4543616 | 6968740 | 8222465
Note: |  | (1) All the rates are with considering price variation clause.
(2) In case of non-availability of H-Beam for structure double welded RS Joist may be used and cost should be taken on actual material used
Note on C31: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category A
Note on C92: Barun Chakraborty: Earlier name was - SUB TOTAL - A (1+2+3)
Note on C97: 89326879: Earlier name was - Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) including all labour, T&P, transportation, loading unloading, royalty, taxes etc. complete and including spreading in 100 mm thick layers complete (Metal measured in stacks will be reduced by 8% for voids).
Note on E102: 89326879: Earlier unit taken as Mtr
*

## B-4
COST SCHEDULE B-4
(33/11 kV SUB-STATIONS)
11 kV OUT DOOR YARD EXTENSION FOR ADDL. BAY WITH CIRCUIT BREAKER
2019-20
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | 1.6 MVA & Above
[6 empty] | Qnty | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | H-Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 No = 593.6 Kgs | 7130601958 | Kg | 53.8792 | 594 | 32004.2329
2 |  | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1 x 11 mtr = 408.1 kg/pole x 2 Nos = 816.2 Kgs. | 7130601965 | Kg | 53.8792 | 816.2 | 43976.1867
3 |  | MS DC Cross arm (100x50 mm), 5.2 Mtr long for bus bar | 7130810684 | Set | 8809.64 | 6 | 52857.84
4 |  | MS DC Cross arm (100x50 mm), 8' centre for bus bar | 7130810517 | Set | 4736.61 | 2 | 9473.22
5 |  | Strain set with hardware suitable for 100 Sqmm ACSR conductor for 11 kV bus. |  | Set |  | 21
| (i) | 11 kV Polymer Disc insulator for double disc | 7130820010 | No | 119.1 | 42 | 5002.2
| (ii) | Hardware suitable for 100 Sqmm ACSR Dog conductor for 11 kV bus. | 7130820248 | No | 256.44 | 21 | 5385.24
6 |  | 11 kV Polymeric Pin insulator with Pin | 7130820008 | Each | 132.09 | 3 | 396.27
7 |  | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 328.57 | 3 | 985.71
8 |  | 11 kV Isolator (600 A.) | 7131930663 | Each | 23345.09 | 2 | 46690.18
9 |  | 11 kV AB Switch | 7131930221 | Each | 8496 | 1 | 8496
10 |  | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2970 | 1.8 | 5346 | Material cost including GST and labour.
11 |  | ACSR 100 Sqmm Al. Eq. Dog Conductor | 7130830063 | Mtr | 67.4322 | 50 | 3371.612
12 |  | Terminal clamp for jumpering of 100 Sqmm Al. Eq ACSR Conductor / Isolator | 7130830585 | No | 275.5 | 24 | 6612
13 |  | 11 kV feeder control VCB with CT's (One 11 kV VCB controlling two feeders) with control panel. |  | No | 189755.88 | 1
| (i) | 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 119502.62 | 1 | 119502.62
| (ii) | 11 kV feeder Control Panel | 7131960008 | No | 26777.87 | 1 | 26777.87
| (iii) | 11 kV CT's 300-150/5 Amps | 7132230188 | No | 13447.4 | 3 | 40342.2
| (iv) | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 3133.19 | 1 | 3133.19
14 |  | Concreting of foundation of VCB (1:3:6) | 7130200202 | Cmt | 2970 | 6 | 17820 | Material cost including GST and labour.
15 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 129.5439 | 60 | 7772.6358
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 68.1431 | 120 | 8177.1672
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.1091 | 60 | 2346.5442
16 |  | H.T. STATIC TRIVECTOR METER for feeder metering. |  | No | 3611.89 | 1
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 3611.89 | 1 | 3611.89
17 |  | 11 kV CT/PT unit 200-100/5 Amp. | 7132230412 | Each | 37649.28 | 1 | 37649.28
18 |  | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 2 | 302.9
19 |  | Aluminium Paint | 7130210809 | Ltr | 338.4 | 2 | 676.8
20 |  | M.S. Nuts & Bolts |  | Kg |  | 30
| a | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 71.59 | 3 | 214.77
| b | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 70.4 | 2 | 140.8
| c | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 70.4 | 2 | 140.8
| d | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 69.2 | 6 | 415.2
| e | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 69.2 | 15 | 1038
| f | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 69.2 | 2 | 138.4
21 |  | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 490797.7588
22 |  | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 415930.3041 | NEW ROW ADDED
23 |  | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 36809.8319 | Earlier name was - Incidental Charges @ 9%
24 | a | Services on Painting of structure |  | No | 4155.5878 | 1 | 4155.5878
| b | Construction of brick masonry cable trench with cover |  | RM | 2151.893 | 5 | 10759.465
25 |  | Labour charges |  |  |  |  | 34315.4234
| i | as per Schedule No. BL-4 |  |  |  |  | 29563.86
| ii | for concreting of structure |  | Cmt | 609.1748 | 1.8 | 1096.5146
| iii | for foundation of VCB |  | Cmt | 609.1748 | 6 | 3655.0488
26 |  | Transport charges upto 50 Km lead from area stores to construction site for addl. lead refer Schedule T-2. |  |  |  |  | 4480.4407
27 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 21, 23, 24, 25, 26 |  |  |  |  | 72664.8134
28 |  | Total Estimated Cost excluding GST (Row 22, 23, 24, 25, 26, 27) |  |  |  |  | 579115.8663
29 |  | Applicable CGST @ 9% on Row 28 |  |  | 0.09 |  | 52120.428
30 |  | Applicable SGST @ 9% on Row 28 |  |  | 0.09 |  | 52120.428
31 |  | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 683356.7222
32 |  | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 683357
Note :- |  | All the rates are with considering price variation clause.
Note on C36: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category A
Note on C47: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on E20: Barun Chakraborty: Earlier unit was - Set

## B-5
COST SCHEDULE B-5
| (33/11 kV SUB-STATIONS) |  |  |  | 2019-20
33 kV OUT DOOR YARD EXTENSION FOR ADDITIONAL BAY.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 Nos = 593.6 Kgs | 7130601958 | Kg | 53.8792 | 593.6 | 31982.6812
2 | MS DC cross arm (100x50 mm), 5.2 Mtr. long for bus bar | 7130810684 | Set | 8809.64 | 6 | 52857.84
3 | Strain set with hardware suitable for 80 Sqmm ACSR conductor for 33 kV bus (3 disc insulator per disc) |  | Set | 13720.05 | 15
| (i) 33 kV Polymer Disc Insulator | 7130820013 | No | 219.41 | 45 | 9873.45
| (ii) 33 kV Hardware | 7130820248 | Each | 256.44 | 15 | 3846.6
4 | 33 kV Isolator (600 Amps.) without earth switch | 7131930752 | No | 40401.22 | 2 | 80802.44
5 | Terminal clamp for isolators | 7130830585 | No | 275.5 | 12 | 3306
6 | T-clamps for bus jumper | 7130830585 | No | 275.5 | 6 | 1653
7 | ACSR 100 Sqmm Al. Eq. Conductor | 7130830063 | Mtr | 67.4322 | 50 | 3371.612
8 | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2970 | 0.9 | 2673 | Material cost including GST and labour.
9 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | Each | 325.76 | 6 | 1954.56
10 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 2 | 302.9
11 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 2 | 676.8
12 | M.S. Nuts & Bolts |  | Kg |  | 40
| MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 71.59 | 2 | 143.18
| MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 70.4 | 3 | 211.2
| MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 70.4 | 5 | 352
| MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 69.2 | 15 | 1038
| MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 69.2 | 10 | 692
| MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 69.2 | 5 | 346
13 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 196083.2632
14 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 166172.257 | NEW ROW ADDED
15 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 14706.2447 | Earlier name was - Incidental Charges @ 9%
16 | Services on Painting on structure |  | No | 4155.5878 | 1 | 4155.5878
17 | Labour charges as per Schedule No BL-5 |  |  |  |  | 22935.54
18 | Labour charges for concreting |  | Cmt | 609.1748 | 0.9 | 548.2573
19 | Transport charges upto 50 Km lead from Area stores to construction site for addl. lead refer Schedule T-2. |  |  |  |  | 4480.4407
20 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 13, 15, 16, 17, 18, 19 |  |  |  |  | 30363.6667
21 | Total Estimated Cost excluding GST (Row 14, 15, 16, 17, 18, 19, 20) |  |  |  |  | 243361.9942
22 | Applicable CGST @ 9% on Row 21 |  |  | 0.09 |  | 21902.5795
23 | Applicable SGST @ 9% on Row 21 |  |  | 0.09 |  | 21902.5795
24 | Total Estimated Cost including GST (Row 21+22+23) |  |  |  |  | 287167.1532
25 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 287167
Note: -For the provision of 33 kV VCB installation, the cost Schedule No.- B-6 may be referred to. All the rates are with considering price variation clause
Note on B28: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## B-6
COST SCHEDULE B-6
2019-20
INSTALLATION OF 33 kV VCB
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | 33 kV VCB with control panel & CT |  | No | 362871.08 | 1
| (i) | 33 kV VCB (without CT's & Panel) | 7131943380 | No | 244236.87 | 1 | 244236.87
| (ii) | 33 kV Control Panel | 7131960524 | No | 40103.54 | 1 | 40103.54
| (iii) | 33 kV CT's 300-150/5 Amps | 7132230263 | No | 26176.89 | 3 | 78530.67
| (iv) | Marshelling Box (with 10 No. connectors) | 7130352046 | No | 3133.19 | 1 | 3133.19
2 |  | Concreting of foundation of 33 kV breaker (1:3:6) | 7130200202 | Cmt | 2970 | 7 | 20790 | Material cost including GST and labour.
3 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 129.5439 | 60 | 7772.6358
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 68.1431 | 120 | 8177.1672
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.1091 | 60 | 2346.5442
4 |  | Terminal clamps | 7130830585 | No | 275.5 | 6 | 1653
5 |  | Tee clamp for jumper | 7130830585 | No | 275.5 | 6 | 1653
6 |  | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 408396.6172
7 |  | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 346098.8281 | NEW ROW ADDED
8 |  | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 30629.7463 | Earlier name was - Incidental Charges @ 9%
9 |  | Labour charges for concreting |  | Cmt | 609.1748 | 7 | 4264.2236
10 |  | Labour charges as per Schedule No BL-6 |  |  |  |  | 8677
11 |  | Transportation charges |  |  |  |  | 7669.0561
12 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 06, 08, 09, 10, 11 |  |  |  |  | 57454.5804
13 |  | Total Estimated Cost excluding GST (Row 07, 08, 09, 10, 11, 12) |  |  |  |  | 454793.4345
14 |  | Applicable CGST @ 9% on Row 13 |  |  | 0.09 |  | 40931.4091
15 |  | Applicable SGST @ 9% on Row 13 |  |  | 0.09 |  | 40931.4091
16 |  | Total Estimated Cost including GST (Row 13+14+15) |  |  |  |  | 536656.2527
17 |  | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 536656
Note on C19: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## B-8
COST SCHEDULE B-8
AUGMENTATION OF 33/11 kV SUB-STATION CAPACITY BY REPLACEMENT OF POWER TRANSFORMER
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | 1.6 to 3.15 MVA |  | 3.15 to 5.0 MVA without 33 kV VCB |  | 3.15 to 5.0 MVA with 33 kV VCB
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 33/11 kV 3.15 MVA X-mer | 7132220095 | No | 2393149.15 | 1 | 2393149.15 | -- | -- | -- | --
2 | 33/11 kV 5.0 MVA X-mer | 7132220097 | No | 3379006.13 | -- | -- | 1 | 3379006.13 | 1 | 3379006.13
3 | 33 kV VCB (With CT's and control panel) |  | No |  | 1 |  | -- | -- | 1
| (i) 33 kV VCB (without CT's and panels) | 7131943380 | No | 244236.87 | 1 | 244236.87 |  |  | 1 | 244236.87
| (ii) 33 kV Control Panel | 7131960524 | No | 40103.54 | 1 | 40103.54 |  |  | 1 | 40103.54
| (iii) 33 kV CT's (300-150/5) Amps | 7132230263 | No | 26176.89 | 3 | 78530.67 |  |  | 3 | 78530.67
4 | Concreting of foundation for 33 kV VCB (1:3:6) | 7130200202 | Cmt | 2970 | -- | -- | -- | -- | 7 | 20790 | Material cost including GST and labour.
5 | Control cabling
a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 129.5439 | 60 | 7772.6358 | 60 | 7772.6358 | 60 | 7772.6358
b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 68.1431 | 120 | 8177.1672 | 120 | 8177.1672 | 120 | 8177.1672
c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 39.1091 | 60 | 2346.5442 | 60 | 2346.5442 | 60 | 2346.5442
6 | Terminal clamp for transformer | 7130830586 | No | 220.16 |  |  |  |  | 7 | 1541.12
7 | T-clamps for jumper | 7130830586 | No | 220.16 | -- | -- | -- | -- | 3 | 660.48
8 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 2774316.5772 |  | 3397302.4772 |  | 3783165.1572
9 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 2351115.7434 |  | 2879069.8959 |  | 3206072.1671 | NEW ROW ADDED
10 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 208073.7433 |  | 254797.6858 |  | 283737.3868 | Earlier name was - Incidental Charges @ 9%
11 | Labour charges as per Schedule No BL-8 |  |  |  |  | 82431 |  | 82431 |  | 82431
12 | Labour charges for concreting |  | Cmt | 609.1748 | -- | -- | -- | -- | 7 | 4264.2236
13 | Transport charges for transformer upto 50 Kms lead |  |  |  |  | 13038.2543 |  | 23409.8106 |  | 23409.8106
14 | Transport charges for VCB |  |  |  |  | 7669.0561 |  | 0 |  | 7669.0561
15 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 08, 10, 11, 12, 13, 14 |  |  |  |  | 385691.0789 |  | 469742.6217 |  | 523084.5793
16 | Total Estimated Cost excluding GST (Row 09, 10, 11, 12, 13, 14, 15) |  |  |  |  | 3048018.876 |  | 3709451.0141 |  | 4130668.2235
17 | Applicable CGST @ 9% on Row 16 |  |  | 0.09 |  | 274321.6988 |  | 333850.5913 |  | 371760.1401
18 | Applicable SGST @ 9% on Row 16 |  |  | 0.09 |  | 274321.6988 |  | 333850.5913 |  | 371760.1401
19 | (-) Cost of Old Transformer assuming 25 years of life & 5 years in service. |  |  |  |  | 584300.84 |  | 1491844.86 |  | 1491844.86
20 | Total Estimated Cost of Augmentation including GST (Row 16+17+18-19) |  |  |  |  | 3012361.4336 |  | 2885307.3366 |  | 3382343.6437
21 | Total Estimated Cost of Augmentation including GST (Rounded off) |  |  |  |  | 3012361 |  | 2885307 |  | 3382344
Note:- All the rates are with considering price variation clause.
Note on B23: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## B-9
COST SCHEDULE B-9
INSTALLATION OF 1.6 MVA 33/11 kV SUB-STATION ON LINE
2019-20
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | CIVIL WORKS (Rate as per SoR PWD)
| 1 | Land |  | Sq Mtr | LS
| 2 | Construction of 1.5 Mtr high barbed wire fencing in angle iron post as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Mtr | 406 | 32 | 12992
| 3 | Construction of 4.50 m x 2.15 m size yard / area gate as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, taxes etc. complete. |  | Each | 35276 | 1 | 35276
| 4 | Total of 01 : - |  |  |  |  | 48268
2 |  | EQUIPMENTS AND BUS BAR ARRANGEMENT
| 1 | Power Transformer 1.6 MVA | 7132220091 | No | 805738.17 | 1 | 805738.17
| 2 | PCC supports 280 Kg; 9.0 Mtr. long | 7130800033 | No | 4402.65 | 2 | 8805.3
| 3 | 33 kV "V" cross arm | 7130810595 | No | 2429.24 | 2 | 4858.48
|  | (i) Cross arm clamp | 7130810361 | Pair | 319.69 | 2 | 639.38
| 4 | 33 kV Top clamp | 7130810676 | No | 404.18 | 5 | 2020.9
| 5 | 33 kV A.B. Switch | 7131930321 | Each | 18863.48 | 1 | 18863.48
| 6 | 33 kV D.O. Fuse Unit | 7131930415 | Each | 2886.87 | 3 | 8660.61
| 7 | 33 kV Polymer Lightning Arrestor | 7130840021 | Each | 3221.41 | 3 | 9664.23
| 8 | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 325.76 | 9 | 2931.84
| 9 | MS Channel 100x50 mm, 5.2 Mtr. Long for D.O., A.B. switch and LA mounting. | 7130810684 | Set | 8809.64 | 2 | 17619.28
| 10 | PCC supports 140 Kg; 8.0 Mtr. for 11 kV Bus | 7130800012 | No | 2255.2 | 8 | 18041.6
| 11 | MS Channel 5.2 Mtr. long | 7130810684 | No | 8809.64 | 16 | 140954.24
| 12 | 11 kV AB Switch complete | 7131930221 | Each | 8496 | 3 | 25488
| 13 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 328.57 | 3 | 985.71
| 14 | 11 kV Strain set with hardware |  | Set |  | 21
|  | 11 kV Polymer Disc insulator | 7130820010 | No | 119.1 | 21 | 2501.1
|  | 11 kV Hardware | 7130820241 | No | 123.43 | 21 | 2592.03
| 15 | ACSR Conductor 80 Sqmm Al. Eq. Raccoon Conductor | 7130830060 | Mtr. | 51.3096 | 20 | 1026.1914
| 16 | T-clamps for Raccoon Conductor | 7130830586 | No | 220.16 | 27 | 5944.32
| 17 | Bimetallic Clamps for Transformer & auto recloser | 7130830052 | No | 671.36 | 12 | 8056.32
| 18 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 5 | 757.25
| 19 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 5 | 1692
| 20 | M.S. Nut- Bolts |  | Kg |  | 125
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 71.59 | 2 | 143.18
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 70.4 | 2 | 140.8
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 70.4 | 25 | 1760
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 69.2 | 40 | 2768
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 69.2 | 50 | 3460
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 69.2 | 6 | 415.2
| 21 | M.S. Flat 50x6 mm | 7130600173 | Kg | 46.9271 | 100 | 4692.714
| 22 | Earthing of Sub-station |  |  | 15024.865
|  | (i) G.I. Pipe of 40 mm dia. 3.04 Mtr. long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | 7130642039 | No | 876.17 | 12 | 10514.04
|  | (ii) MS flat 50x6 mm size | 7130600173 | Kg | 46.9271 | 60 | 2815.6284
|  | (iii) G.I. Wire 8 SWG | 7130870043 | Kg | 65.0097 | 10 | 650.0966
|  | (iv) G.I. Nuts and bolts 16x40 mm | 7130620133 | Kg | 99.03 | 5 | 495.15
|  | (v) G.I. Nuts and bolts 16x65 mm | 7130620140 | Kg | 99.03 | 4 | 396.12
|  | (vi) G.I. Spring washers | 7130622922 | Kg | 153.83 | 1 | 153.83
| 23 | SUB TOTAL-1 (Material cost including GST) : - |  |  |  |  | 1116245.1904
3 |  | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 945970.5003 | NEW ROW ADDED
4 |  | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 83718.3893 | Earlier name was - Incidental Charges @ 9%
5 |  | Services On Earthing of sub-station. |  | No | 3203.0407 | 1 | 3203.0407
6 |  | Labour charges as per Schedule No BL-9 |  |  |  |  | 101764.09
7 |  | Transportation charges |  |  |  |  | 29342.9116
8 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 02(23), 04, 05, 06, 07 |  |  |  |  | 166784.2027
9 |  | Total Estimated Cost excluding GST (Row 03, 04, 05, 06, 07, 08) |  |  |  |  | 1330783.1347
10 |  | Applicable CGST @ 9% on Row 09 |  |  | 0.09 |  | 119770.4821
11 |  | Applicable SGST @ 9% on Row 09 |  |  | 0.09 |  | 119770.4821
12 |  | Total Estimated Cost including GST (Row 09+10+11) |  |  |  |  | 1570324.0989 | NEW ROW ADDED
13 |  | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1570324 | NEW ROW ADDED
14 |  | Total cost including Civil Works [ Row 01(4)+12 ] |  |  |  |  | 1618592.0989
15 |  | Total Cost including Civil Works (Rounded off) : - |  |  |  |  | 1618592
Note:- All the rates are with considering price variation clause.
Note on C51: Barun Chakraborty: Earlier name was - Total of 02
Note on E19: Barun Chakraborty: Earlier unit was - Set

## C-1
COST SCHEDULE C-1
1 KM OF 11 kV LINE ON PCC POLE 140 KG 8.0 METER LONG WITH MAXIMUM OF 65 Mtrs SPAN USING RABBIT AND WEASEL CONDUCTOR
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Using RABBIT Conductor |  |  | Using WEASEL Conductor
|  |  |  | Qnty | Rate | Amount | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 140 Kg, 8.0 Mtr long PCC Poles | 7130800012 | No | 16 | 2255.2 | 36083.2 | 16 | 2255.2 | 36083.2
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 16 | 1091.69 | 17467.04 | 16 | 1091.69 | 17467.04
3 | Cross Arm Clamp | 7130810361 | Pair | 16 | 319.69 | 5115.04 | 16 | 319.69 | 5115.04
4 | 11 kV Top clamp angle type with cleat | 7130810679 | No | 16 | 306.26 | 4900.16 | 16 | 306.26 | 4900.16
5 | Earthing Set (Coil earth as per Drawing No :-G/007 | 7130870013 | No | 16 | 118.52 | 1896.32 | 16 | 118.52 | 1896.32
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 48 | 132.09 | 6340.32 | 48 | 132.09 | 6340.32
7 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 34.7014 | 107574.247
8 | ACSR conductor Weasel with 3% sag | 7130830055 | Mtr |  |  |  | 3100 | 21.0579 | 65279.397
9 | Jointing sleeves suitable for 80 Sq mm. Al. Eq. ACSR Raccoon Conductor | 7130830050 | No | 6 | 37.29 | 223.74 | 6 | 37.29 | 223.74
10 | (i) Stay set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 160.97 | 643.88 | 4 | 160.97 | 643.88
11 | Red Oxide Paint | 7130211158 | Ltr | 4 | 151.45 | 605.8 | 4 | 151.45 | 605.8
12 | Aluminium Paint | 7130210809 | Ltr | 4 | 338.4 | 1353.6 | 4 | 338.4 | 1353.6
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 32 | 78.5018 | 2512.0586 | 32 | 78.5018 | 2512.0586
14 | Danger Board | 7130880041 | Each | 16 | 92.6 | 1481.6 | 16 | 92.6 | 1481.6
15 | Binding wire and tape | 7130830006 | Kg | 3 | 160.41 | 481.23 | 3 | 160.41 | 481.23
16 | MS Nuts and Bolts |  | Kg | 18 |  |  | 18
| 16x90 mm | 7130620619 | Kg | 2 | 70.4 | 140.8 | 2 | 70.4 | 140.8
| 16x160 mm | 7130620627 | Kg | 16 | 69.2 | 1107.2 | 16 | 69.2 | 1107.2
17 | Guarding :- |  |  |  | 7408.3915 |  |  | 7408.3915
| (i) 11 kV Guarding Channel 100x50 mm set | 7130810511 | No | 1 | 2588.62 | 2588.62 | 1 | 2588.62 | 2588.62
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 65.0097 | 2275.3381 | 35 | 65.0097 | 2275.3381
| (iii) Stay Clamp | 7130810026 | Pair | 2 | 160.97 | 321.94 | 2 | 160.97 | 321.94
| (iv) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 72.6867 | 799.5534 | 11 | 72.6867 | 799.5534
| (v) Stay set 16 mm | 7130860032 | No | 2 | 455.31 | 910.62 | 2 | 455.31 | 910.62
| (vi) I- Bolt Big size | 7130620013 | No | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32
18 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  | 22 |  |  | 22
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 28 | 158 | 4424 | 28 | 158 | 4424 | Material cost including GST and labour.
19 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 203178.9738 |  |  | 160884.1238
20 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 172185.571 |  |  | 136342.4778 | NEW ROW ADDED
21 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 15238.423 |  | 0.075 | 12066.3093 | Earlier name was - Incidental Charges @ 9%
22 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 12 | 311.3185 | 3735.822 | 12 | 311.3185 | 3735.822
23 | Labour charges as per Sch No.- CL-1 |  |  |  |  | 41270.56 |  |  | 36726.55
24 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 9626.381 |  |  | 9626.381
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 19, 21, 22, 23, 24 |  |  |  |  | 34131.27 |  |  | 27879.8983
26 | Total Estimated Cost excluding GST (Row 20, 21, 22, 23, 24, 25) |  |  |  |  | 276188.027 |  |  | 226377.4383
27 | Applicable CGST @ 9% on Row 26 |  |  |  | 0.09 | 24856.9224 |  | 0.09 | 20373.9694
28 | Applicable SGST @ 9% on Row 26 |  |  |  | 0.09 | 24856.9224 |  | 0.09 | 20373.9694
29 | Total Estimated Cost including GST (Row 26+27+28) |  |  |  |  | 325901.8718 |  |  | 267125.3772
30 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 325902 |  |  | 267125
Note: - Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B38: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## C-2
COST SCHEDULE C-2
11 kV DP STRUCTURE ON PCC POLE 140 KG 8 METER LONG (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg, 8.0 Mtr long PCC Poles | 7130800012 | No | 2 | 2255.2 | 4510.4
2 | DC Cross arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | Set | 1 | 4104.29 | 4104.29
3 | 11 kV Polymer Disc Insulator | 7130820010 | No. | 6 | 119.1 | 714.6
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 123.43 | 740.58
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 132.09 | 396.27
6 | Horizontal & Cross Bracing 4' Center with set of 4 back Clamps |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 43.1218 | 2242.3346
| (ii) Back Clamp for Pole | 7130810692 | Pair | 4 | 333.29 | 1333.16
7 | (i) Stay set 16 mm | 7130860032 | No | 6 | 455.31 | 2731.86
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per Stay | 7130860077 | Kg | 33 | 72.6867 | 2398.6601
| (iii) Stay Clamp | 7130810026 | Pair | 6 | 160.97 | 965.82
8 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay (1:3:6) | 7130200202 | Cmt | 1.8 | 2970 | 5346 | Material cost including GST and labour.
9 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 118.52 | 237.04
10 | Red Oxide paint | 7130211158 | Ltr | 0.5 | 151.45 | 75.725
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 338.4 | 169.2
12 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 78.5018 | 314.0073
13 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6
14 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795
| 16x200 mm | 7130620631 | Kg | 5.5 | 69.2 | 380.6
15 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 26788.9421
16 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 22702.4933 | NEW ROW ADDED
17 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 2009.1707 | Earlier name was - Incidental Charges @ 9%
18 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 2 | 311.3185 | 622.637
19 | Labour charges as per Sch. No - CL-2 |  |  |  |  | 8433.26
20 | Labour charges for concreting |  | Cmt | 1.8 | 609.1748 | 1096.5146
21 | Transport charges upto 50 Kms. average lead from Area stores to construction camp incl. site transport (Transport Sch T-1) |  |  |  |  | 3653.2451
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 15, 17, 18, 19, 20, 21 |  |  |  |  | 5325.4712
23 | Total Estimated Cost excluding GST (Row 16, 17, 18, 19, 20, 21, 22) |  |  |  |  | 43842.7918
24 | Applicable CGST @ 9% on Row 23 |  |  |  | 0.09 | 3945.8513
25 | Applicable SGST @ 9% on Row 23 |  |  |  | 0.09 | 3945.8513
26 | Total Estimated Cost including GST (Row 23+24+25) |  |  |  |  | 51734.4943
27 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 51734
Note: | All the rates are with considering price variation clause.
Note on B29: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D16: Barun Chakraborty: Earlier unit was - No.
Note on D19: 89326879: Earlier unit was - No.

## C-3
COST SCHEDULE C-3
2019-20
1 KM OF 11 kV LINE ON H-BEAM / PCC POLE SUPPORT WITH MAXIMUM OF 80 Mtrs SPAN USING RABBIT CONDUCTOR
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 12 Nos = 4897.2 Kgs | 7130601965 | Kg | 4897.2 | 53.8792 | 263857.1203
2 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No |  |  |  | 12 | 7605.2 | 91262.4
3 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 12 | 1091.69 | 13100.28 | 12 | 1091.69 | 13100.28
4 | Back Clamp for Cross Arm
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 12 | 333.29 | 3999.48
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair |  |  |  | 12 | 300.41 | 3604.92
5 | 11 kV Top clamp angle type with cleat | 7130810679 | No | 12 | 306.26 | 3675.12 | 12 | 306.26 | 3675.12
6 | Earthing Set (Coil earth as per Drawing No :- G/007 | 7130870013 | No | 12 | 118.52 | 1422.24 | 12 | 118.52 | 1422.24
7 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 36 | 132.09 | 4755.24 | 36 | 132.09 | 4755.24
8 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 34.7014 | 107574.247 | 3100 | 34.7014 | 107574.247
9 | Jointing sleeves suitable for 50 Sqmm Al Eq. ACSR Conductor | 7130830854 | No | 6 | 30.07 | 180.42 | 6 | 30.07 | 180.42
10 | (I) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (II) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 34 | 72.6867 | 2471.3468 | 34 | 72.6867 | 2471.3468
(III) Stay Clamp
| (i) Stay Clamp For "H" Beam | 7130810692 | Pair | 4 | 333.29 | 1333.16
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair |  |  |  | 4 | 300.41 | 1201.64
11 | Concreting of supports @ 0.6 Cmt. Per Pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC & @ 0.2 Cmt. Per Stay and @ 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt. | 9 | 2970 | 26730 | 7.8 | 2970 | 23166 | Material cost including GST and labour.
12 | Red Oxide Paint | 7130211158 | Ltr | 3 | 151.45 | 454.35 | 1.7 | 151.45 | 257.465
13 | Aluminium Paint | 7130210809 | Ltr | 3 | 338.4 | 1015.2 | 1.8 | 338.4 | 609.12
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 24 | 78.5018 | 1884.0439 | 24 | 78.5018 | 1884.0439
15 | Danger Board | 7130880041 | Each | 12 | 92.6 | 1111.2 | 12 | 92.6 | 1111.2
16 | Binding wire and tape | 7130830006 | Kg | 3 | 160.41 | 481.23 | 3.5 | 160.41 | 561.435
17 | MS Nuts and Bolts |  | Kg | 13 |  |  | 18
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795
| 16x65 mm | 7130620614 | Kg | 6 | 70.4 | 422.4
| 16x90 mm | 7130620619 | Kg |  |  |  | 3.5 | 70.4 | 246.4
| 16x140 mm | 7130620625 | Kg | 6.5 | 69.2 | 449.8
| 16x160 mm | 7130620627 | Kg |  |  |  | 14.5 | 69.2 | 1003.4
18 | Guarding |  | LS
| (i) 11 kV Guarding Channel 100x50 mm | 7130810511 | No | 1 | 2588.62 | 2588.62 | 1 | 2588.62 | 2588.62
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 65.0097 | 2275.3381 | 35 | 65.0097 | 2275.3381
| (iii) Stay Clamp | 7130810026 | Pair | 2 | 160.97 | 321.94 | 2 | 160.97 | 321.94
| (iv) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 17 | 72.6867 | 1235.6734 | 17 | 72.6867 | 1235.6734
| (v) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 2 | 455.31 | 910.62 | 2 | 455.31 | 910.62
| (vi) I- Bolt Big Size | 7130620013 | No. | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32
19 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 444618.4245 |  |  | 267752.6692
20 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 376795.275 |  |  | 226909.0417 | NEW ROW ADDED
21 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 33346.3818 |  | 0.075 | 20081.4502 | Earlier name was - Incidental Charges @ 9%
22 | Labour charges as per Sch No - CL-4 |  |  |  |  | 58156.45 |  |  | 59738.95
23 | Labour charges for concreting |  | Cmt | 9 | 609.1748 | 5482.5731 | 7.8 | 609.1748 | 4751.5634
24 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 9626.381 |  |  | 9626.381
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 19, 21, 22, 23, 24 |  |  |  |  | 68903.7763 |  |  | 45243.8767
26 | Total Estimated Cost excluding GST (Row 20, 21, 22, 23, 24, 25) |  |  |  |  | 552310.8373 |  |  | 366351.263
27 | Applicable CGST @ 9% on Row 26 |  |  |  | 0.09 | 49707.9754 |  | 0.09 | 32971.6137
28 | Applicable SGST @ 9% on Row 26 |  |  |  | 0.09 | 49707.9754 |  | 0.09 | 32971.6137
29 | Total Estimated Cost including GST (Row 26+27+28) |  |  |  |  | 651726.788 |  |  | 432294.4903
30 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 651727 |  |  | 432294
Note: - Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
All the rates are with considering price variation clause.
Note on B43: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D12: Barun Chakraborty: Earlier unit was - No.
Note on D13: Barun Chakraborty: Earlier unit was - No.
Note on D22: Barun Chakraborty: Earlier unit was - No.
Note on D23: Barun Chakraborty: Earlier unit was - No.

## C-3 (A)
COST SCHEDULE C-3 (A)
2019-20
ADDITIONAL (MID SPAN) POLES FOR 11 kV LINE
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-BEAM 152X152 MM 37.10 Kg/MTR 11.0 MTR LONG
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole | 7130601965 | Kg | 408.1 | 53.8792 | 21988.0934
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 1 | 1091.69 | 1091.69
3 | Back Clamp for Cross Arm
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 1 | 333.29 | 333.29
4 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 1 | 306.26 | 306.26
5 | Earthing Set (Coil earth as per Drawing No:-G/007 | 7130870013 | No | 1 | 118.52 | 118.52
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 132.09 | 396.27
7 | Concreting of supports H-Beam @ 0.6 Cmt. Per Pole & @ 0.2 Cmt. Per Stay and 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt. | 0.65 | 2970 | 1930.5 | Material cost including GST and labour.
8 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 78.5018 | 157.0037
9 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6
10 | MS Nuts and Bolts
| 16x40 mm | 7130620609 | Kg | 0.25 | 71.59 | 17.8975
| 16x65 mm | 7130620614 | Kg | 0.6 | 70.4 | 42.24
| 16x140 mm | 7130620625 | Kg | 0.55 | 69.2 | 38.06
11 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 26512.4245
12 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 22468.1564 | NEW ROW ADDED
13 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 1988.4318 | Earlier name was - Incidental Charges @ 9%
14 | Labour charges as per Sch No. CL-4 (revised based on one pole) |  |  |  |  | 2831.7851
15 | Labour charges for concreting |  | Cmt | 0.65 | 609.1748 | 395.9636
16 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) - Taken 5% of |  |  |  |  | 481.3222
17 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 11, 13, 14, 15, 16 |  |  |  |  | 4026.2409
18 | Total Estimated Cost excluding GST (Row 12, 13, 14, 15, 16, 17) |  |  |  |  | 32191.9
19 | Applicable CGST @ 9% on Row 18 |  |  |  | 0.09 | 2897.271
20 | Applicable SGST @ 9% on Row 18 |  |  |  | 0.09 | 2897.271
21 | Total Estimated Cost per pole including GST (Row 18+19+20) |  |  |  |  | 37986.442
22 | Total Estimated Cost per pole including GST (Rounded off) |  |  |  |  | 37986
Note on B23: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D12: Barun Chakraborty: Earlier unit was - No.

## C-3 (B)
COST SCHEDULE C-3 (B)
COST PER KM OF 11 kV LINE ON AERIAL BUNCHED CABLE (ABC) OF 35 & 70 SQ.MM. ON 11 MTR. LONG H - BEAM / 9.0 MTR LONG PCC POLE OF SPAN 35 MTRS.
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | "H" Beam 152x152mm 37.1 Kg/Mtr 11.0 Mtr long |  |  |  | 200 Kg; 9.0 Mtr long PCC Pole
[5 empty] | Using 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 29 Nos = 11835 Kgs | 7130601965 | Kg | 53.8792 | 11835 | 637660.0953 | 11835 | 637660.0953
2 | 200 Kg 9.0 Meter long PCC Pole | 7130800001 | No. | 3046.2 |  |  |  |  | 29 | 88339.8 | 29 | 88339.8
3 | 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm (incl. 6% sag) | 7130310057 | Km | 324086.39 | 1.06 | 343531.5734 |  |  | 1.06 | 343531.5734
4 | 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm (incl. 6% sag) | 7130310058 | Km | 458499.87 |  |  | 1.06 | 486009.8622 |  |  | 1.06 | 486009.8622
5 | 11 kV Termination kit 35-70 sqmm | 7130320048 | Set | 2542.72 | 9 | 22884.48 | 9 | 22884.48 | 9 | 22884.48 | 9 | 22884.48
6 | 11 kV AB Cable straight through jointing kit suitable for 35-70 sqmm | 7130310061 | Set | 4014.82 | 6 | 24088.92 | 6 | 24088.92 | 6 | 24088.92 | 6 | 24088.92
7 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 2408.9 | 16 | 38542.4 | 16 | 38542.4 | 16 | 38542.4 | 16 | 38542.4
8 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 2141.24 | 21 | 44966.04 | 21 | 44966.04 | 21 | 44966.04 | 21 | 44966.04
9 | Eye Hook | 7130893004 | No. | 182.42 | 40 | 7296.8 | 40 | 7296.8 | 40 | 7296.8 | 40 | 7296.8
10 | Stay set 16 mm | 7130860032 | No. | 455.31 | 12 | 5463.72 | 12 | 5463.72 | 12 | 5463.72 | 12 | 5463.72
11 | Stay wire 7/10 SWG 10 kg/stay | 7130860077 | Kg | 72.6867 | 120 | 8722.4004 | 120 | 8722.4004 | 120 | 8722.4004 | 120 | 8722.4004
12 | Earth spike | 7130870010 | No. | 789.29 | 29 | 22889.41 | 29 | 22889.41 | 29 | 22889.41 | 29 | 22889.41
13 | G.I. Wire 6 SWG | 7130870045 | Kg | 65.0097 | 24 | 1560.2318 | 24 | 1560.2318 | 24 | 1560.2318 | 24 | 1560.2318
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 78.5018 | 58 | 4553.1061 | 58 | 4553.1061 | 58 | 4553.1061 | 58 | 4553.1061
15 | Pole Clamp | 7130810077 | No. | 447.76 | 37 | 16567.12 | 37 | 16567.12 | 37 | 16567.12 | 37 | 16567.12
16 | Danger Board | 7130880041 | Each | 92.6 | 29 | 2685.4 | 29 | 2685.4 | 29 | 2685.4 | 29 | 2685.4
17 | Pad Connector | 7130880006 | No. | 143.84 | 3 | 431.52 | 3 | 431.52 | 3 | 431.52 | 3 | 431.52
18 | Concreting of Pole @ 0.65 Cmt per pole and 0.2 Cmt per stay (1:3:6) | 7130200202 | Cmt. | 2970 | 21.25 | 63112.5 | 21.25 | 63112.5 | 2.4 | 7128 | 2.4 | 7128 | Material cost including GST and labour.
19 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 8 | 1211.6 | 8 | 1211.6
20 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 8 | 2707.2 | 8 | 2707.2
21 | M.S.Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30 |  | 30
| 16x40 mm | 7130620609 | Kg | 71.59 | 12 | 859.08 | 12 | 859.08 | 12 | 859.08 | 12 | 859.08
| 16x65 mm | 7130620614 | Kg | 70.4 | 12 | 844.8 | 12 | 844.8 | 12 | 844.8 | 12 | 844.8
| 16x140 mm | 7130620625 | Kg | 69.2 | 6 | 415.2 | 6 | 415.2 | 6 | 415.2 | 6 | 415.2
22 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130820029 | No. | 33.18 | 530 | 17585.4 | 530 | 17585.4 | 530 | 17585.4 | 530 | 17585.4
23 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1268578.9971 |  | 1411057.2859 |  | 659355.4018 |  | 801833.6906
24 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1075066.9467 |  | 1195811.2592 |  | 558775.7642 |  | 679520.0768 | NEW ROW ADDED
25 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 95143.4248 | 0.075 | 105829.2964 | 0.075 | 49451.6551 | 0.075 | 60137.5268 | Earlier name was - Incidental Charges @ 9%
26 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No. | 311.3185 |  |  |  |  | 29 | 9028.2364 | 29 | 9028.2364
27 | Labour charges as per Sch No. CL-3(B) |  |  |  |  | 176040.55 |  | 176040.55 |  | 158307.39 |  | 158307.39
28 | Labour charges for concreting |  | Cmt | 609.1748 | 21.25 | 12944.9644 | 21.25 | 12944.9644 | 2.4 | 1462.0195 | 2.4 | 1462.0195
29 | Transportation charges |  |  |  |  | 24065.5894 |  | 24065.5894 |  | 24065.5894 |  | 24065.5894
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 23, 25, 26, 27, 28, 29 |  |  |  |  | 197096.6907 |  | 216242.2108 |  | 112708.7865 |  | 131854.3066
31 | Total Estimated Cost excluding GST (Row 24, 25, 26, 27, 28, 29, 30) |  |  |  |  | 1580358.1659 |  | 1730933.8702 |  | 913799.4412 |  | 1064375.1455
32 | Applicable CGST @ 9% on Row 31 |  |  | 0.09 |  | 142232.2349 |  | 155784.0483 |  | 82241.9497 |  | 95793.7631
33 | Applicable SGST @ 9% on Row 31 |  |  | 0.09 |  | 142232.2349 |  | 155784.0483 |  | 82241.9497 |  | 95793.7631
34 | Total Estimated Cost including GST (Row 31+32+33) |  |  |  |  | 1864822.6358 |  | 2042501.9668 |  | 1078283.3406 |  | 1255962.6717
35 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1864823 |  | 2042502 |  | 1078283 |  | 1255963
Note on B35: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## C-3 (C)
COST SCHEDULE C-3 (C)
SCHEDULE FOR AUGMENTATION OF 1 kM OF 11 kV LINE FROM WEASEL TO RACCOON CONDUCTOR
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty | Rate | Amount
1 | Raccoon Conductor | 7130830060 | Km | 3.03 | 51309.57 | 155467.9971
2 | 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2588.62 | 2588.62
3 | G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 65.0097 | 2275.3381
4 | Stay Clamp | 7130810026 | Pair | 2 | 160.97 | 321.94
5 | Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 72.6867 | 799.5534
6 | Stay set 16 mm | 7130860032 | No | 2 | 455.31 | 910.62
7 | I-Bolt Big size | 7130620013 | No | 4 | 128.08 | 512.32
8 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 162876.3886
9 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 138030.8378 | NEW ROW ADDED
10 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 12215.7291 | Earlier name was - Incidental Charges @ 9%
11 | Dismantling Charges |  | Ckt Km | 1 | 5925.65 | 5925.65
12 | Stringing Charges as per Labour Rate Schedule AL-1 |  | Ckt Km | 1 | 11851.3 | 11851.3
13 | Transportation charges |  |  |  |  | 3667.8627
14 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 08, 10, 11, 12, 13 |  |  |  |  | 24567.1163
15 | Total Estimated Cost excluding GST (Row 09, 10, 11, 12, 13, 14) |  |  |  |  | 196258.4959
16 | Applicable CGST @ 9% on Row 15 |  |  |  | 0.09 | 17663.2646
17 | Applicable SGST @ 9% on Row 15 |  |  |  | 0.09 | 17663.2646
18 | Total Estimated Cost including GST (Row 15+16+17) |  |  |  |  | 231585.0251
19 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 231585
Note on B14: Barun Chakraborty: Earlier name was - Material Cost

## C-3 (D)
COST SCHEDULE C-3 (D)
SCHEDULE FOR AUGMENTATION OF 1 kM OF 11 kV LINE FROM WEASEL TO RABBIT CONDUCTOR
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Rabbit Conductor | 7130830057 | Km | 3.03 | 34701.37 | 105145.1511
2 | 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2588.62 | 2588.62
3 | G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 65.0097 | 2275.3381
4 | Stay Clamp | 7130810026 | Pair | 2 | 160.97 | 321.94
5 | Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 72.6867 | 799.5534
6 | Stay set 16 mm | 7130860032 | No | 2 | 455.31 | 910.62
7 | I-Bolt Big size | 7130620013 | No. | 4 | 128.08 | 512.32
8 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 112553.5426
9 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 95384.3581 | NEW ROW ADDED
10 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 8441.5157 | Earlier name was - Incidental Charges @ 9%
11 | Dismantling Charges |  | Ckt Km | 1 | 5484.055 | 5484.055
12 | Stringing Charges as per Labour Rate Schedule CL-1 |  | Ckt Km | 1 | 10968.11 | 10968.11
13 | Transportation charges |  |  |  |  | 3667.8627
14 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 08, 10, 11, 12, 13 |  |  |  |  | 17639.3857
15 | Total Estimated Cost excluding GST (Row 09, 10, 11, 12, 13, 14) |  |  |  |  | 141585.2872
16 | Applicable CGST @ 9% on Row 15 |  |  |  | 0.09 | 12742.6758
17 | Applicable SGST @ 9% on Row 15 |  |  |  | 0.09 | 12742.6758
18 | Total Estimated Cost including GST (Row 15+16+17) |  |  |  |  | 167070.6389
19 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 167071
Note on B15: Barun Chakraborty: Earlier name was - Material Cost

## C-3 (E)
COST SCHEDULE C-3 (E)
2019-20
COST PER KM OF 11 kV OVERHEAD XLPE CABLE LINE ON H - BEAM POLE WITH AVERAGE SPAN 30 MTRS.
Assumed as if cable length is 500 Mtr. in one stroke.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 33 Nos = 13467.3 Kgs | 7130601965 | Kg | 13467.3 | 53.8792 | 725607.0808
2 | 11 kV XLPE 3 Core Cable 120 sqmm (incl. sag 6%) | 7130310078 | Mtr. | 1060 | 817.6462 | 866704.9614
3 | 11 kV Heat Shrinkable Type Straight Through jointing kit for 150 sqmm XLPE Cable | 7130352040 | Set | 42 | 18791.14 | 789227.88
4 | 11 kV Straight thru' joint kit suitable for 120 sqmm Cable | 7130310062 | Set | 4 | 4224.96 | 16899.84
5 | Earth spike | 7130870010 | No. | 6 | 789.29 | 4735.74
6 | D.C.Cross Arm 5.2 Mtr. Channel | 7130810684 | Set | 2 | 8809.64 | 17619.28
7 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 2 | 2408.9 | 4817.8
8 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 31 | 2141.24 | 66378.44
9 | Eye Hook | 7130893004 | No. | 33 | 182.42 | 6019.86
10 | Stay set without stay wire 20 mm | 7130860033 | No. | 12 | 829.62 | 9955.44
11 | Stay wire 7/8 SWG 10 kg/stay | 7130860076 | Kg | 120 | 71.9816 | 8637.7968
12 | Stay clamp for H-Beam | 7130810692 | Pair | 24 | 333.29 | 7998.96
13 | Clamp for H-Beam | 7130810692 | Pair | 33 | 333.29 | 10998.57
14 | M.S.Angle 65x65x6 mm | 7130600032 | Kg | 330 | 43.1218 | 14230.2006
15 | Red Oxide Paint | 7130211158 | Ltr | 3 | 151.45 | 454.35
16 | Aluminium Paint | 7130210809 | Ltr | 3 | 338.4 | 1015.2
17 | Earthing Coil | 7130870013 | No. | 33 | 118.52 | 3911.16
18 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 66 | 78.5018 | 5181.1208
19 | Danger Board | 7130880041 | No. | 33 | 92.6 | 3055.8
20 | Concreting of Pole @ 0.65 Cmt per pole and 0.3 Cmt per stay (1:3:6) | 7130200202 | Cmt | 25.05 | 2970 | 74398.5 | Material cost including GST and labour.
21 | M.S.Nuts and Bolts |  | Kg | 40
| 16x65 mm | 7130620614 | Kg | 26 | 70.4 | 1830.4
| 16x200 mm | 7130620631 | Kg | 14 | 69.2 | 968.8
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 2640647.1804
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 2237836.5936
24 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 198048.5385
25 | Labour charges 7% of material cost |  |  |  |  | 360619.0598
26 | Labour charges for concreting |  | Cmt | 25.05 | 609.1748 | 15259.8286
27 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) | 3% of material cost |  |  |  | 108784.5665
28 | Service in lieu of Earthing Coal & Salt etc |  | No. | 33 | 2765.8829 | 91274.1353
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 22, 24, 25, 26, 27, 28 |  |  |  |  | 426829.1636
30 | Total Estimated Cost excluding GST (Row 23, 24, 25, 26, 27, 28, 29) |  |  |  |  | 3438651.8859
31 | Applicable CGST @ 9% on Row 30 |  |  |  | 0.09 | 309478.6697
32 | Applicable SGST @ 9% on Row 30 |  |  |  | 0.09 | 309478.6697
33 | Total Estimated Cost including labour charges & GST (Row 30+31+32) |  |  |  |  | 4057609.2254
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 4057609
Note on B10: 89326879: Earlier name was - 11 kV End Termination kit for XLPE Cable 150 sqmm
Note on B31: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D19: Barun Chakraborty: Earlier unit was - No.
Note on D20: Barun Chakraborty: Earlier unit was - No.

## C-4
COST SCHEDULE C-4
11 kV DP STRUCTURE ON H-BEAM / PCC POLE SUPPORT (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 53.8792 | 43976.1867
2 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No |  |  |  | 2 | 7605.2 | 15210.4
3 | DC Cross Arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | Set | 1 | 4104.29 | 4104.29 | 1 | 4104.29 | 4104.29
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 6 | 119.1 | 714.6 | 6 | 119.1 | 714.6
5 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 123.43 | 740.58 | 6 | 123.43 | 740.58
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 3 | 132.09 | 396.27 | 3 | 132.09 | 396.27
7 | Horizontal & Cross Bracing 4' center with set of 4 back clamp |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 43.1218 | 2242.3346 | 52 | 43.1218 | 2242.3346
Back Clamp for Pole
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 333.29 | 1333.16
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair |  |  |  | 4 | 300.41 | 1201.64
8 | (I) Stay set 16 mm | 7130860032 | No | 6 | 455.31 | 2731.86 | 6 | 455.31 | 2731.86
| (II) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 51 | 72.6867 | 3707.0202 | 51 | 72.6867 | 3707.0202
(III) Stay Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 6 | 333.29 | 1999.74
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair |  |  |  | 6 | 300.41 | 1802.46
9 | Concreting of pole @ 0.6 Cmt Per Pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC & @ 0.2 Cmt per stay and @ 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt | 2.5 | 2970 | 7425 | 2.3 | 2970 | 6831 | Material cost including GST and labour.
10 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 118.52 | 237.04 | 2 | 118.52 | 237.04
11 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 151.45 | 75.725 | 0.5 | 151.45 | 75.725
12 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 338.4 | 169.2 | 0.5 | 338.4 | 169.2
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073
14 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
15 | MS Nuts and Bolts |  | Kg | 6 |  |  | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795 | 0.5 | 71.59 | 35.795
| 16x200 mm | 7130620631 | Kg | 5.5 | 69.2 | 380.6 | 5.5 | 69.2 | 380.6
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 70676.0088 |  |  | 40987.4221
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 59894.9228 |  |  | 34735.1035 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 5300.7007 |  | 0.075 | 3074.0567 | Earlier name was - Incidental Charges @ 9%
19 | Labour charges for concreting |  | Cmt | 2.5 | 609.1748 | 1522.937 | 2.3 | 609.1748 | 1401.102
20 | Labour charges as per Sch No.- CL-5 |  |  |  |  | 10568.93 |  |  | 10820.47
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 3653.2451 |  |  | 3653.2451
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 16, 18, 19, 20, 21 |  |  |  |  | 11465.2277 |  |  | 7492.037
23 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22) |  |  |  |  | 92405.9632 |  |  | 61176.0142
24 | Applicable CGST @ 9% on Row 23 |  |  |  | 0.09 | 8316.5367 |  | 0.09 | 5505.8413
25 | Applicable SGST @ 9% on Row 23 |  |  |  | 0.09 | 8316.5367 |  | 0.09 | 5505.8413
26 | Total Estimated Cost including GST (Row 23+24+25) |  |  |  |  | 109039.0365 |  |  | 72187.6968
27 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 109039 |  |  | 72188
Note: | All the rates are with considering price variation clause.
Note on B34: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D11: Barun Chakraborty: Earlier unit was - No.
Note on D18: Barun Chakraborty: Earlier unit was - No.
Note on D19: Barun Chakraborty: Earlier unit was - No.
Note on D23: Barun Chakraborty: Earlier unit was - No.
Note on D24: Barun Chakraborty: Earlier unit was - No.

## C-5
COST SCHEDULE C-5
1 kM OF 11 kV LINE ON 175x85 MM R.S. JOIST WITH MAXIMUM OF 65 Mtrs. SPAN USING RABBIT AND WEASEL CONDUCTOR
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Using RABBIT Conductor |  |  | Using WEASEL Conductor
|  |  |  | Qnty | Rate | Amount | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | R.S. Joist (175X85) mm 11 Mtr. Long i.e. 19.495 kg/mtr x 11 Mtr = 214.44 kg x 12 No = 2573.28 Kgs | 7130600675 | Kg | 2573 | 44.9155 | 115567.633 | 2573 | 44.9155 | 115567.633
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 12 | 1091.69 | 13100.28 | 12 | 1091.69 | 13100.28
3 | Back Clamp for Cross Arm | 7130810361 | Pair | 12 | 319.69 | 3836.28 | 12 | 319.69 | 3836.28
4 | 11 kV Top clamp Angle type with cleat | 7130810679 | No | 12 | 306.26 | 3675.12 | 12 | 306.26 | 3675.12
5 | Earthing Set (Coil earth as per Drawing No:-G/007) | 7130870013 | No | 12 | 118.52 | 1422.24 | 12 | 118.52 | 1422.24
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 36 | 132.09 | 4755.24 | 36 | 132.09 | 4755.24
7 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 34.7014 | 107574.247
8 | ACSR conductor Weasel with 3% sag | 7130830055 | Mtr |  |  |  | 3100 | 21.0579 | 65279.397
9 | Jointing sleeves suitable for 80 Sq.mm. Al Eq. ACSR Conductor | 7130830050 | No | 6 | 37.29 | 223.74 | 6 | 37.29 | 223.74
10 | (i) Stay set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 34 | 72.6867 | 2471.3468 | 34 | 72.6867 | 2471.3468
| (iii) Stay Clamp for R.S. Joist | 7130810216 | Pair | 4 | 319.69 | 1278.76 | 4 | 319.69 | 1278.76
11 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay & pole base padding @ 0.05 cmt/pole (1:3:6) | 7130200202 | Cmt | 5.4 | 2970 | 16038 | 5.4 | 2970 | 16038 | Material cost including GST and labour.
12 | Red Oxide Paint | 7130211158 | Ltr | 2.5 | 151.45 | 378.625 | 2.5 | 151.45 | 378.625
13 | Aluminium Paint | 7130210809 | Ltr | 2.5 | 338.4 | 846 | 2.5 | 338.4 | 846
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 24 | 78.5018 | 1884.0439 | 24 | 78.5018 | 1884.0439
15 | Danger Board | 7130880041 | Each | 12 | 92.6 | 1111.2 | 12 | 92.6 | 1111.2
16 | Binding wire and tape | 7130830006 | Kg | 3 | 160.41 | 481.23 | 3 | 160.41 | 481.23
17 | MS Nuts and Bolts |  | Kg | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 5 | 71.59 | 357.95 | 5 | 71.59 | 357.95
| 16x65 mm | 7130620614 | Kg | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6
| 16x90 mm | 7130620619 | Kg | 5 | 70.4 | 352 | 5 | 70.4 | 352
18 | Guarding :-
| (i) 11 kV Guarding Channel 100x50 mm | 7130810511 | No | 1 | 2588.62 | 2588.62 | 1 | 2588.62 | 2588.62
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 65.0097 | 2275.3381 | 35 | 65.0097 | 2275.3381
| (iii) Stay Clamp | 7130810026 | Pair | 2 | 160.97 | 321.94 | 2 | 160.97 | 321.94
| (iv) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 17 | 72.6867 | 1235.6734 | 17 | 72.6867 | 1235.6734
| (v) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 2 | 455.31 | 910.62 | 2 | 455.31 | 910.62
| (vi) I- Bolt Big size | 7130620013 | No | 4 | 128.08 | 512.32 | 4 | 128.08 | 512.32
19 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 285301.2871 |  |  | 243006.4372
20 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 241780.7518 |  |  | 205937.6586 | NEW ROW ADDED
21 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 21397.5965 |  | 0.075 | 18225.4828 | Earlier name was - Incidental Charges @ 9%
22 | Labour charges for concreting |  | Cmt | 5.4 | 609.1748 | 3289.5439 | 5.4 | 609.1748 | 3289.5439
23 | Labour charges as per Sch. No. CL-6 |  |  |  |  | 58156.45 |  |  | 57244.82
24 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) |  |  |  |  | 9626.381 |  |  | 9626.381
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 19, 21, 22, 23, 24 |  |  |  |  | 47221.4073 |  |  | 41424.0831
26 | Total Estimated Cost excluding GST (Row 20, 21, 22, 23, 24, 25) |  |  |  |  | 381472.1306 |  |  | 335747.9694
27 | Applicable CGST @ 9% on Row 26 |  |  |  | 0.09 | 34332.4918 |  | 0.09 | 30217.3172
28 | Applicable SGST @ 9% on Row 26 |  |  |  | 0.09 | 34332.4918 |  | 0.09 | 30217.3172
29 | Total Estimated Cost including GST (Row 26+27+28) |  |  |  |  | 450137.1141 |  |  | 396182.6039
30 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 450137 |  |  | 396183
Note: - (1) Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
(2) All the rates are with considering price variation clause.
Note on B39: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## C-6
2019-20
COST SCHEDULE C-6
11 kV DP STRUCTURE ON 175X85 MM R.S. JOIST (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
Sl. No. | PARTICULARS | New SAP Bin Code | Unit | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | R.S. Joist (175x85 mm) 11 Mtr Long i.e. 214.44 Kg/pole @ 19.495 Kg/Mtr. i.e.214.44x2 No pole=428.89 Kgs | 7130600675 | Kg | 428.89 | 44.9155 | 19263.8174
2 | DC Cross arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | Set | 1 | 4104.29 | 4104.29
3 | 11 kV Polymer Disc Insulator | 7130820010 | No. | 6 | 119.1 | 714.6
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 123.43 | 740.58
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 132.09 | 396.27
6 | Horizontal & Cross Bracing 4' Center with set of 4 back clamp |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 43.1218 | 2242.3346
| (ii) Back Clamp for Pole | 7130810216 | Pair | 4 | 319.69 | 1278.76
7 | (i) Stay set 16 mm | 7130860032 | No | 6 | 455.31 | 2731.86
| (ii) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 51 | 72.6867 | 3707.0202
| (iii) Stay Clamp for R.S. Joist | 7130810216 | Pair | 6 | 319.69 | 1918.14
8 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay & pole base padding @ 0.05 Cmt/pole (1:3:6) | 7130200202 | Cmt | 1.9 | 2970 | 5643 | Material cost including GST and labour.
9 | Earthing Set (Coil earth as per Drawing No - G/007) | 7130870013 | No | 1 | 118.52 | 118.52
10 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 151.45 | 75.725
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 338.4 | 169.2
12 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 78.5018 | 314.0073
13 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6
14 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795
| 16x65 mm | 7130620614 | Kg | 2.5 | 70.4 | 176
| 16x200 mm | 7130620631 | Kg | 3 | 69.2 | 207.6
15 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 43930.1195
16 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 37228.9148 | NEW ROW ADDED
17 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 3294.759 | Earlier name was - Incidental Charges @ 9%
18 | Labour charges for concreting |  | Cmt | 1.9 | 609.1748 | 1157.4321
19 | Labour charges as per Sch. No. CL-7 |  |  |  |  | 10568.93
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 3653.2451
21 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 15, 17, 18, 19, 20 |  |  |  |  | 7825.5607
22 | Total Estimated Cost excluding GST (Row 16, 17, 18, 19, 20, 21) |  |  |  |  | 63728.8417
23 | Applicable CGST @ 9% on Row 22 |  |  |  | 0.09 | 5735.5958
24 | Applicable SGST @ 9% on Row 22 |  |  |  | 0.09 | 5735.5958
25 | Total Estimated Cost including GST (Row 22+23+24) |  |  |  |  | 75200.0332
26 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 75200
Note: | All the rates are with considering price variation clause.
Note on B29: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## C-7(A-1)
COST SCHEDULE C-7 (A-1)
2019-20
11/0.4 kV OUT DOOR SUB-STATION (USING PCC POLE FOR 25/63 kVA TRANSFORMER & DOUBLE WELDED R.S. JOIST 175x85 mm FOR 100/200 kVA TRANSFORMER AND SINGLE CORE PVC INSULATED CABLE)
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 54301.19 | 54301.19
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 98272.48 | 98272.48
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 129355.28 | 129355.28
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 243208.4 | 243208.4
2 | (i) 140 Kg 8.0 Mtr long PCC Pole | 7130800012 | No | 3 | 2255.2 | 6765.6 | 3 | 2255.2 | 6765.6 | -- | -- | -- | -- | -- | --
| (ii) 175x85 mm 11.0 Mtr long R.S. Joist @19.495 Kg/mtr x 9 mtr = 175.45 kg/pole x 2 No = 428.9 Kgs, For 4 No pole = 857.8 Kg | 7130600675 | Kg | [6 empty] | 857.78 | 44.9155 | 38527.6347 | 857.78 | 44.9155 | 38527.6347
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3
| 11 kV H.W. | 7130820241 | No. | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26
7 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | M.S. Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 160.97 | 643.88 | 4 | 160.97 | 643.88 | 4 | 160.97 | 643.88
10 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 1.85 | 2970 | 5494.5 | 1.85 | 2970 | 5494.5 | 1.85 | 2970 | 5494.5 | 1.85 | 2970 | 5494.5 | Material cost including GST and labour.
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
13 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 78.5018 | 471.011 | 6 | 78.5018 | 471.011 | 8 | 78.5018 | 628.0146 | 8 | 78.5018 | 628.0146
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 151.45 | 151.45 | 1 | 151.45 | 151.45 | 3 | 151.45 | 454.35 | 3 | 151.45 | 454.35
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4 | 1 | 338.4 | 338.4 | 3 | 338.4 | 1015.2 | 3 | 338.4 | 1015.2
18 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59
| 16x65 mm | 7130620614 | Kg | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6
| 16x140 mm | 7130620625 | Kg | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8
| 16x200 mm | 7130620631 | Kg | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1872.24 | 1872.24 | -- |  |  | -- |  |  | --
21 | PVC insulated Single Core Armoured cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 14.1956 | 1703.466 | -- | [5 empty] | --
ii | 70 Sqmm | 7130311010 | Mtr | -- | -- | -- | 120 | 51.4677 | 6176.1264 | 120 | 51.4677 | 6176.1264 | -- | -- | --
iii | 150 Sqmm | 7130311011 | Mtr | -- | -- | -- | -- | -- | -- | 40 | 101.1857 | 4047.4264 | 120 | 101.1857 | 12142.2792
iv | 300 Sqmm | 7130311012 | Mtr | -- | -- | -- | -- | -- | -- | -- | -- | -- | 40 | 200.8365 | 8033.4592
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15779.98 | 15779.98 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19725.8 | 19725.8
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 39449.95 | 39449.95
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 98776.0769 |  |  | 161127.7673 |  |  | 241598.5521 |  |  | 384484.1277
25 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 83708.5397 |  |  | 136548.9553 |  |  | 204744.5357 |  |  | 325834.0065 | NEW ROW ADDED
26 | Incidental Charges @7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 7408.2058 |  | 0.075 | 12084.5825 |  | 0.075 | 18119.8914 |  | 0.075 | 28836.3096 | Earlier name was - Incidental Charges @ 9%
27 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 311.3185 | 933.9555 | 3 | 311.3185 | 933.9555 | 0 | 0 | 0 | 0 | 0 | 0 |  | 192.6179
28 | Labour charges for concreting |  | Cmt | 1.85 | 609.1748 | 1126.9734 | 1.85 | 609.1748 | 1126.9734 | 1.85 | 609.1748 | 1126.9734 | 1.85 | 609.1748 | 1126.9734
29 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833
30 | Labour charges as per Sch CL-3 |  |  |  |  | 12048.82 |  |  | 12656.58 |  |  | 12656.58 |  |  | 15704.86
31 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 5537.2746 |  |  | 6130.1323 |  |  | 6130.1323 |  |  | 6130.1323
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 24, 26, 27, 28, 29, 30, 31 |  |  |  |  | 16766.1237 |  |  | 25294.7093 |  |  | 35991.2266 |  |  | 55572.5108
33 | Total Estimated Cost excluding GST (Row 25, 26, 27, 28, 29, 30, 31, 32) |  |  |  |  | 135827.576 |  |  | 203073.5717 |  |  | 287067.0227 |  |  | 441502.476
34 | Applicable CGST @ 9% on Row 33 |  |  |  | 0.09 | 12224.4818 |  | 0.09 | 18276.6215 |  | 0.09 | 25836.032 |  | 0.09 | 39735.2228
35 | Applicable SGST @ 9% on Row 33 |  |  |  | 0.09 | 12224.4818 |  | 0.09 | 18276.6215 |  | 0.09 | 25836.032 |  | 0.09 | 39735.2228
36 | Total Estimated Cost including GST (Row 33+34+35) |  |  |  |  | 160276.5396 |  |  | 239626.8146 |  |  | 338739.0868 |  |  | 520972.9216
37 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 160277 |  |  | 239627 |  |  | 338739 |  |  | 520973
Note (A) :- (1) All the rates are with considering price variation clause.
(2) Single RS Joist 175x85 mm may be used in place of PCC pole for 25/63 kVA Transformer
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer
Note on B52: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D15: Barun Chakraborty: Earlier unit was - No.

## C-7(A-2)
COST SCHEDULE C-7 (A-2)
2019-20
11/0.4 kV OUT DOOR SUB-STATION (USING PCC POLE FOR 25/63 kVA TRANSFORMER & DOUBLE WELDED RS JOIST 175x85 mm FOR 100/200 kVA TRANSFORMER AND SINGLE CORE CABLE)
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 54301.19 | 54301.19
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 98272.48 | 98272.48
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 129355.28 | 129355.28
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 243208.4 | 243208.4
2 | (i) 140 Kg 8.0 Mtr. long PCC Pole | 7130800012 | No | 3 | 2255.2 | 6765.6 | 3 | 2255.2 | 6765.6 | -- | -- | -- | -- | -- | --
| (ii) 175x85 mm 11.0 Mtr long R.S. Joist @ 19.495 Kg/mtr x 9 mtr = 175.45 kg/pole x 2 No = 428.9 Kgs, For 4 No pole = 857.8 Kg | 7130600675 | Kg | [6 empty] | 857.78 | 44.9155 | 38527.6347 | 857.78 | 44.9155 | 38527.6347
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3
5 | 11 kV H.W | 7130820241 | No | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54
7 | 11 kV DO fuse & LA mounting DC cross arm (75x40 mm) | 7130810509 | No | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26
8 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
9 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364
10 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 160.97 | 643.88 | 4 | 160.97 | 643.88 | 4 | 160.97 | 643.88
11 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 1.85 | 2970 | 5494.5 | 1.85 | 2970 | 5494.5 | 1.85 | 2970 | 5494.5 | 1.85 | 2970 | 5494.5 | Material cost including GST and labour.
12 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419
13 | Transformer mounting Cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
14 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
15 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449
16 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 78.5018 | 471.011 | 6 | 78.5018 | 471.011 | 8 | 78.5018 | 628.0146 | 8 | 78.5018 | 628.0146
17 | Red Oxide Paint | 7130211158 | Ltr | 1 | 151.45 | 151.45 | 1 | 151.45 | 151.45 | 3 | 151.45 | 454.35 | 3 | 151.45 | 454.35
18 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4 | 1 | 338.4 | 338.4 | 3 | 338.4 | 1015.2 | 3 | 338.4 | 1015.2
19 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71
20 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59
| 16x65 mm | 7130620614 | Kg | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6
| 16x140 mm | 7130620625 | Kg | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8
| 16x200 mm | 7130620631 | Kg | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346
21 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1872.24 | 1872.24 | -- |  |  | -- |  |  | --
22 | Single Core cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 14.1956 | 1703.466 | -- | [5 empty] | --
ii | 35 Sqmm | 7130310021 | Mtr |  |  |  | 80 | 29.2318 | 2338.5416
iii | 50 Sqmm | 7130311009 | Mtr |  |  |  | 40 | 37.1536 | 1486.1452 | 120 | 37.1536 | 4458.4356
iv | 70 Sqmm | 7130311010 | Mtr | -- | [5 empty] | 40 | 51.4677 | 2058.7088 | 120 | 51.4677 | 6176.1264
v | 150 Sqmm | 7130311011 | Mtr | -- | [8 empty] | 40 | 101.1857 | 4047.4264
23 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15779.98 | 15779.98 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19725.8 | 19725.8
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 39449.95 | 39449.95
24 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
25 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 98776.0769 |  |  | 158776.3277 |  |  | 237892.1437 |  |  | 374531.9421
26 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 83708.5397 |  |  | 134556.2099 |  |  | 201603.5116 |  |  | 317399.9509 | NEW ROW ADDED
27 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 7408.2058 |  | 0.075 | 11908.2246 |  | 0.075 | 17841.9108 |  | 0.075 | 28089.8957 | Earlier name was - Incidental Charges @ 9%
28 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 311.3185 | 933.9555 | 3 | 311.3185 | 933.9555 | 0 | 0 | 0 | 0 | 0 | 0
29 | Labour charges for concreting |  | Cmt | 1.85 | 609.1748 | 1126.9734 | 1.85 | 609.1748 | 1126.9734 | 1.85 | 609.1748 | 1126.9734 | 1.85 | 609.1748 | 1126.9734
30 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833
31 | Labour charges as per Sch. CL-3 |  |  |  |  | 12048.82 |  |  | 12656.58 |  |  | 12656.58 |  |  | 15704.86
32 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 5537.2746 |  |  | 6130.1323 |  |  | 6130.1323 |  |  | 6130.1323
33 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 25, 27, 28, 29, 30, 31, 32 |  |  |  |  | 16766.1237 |  |  | 24978.7346 |  |  | 35493.1779 |  |  | 54235.1859
34 | Total Estimated Cost excluding GST (Row 26, 27, 28, 29, 30, 31, 32, 33) |  |  |  |  | 135827.576 |  |  | 200588.4936 |  |  | 283149.9694 |  |  | 430984.6815
35 | Applicable CGST @ 9% on Row 34 |  |  |  | 0.09 | 12224.4818 |  | 0.09 | 18052.9644 |  | 0.09 | 25483.4972 |  | 0.09 | 38788.6213
36 | Applicable SGST @ 9% on Row 34 |  |  |  | 0.09 | 12224.4818 |  | 0.09 | 18052.9644 |  | 0.09 | 25483.4972 |  | 0.09 | 38788.6213
37 | Total Estimated Cost including GST (Row 34+35+36) |  |  |  |  | 160276.5396 |  |  | 236694.4225 |  |  | 334116.9639 |  |  | 508561.9242
38 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 160277 |  |  | 236694 |  |  | 334117 |  |  | 508562
Note (A) :- (1) All the rates are with considering price variation clause.
(2) Single RS Joist175x85 mm may be used in place of PCC pole for 25/63 kVA Transformer
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer
Note on B53: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D15: Barun Chakraborty: Earlier unit was - No.
Note on D24: 89326879: Earlier unit was - No.

## C-7(B-1)
COST SCHEDULE C-7 (B-1)
11/0.4 kV OUT DOOR SUB-STATION (USING H-BEAM POLE FOR 25 / 63 / 100 / 200 kVA TRANSFORMER AND SINGLE CORE PVC CABLE)
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 54301.19 | 54301.19
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 98272.48 | 98272.48
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 129355.28 | 129355.28
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 243208.4 | 243208.4
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3
| 11 kV H.W | 7130820241 | No. | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16
10 | Concreting of supports @ 0.6 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | Material cost including GST and labour.
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
13 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
14 | Earthing set (Pipe earth as per drg. no.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 151.45 | 151.45 | 1 | 151.45 | 151.45 | 3 | 151.45 | 454.35 | 3 | 151.45 | 454.35
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4 | 1 | 338.4 | 338.4 | 3 | 338.4 | 1015.2 | 3 | 338.4 | 1015.2
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | kg | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59
| 16x65 mm | 7130620614 | kg | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6
| 16x140 mm | 7130620625 | kg | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8
| 16x200 mm | 7130620631 | kg | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1872.24 | 1872.24 | -- |  |  | -- |  |  | --
21 | PVC insulated Single Core Armoured cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 14.1956 | 1703.466 | -- | [5 empty] | --
ii | 70 Sqmm | 7130311010 | Mtr | -- |  |  | 120 | 51.4677 | 6176.1264 | 120 | 51.4677 | 6176.1264 | --
iii | 150 Sqmm | 7130311011 | Mtr | -- | [5 empty] | 40 | 101.1857 | 4047.4264 | 120 | 101.1857 | 12142.2792
iv | 300 Sqmm | 7130311012 | Mtr | [9 empty] | 40 | 200.8365 | 8033.4592
22 | LT Distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15779.98 | 15779.98 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19725.8 | 19725.8
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 39449.95 | 39449.95
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 137261.44 |  |  | 199613.1304 |  |  | 248164.8768 |  |  | 391694.3324
25 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 116323.2542 |  |  | 169163.6698 |  |  | 210309.2176 |  |  | 331944.3495 | NEW ROW ADDED
26 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 10294.608 |  | 0.075 | 14970.9848 |  | 0.075 | 18612.3658 |  | 0.075 | 29377.0749 | Earlier name was - Incidental Charges @ 9%
27 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833
28 | Labour charges as per Sch. CL-3 |  |  |  |  | 12048.82 |  |  | 12656.58 |  |  | 12656.58 |  |  | 15704.86
29 | Labour charges for concreting |  | Cmt | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671
30 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 5537.2746 |  |  | 6130.1323 |  |  | 6130.1323 |  |  | 6130.1323
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 24, 26, 27, 28, 29, 30 |  |  |  |  | 21839.8866 |  |  | 30368.4722 |  |  | 36892.6132 |  |  | 56560.4188
32 | Total Estimated Cost excluding GST (Row 25, 26, 27, 28, 29, 30, 31) |  |  |  |  | 175620.7938 |  |  | 242866.7896 |  |  | 294177.8593 |  |  | 449293.7859
33 | Applicable CGST @ 9% on Row 32 |  |  |  | 0.09 | 15805.8714 |  | 0.09 | 21858.0111 |  | 0.09 | 26476.0073 |  | 0.09 | 40436.4407
34 | Applicable SGST @ 9% on Row 32 |  |  |  | 0.09 | 15805.8714 |  | 0.09 | 21858.0111 |  | 0.09 | 26476.0073 |  | 0.09 | 40436.4407
35 | Total Estimated Cost including GST (Row 32+33+34) |  |  |  |  | 207232.5367 |  |  | 286582.8117 |  |  | 347129.8739 |  |  | 530166.6673
36 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 207233 |  |  | 286583 |  |  | 347130 |  |  | 530167
Note (A) :- (1) All the rates are with considering price variation clause.
(2) As per requirement 315 kVA Transformer may be used against 200 kVA schedule
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer
Note on B52: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D15: Barun Chakraborty: Earlier unit was - No.
Note on D24: Barun Chakraborty: Earlier unit was - No.

## C-7 (B-1) A
COST SCHEDULE C-7 (B-1) A
RELOCATION OF 25 / 63 / 100 kVA 11/0.4 kV X-MER S/S USING H- BEAM POLE AND 3.5 CORE PVC CABLE [BASED ON COST SCHEDULE C-7 (B-1) EXCEPT TRANSFORMER COST ]
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | H-BEAM 152x152 mm; 37.1 Kg /Mtr; 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867
2 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
3 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3
4 | 11 kV H.W | 7130820241 | No. | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54
6 | 11 kV D.O. fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | kg | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16
10 | Concreting of supports @ 0.6 Cmt / pole & @ 0.2 Cmt / Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | Material cost including GST and labour.
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
13 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073
16 | Red Oxide paint | 7130211158 | Ltr | 1 | 151.45 | 151.45 | 1 | 151.45 | 151.45 | 3 | 151.45 | 454.35 | 3 | 151.45 | 454.35
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4 | 1 | 338.4 | 338.4 | 3 | 338.4 | 1015.2 | 3 | 338.4 | 1015.2
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | kg | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59
| 16x65 mm | 7130620614 | kg | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6
| 16x140 mm | 7130620625 | kg | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8
| 16x200 mm | 7130620631 | kg | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1872.24 | 1872.24 | -- |  |  | -- |  |  | --
21 | PVC insulated Single Core Armoured cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 14.1956 | 1703.466 | --
ii | 70 Sqmm | 7130311010 | Mtr | -- |  |  | 120 | 51.4677 | 6176.1264 | 120 | 51.4677 | 6176.1264
iii | 150 Sqmm | 7130311011 | Mtr | -- | [5 empty] | 40 | 101.1857 | 4047.4264 | 120 | 101.1857 | 12142.2792
iv | 300 Sqmm | 7130311012 | Mtr | [9 empty] | 40 | 200.8365 | 8033.4592
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15779.98 | 15779.98 | -- |  |  | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19725.8 | 19725.8
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 39449.95 | 39449.95
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 82960.25 |  |  | 101340.6504 |  |  | 118809.5968 |  |  | 148485.9324
25 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 70305.2966 |  |  | 85881.9071 |  |  | 100686.0989 |  |  | 125835.5359 | NEW ROW ADDED
26 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 6222.0187 |  | 0.075 | 7600.5488 |  | 0.075 | 8910.7198 |  | 0.075 | 11136.4449 | Earlier name was - Incidental Charges @ 9%
27 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833
28 | Labour charges as per Sch. CL-3 |  |  |  |  | 12048.82 |  |  | 12656.58 |  |  | 12656.58 |  |  | 15704.86
29 | Labour charges for concreting |  | Cmt | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671
30 | Transport charges upto 50 Kms average lead from Area stores to construction camp incl. site transport (Transport Sch T-1) |  |  |  |  | 5537.2746 |  |  | 6130.1323 |  |  | 6130.1323 |  |  | 6130.1323
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 24, 26, 27, 28, 29, 30 |  |  |  |  | 14543.1642 |  |  | 17163.1077 |  |  | 19510.4974 |  |  | 23879.29
32 | Total Estimated Cost excluding GST (Row 25, 26, 27, 28, 29, 30, 31) |  |  |  |  | 118233.5245 |  |  | 139009.2263 |  |  | 157470.9789 |  |  | 192263.2136
33 | Applicable CGST @ 9% on Row 32 |  |  |  | 0.09 | 10641.0172 |  | 0.09 | 12510.8304 |  | 0.09 | 14172.3881 |  | 0.09 | 17303.6892
34 | Applicable SGST @ 9% on Row 32 |  |  |  | 0.09 | 10641.0172 |  | 0.09 | 12510.8304 |  | 0.09 | 14172.3881 |  | 0.09 | 17303.6892
35 | Total Estimated Cost including GST (Row 32+33+34) |  |  |  |  | 139515.5589 |  |  | 164030.8871 |  |  | 185815.7551 |  |  | 226870.592
36 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 139516 |  |  | 164031 |  |  | 185816 |  |  | 226871
Note on B48: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D11: Barun Chakraborty: Earlier unit was - No.
Note on D20: Barun Chakraborty: Earlier unit was - No.

## C-7 (B-1) B
COST SCHEDULE -- C-7 (B-1) B
|  |  | RENOVATION OF EXISTING DISTRIBUTION TRANSFORMERS | [13 empty] | 2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER |  |  | 315 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
1 | LT Distribution Box
| 25 kVA |  | No | 0 | 0 | 0
| 63 kVA | 7131950065 | No |  |  |  | 1 | 15779.98 | 15779.98
| 100 kVA | 7131950105 | No | [6 empty] | 1 | 19725.8 | 19725.8
| 200 kVA | 7131950200 | No | [9 empty] | 1 | 39449.95 | 39449.95
| 315 kVA | 7131950207 | No | [12 empty] | 1 | 33850.45 | 33850.45
2 | PVC insulated Single Core Armoured cable
| 25 kVA (70 sq mm) | 7130311010 | Mtr | 120 | 51.4677 | 6176.1264
| 63 kVA (70 sq mm) | 7130311010 | Mtr |  |  |  | 120 | 51.4677 | 6176.1264
| 100 kVA (70 sq mm) | 7130311010 | Mtr | [6 empty] | 120 | 51.4677 | 6176.1264
| 100 kVA (150 sq mm) | 7130311011 | Mtr | [6 empty] | 40 | 101.1857 | 4047.4264
| 200 kVA (150 sq mm) | 7130311011 | Mtr | [9 empty] | 120 | 101.1857 | 12142.2792
| 200 kVA (300 sq mm) | 7130311012 | Mtr | [9 empty] | 40 | 200.8365 | 8033.4592
| 315 kVA (150 sq mm) | 7130311011 | Mtr | [12 empty] | 120 | 101.1857 | 12142.2792
| 315 kVA (300 sq mm) | 7130311012 | Mtr | [12 empty] | 40 | 200.8365 | 8033.4592
3 | Earthing set (Pipe earth as per drg no. G/008) (Material + services)
| (i) GI Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449
4 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 9149.9913 |  |  | 24929.9713 |  |  | 32923.2177 |  |  | 62599.5533 |  |  | 57000.0533
5 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 7754.2299 |  |  | 21127.0943 |  |  | 27901.0319 |  |  | 53050.4689 |  |  | 48305.1299 | NEW ROW ADDED
6 | Incidental Charges @7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 686.2493 |  | 0.075 | 1869.7478 |  | 0.075 | 2469.2413 |  | 0.075 | 4694.9665 |  | 0.075 | 4275.004 | Earlier name was - Incidental Charges @ 9%
7 | Service in lieu of earthing coal & sand |  | Nos | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833
8 | Labour charges as per Sch. CL-7 (B-1)B |  |  |  |  | 4998.8292 |  |  | 5897.6 |  |  | 7614.51 |  |  | 9080.15 |  |  | 9080.15
9 | Transportation charges |  | LS |  |  | 5537.2746 |  |  | 6130.1323 |  |  | 6130.1323 |  |  | 6130.1323 |  |  | 6130.1323
10 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 04, 06, 07, 08, 09 |  |  |  |  | 3583.7535 |  |  | 5890.6419 |  |  | 7179.3481 |  |  | 11350.3107 |  |  | 10597.8779
11 | Total Estimated Cost excluding GST (Row 05, 06, 07, 08, 09, 10) |  |  |  |  | 30858.0198 |  |  | 49212.8997 |  |  | 59591.947 |  |  | 92603.7118 |  |  | 86685.9775
12 | Applicable CGST @ 9% on Row 11 |  |  |  | 0.09 | 2777.2218 |  | 0.09 | 4429.161 |  | 0.09 | 5363.2752 |  | 0.09 | 8334.3341 |  | 0.09 | 7801.738
13 | Applicable SGST @ 9% on Row 11 |  |  |  | 0.09 | 2777.2218 |  | 0.09 | 4429.161 |  | 0.09 | 5363.2752 |  | 0.09 | 8334.3341 |  | 0.09 | 7801.738
14 | Total Estimated Cost including GST (Row 11+12+13) |  |  |  |  | 36412.4634 |  |  | 58071.2217 |  |  | 70318.4975 |  |  | 109272.3799 |  |  | 102289.4534
15 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 36412 |  |  | 58071 |  |  | 70318 |  |  | 109272 |  |  | 102289
Note on B26: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on C18: 89326879: Bin Code changed
Note on K18: 89326879: Earlier Qty. was - 10

## C-7(B-2)
COST SCHEDULE C-7 (B-2)
11/0.4 kV OUT DOOR SUB-STATION (USING H-BEAM POLE FOR 25 / 63 / 100 / 200 kVA TRANSFORMER AND SINGLE CORE CABLE)
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Energy efficient)
| (i) 25 kVA TRANSFORMER (LEVEL-2) * | 7132210018 | Each | 1 | 54301.19 | 54301.19
| (ii) 63 kVA TRANSFORMER (LEVEL-2) * | 7132210019 | Each |  |  |  | 1 | 98272.48 | 98272.48
| (iii) 100 kVA TRANSFORMER (LEVEL-2) * | 7132210020 | Each | [6 empty] | 1 | 129355.28 | 129355.28
| (iv) 200 kVA TRANSFORMER (LEVEL-2) * | 7132210021 | Each | [9 empty] | 1 | 243208.4 | 243208.4
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867 | 816.2 | 53.8792 | 43976.1867
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3 | 3 | 119.1 | 357.3
| 11 kV H.W | 7130820241 | No. | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29 | 3 | 123.43 | 370.29
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54 | 6 | 132.09 | 792.54
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26 | 1 | 1730.26 | 1730.26
7 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64 | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | kg | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364 | 20 | 43.1218 | 862.4364
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24 | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067 | 22 | 72.6867 | 1599.1067
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16 | 4 | 333.29 | 1333.16
10 | Concreting of supports @ 0.6 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole (1:3:6) | 7130200202 | Cmt | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | 2.1 | 2970 | 6237 | Material cost including GST and labour.
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419 | 34 | 43.1218 | 1466.1419
12 | Transformer mounting Cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61 | 1 | 4736.61 | 4736.61
13 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6 | 1 | 92.6 | 92.6
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72 | 9 | 222.08 | 1998.72
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449 | 15 | 65.0097 | 975.1449
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073 | 4 | 78.5018 | 314.0073
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 151.45 | 151.45 | 1 | 151.45 | 151.45 | 3 | 151.45 | 454.35 | 3 | 151.45 | 454.35
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4 | 1 | 338.4 | 338.4 | 3 | 338.4 | 1015.2 | 3 | 338.4 | 1015.2
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71 | 3 | 328.57 | 985.71
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59 | 1 | 71.59 | 71.59
| 16x65 mm | 7130620614 | Kg | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6 | 4 | 70.4 | 281.6
| 16x140 mm | 7130620625 | Kg | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8 | 4 | 69.2 | 276.8
| 16x200 mm | 7130620631 | Kg | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346 | 5 | 69.2 | 346
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1872.24 | 1872.24 | -- |  |  | -- |  |  | --
21 | Single Core cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 14.1956 | 1703.466 | -- | [5 empty] | --
ii | 35 Sqmm | 7130310021 | Mtr | -- |  |  | 80 | 29.2318 | 2338.5416
iii | 50 Sqmm | 7130311009 | Mtr | -- |  |  | 40 | 37.1536 | 1486.1452 | 120 | 37.1536 | 4458.4356
iv | 70 Sqmm | 7130311010 | Mtr | [6 empty] | 40 | 51.4677 | 2058.7088 | 120 | 51.4677 | 6176.1264
v | 150 Sqmm | 7130311011 | Mtr | [9 empty] | 40 | 101.1857 | 4047.4264
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 15779.98 | 15779.98 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 19725.8 | 19725.8
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 39449.95 | 39449.95
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8496 | 8496 | 1 | 8496 | 8496
24 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 137261.44 |  |  | 197261.6908 |  |  | 244458.4684 |  |  | 381742.1468
25 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 116323.2542 |  |  | 167170.9244 |  |  | 207168.1935 |  |  | 323510.2939 | NEW ROW ADDED
26 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 10294.608 |  | 0.075 | 14794.6268 |  | 0.075 | 18334.3851 |  | 0.075 | 28630.661 | Earlier name was - Incidental Charges @ 9%
27 | Service in lieu of Earthing Coal & Sand etc. |  | No | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833 | 1 | 8297.6833 | 8297.6833
28 | Labour Charges as per Sch CL-3 |  |  |  |  | 12048.82 |  |  | 12656.58 |  |  | 12656.58 |  |  | 15704.86
29 | Labour charges for concreting |  | Cmt | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671 | 2.1 | 609.1748 | 1279.2671
30 | Transport charges upto 50 Kms averg. lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 5537.2746 |  |  | 6130.1323 |  |  | 6130.1323 |  |  | 6130.1323
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 24, 26, 27, 28, 29, 30 |  |  |  |  | 21839.8866 |  |  | 30052.4975 |  |  | 36394.5645 |  |  | 55223.0938
32 | Total Estimated Cost excluding GST (Row 25, 26, 27, 28, 29, 30, 31) |  |  |  |  | 175620.7938 |  |  | 240381.7115 |  |  | 290260.8059 |  |  | 438775.9914
33 | Applicable CGST @ 9% on Row 32 |  |  |  | 0.09 | 15805.8714 |  | 0.09 | 21634.354 |  | 0.09 | 26123.4725 |  | 0.09 | 39489.8392
34 | Applicable SGST @ 9% on Row 32 |  |  |  | 0.09 | 15805.8714 |  | 0.09 | 21634.354 |  | 0.09 | 26123.4725 |  | 0.09 | 39489.8392
35 | Total Estimated Cost including GST (Row 32+33+34) |  |  |  |  | 207232.5367 |  |  | 283650.4195 |  |  | 342507.751 |  |  | 517755.6699
36 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 207233 |  |  | 283650 |  |  | 342508 |  |  | 517756
Note (A) :- (1) All the rates are with considering price variation clause.
(2) As per requirement 315 kVA Transformer may be used against 200 kVA schedule
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
* | ISI Marked Energy Efficiency level-2 transformer
Note on B52: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D14: Barun Chakraborty: Earlier unit was - No.
Note on D23: Barun Chakraborty: Earlier unit was - No.

## C-8
COST SCHEDULE C-8
1 Km OF 11 kV LINE ON 365 kG 11 Mtr. LONG PCC POLE USING RACCOON / DOG CONDUCTOR MAXIMUM SPAN 80 METER.
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | PCC Pole using Raccoon Conductor |  | PCC Pole using Dog Conductor
[5 empty] | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | 7605.2 | 12 | 91262.4 | 12 | 91262.4
2 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1091.69 | 12 | 13100.28 | 12 | 13100.28
3 | Stay Clamp for PCC Pole | 7130810193 | Pair | 300.41 | 12 | 3604.92 | 12 | 3604.92
4 | 11 kV Top clamp | 7130810679 | No | 306.26 | 12 | 3675.12 | 12 | 3675.12
5 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 118.52 | 12 | 1422.24 | 12 | 1422.24
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 132.09 | 36 | 4755.24 | 36 | 4755.24
7 | ACSR Raccoon Conductor with 3% sag | 7130830060 | Mtr | 51.3096 | 3100 | 159059.667
8 | ACSR Dog Conductor with 3% sag | 7130830063 | Mtr | 67.4322 |  |  | 3100 | 209039.944
9 | Jointing Sleeves suitable for Raccoon / Dog ACSR Conductor | 7130830051 | No | 145.57 | 6 | 873.42 | 6 | 873.42
10 | (I) Stay set 20 mm | 7130860033 | No | 829.62 | 4 | 3318.48 | 4 | 3318.48
| (II) Stay Wire 7/8 SWG @ 8.5 Kg per stay | 7130860076 | Kg | 71.9816 | 34 | 2447.3758 | 34 | 2447.3758
(III) Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 300.41 | 4 | 1201.64 | 4 | 1201.64
11 | Concreting of support @ 0.5 Cmt/pole, @ 0.3 Cmt/stay & base padding @ 0.05 Cmt /pole (1:3:6) | 7130200202 | Cmt | 2970 | 7.8 | 23166 | 7.8 | 23166 | Material cost including GST and labour.
12 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 2 | 302.9 | 2 | 302.9
13 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 2 | 676.8 | 2 | 676.8
14 | Barbed Wire [ @ 2 Kg/Pole ] | 7130610206 | Kg | 78.5018 | 24 | 1884.0439 | 24 | 1884.0439
15 | Danger Board | 7130880041 | Each | 92.6 | 12 | 1111.2 | 12 | 1111.2
16 | Binding wire and tape | 7130830006 | Kg | 160.41 | 6 | 962.46 | 6 | 962.46
17 | MS Nuts and Bolts |  | Kg |  | 24 |  | 24
| 16x40 mm | 7130620609 | Kg | 71.59 | 1 | 71.59 | 1 | 71.59
| 16x65 mm | 7130620614 | Kg | 70.4 | 12 | 844.8 | 12 | 844.8
| 16x140 mm | 7130620625 | Kg | 69.2 | 11 | 761.2 | 11 | 761.2
18 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 314501.7767 |  | 364482.0537
19 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 266526.9294 |  | 308883.0963 | NEW ROW ADDED
20 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 23587.6333 |  | 27336.154 | Earlier name was - Incidental Charges @ 9%
21 | Labour charges for concreting |  | Cmt | 609.1748 | 7.8 | 4751.5634 | 7.8 | 4751.5634
22 | Labour charges as per Sch No.- CL-4 |  |  |  |  | 60650.58 |  | 62473.87
23 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  | 9626.381 |  | 9626.381 |  | 9626.381
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row -18, 20, 21, 22, 23 |  |  |  |  | 51639.7418 |  | 58583.7528
25 | Total Estimated Cost excluding GST (Row 19, 20, 21, 22, 23, 24) |  |  |  |  | 416782.8288 |  | 471654.8175
26 | Applicable CGST @ 9% on Row 25 |  |  | 0.09 |  | 37510.4546 |  | 42448.9336
27 | Applicable SGST @ 9% on Row 25 |  |  | 0.09 |  | 37510.4546 |  | 42448.9336
28 | Total Estimated Cost including GST (Row 25+26+27) |  |  |  |  | 491803.738 |  | 556552.6847
29 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 491804 |  | 556553
Note: All the rates are with considering price variation clause.
Note on B33: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D12: Barun Chakraborty: Earlier unit was - No.
Note on D22: Barun Chakraborty: Earlier unit was - No.

## C-9
COST SCHEDULE C-9
1 KM OF 11 kV LINE ON H-BEAM 152x152 MM 37.1 Kg /MTR. 13.0 MTR. USING RACCOON / DOG CONDUCTOR MAXIMUM SPAN 80 MTR.
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | H-Beam using Raccoon conductor |  | H-Beam using Dog conductor
[5 empty] | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole x 12 Nos = 5788 Kgs | 7130601958 | Kg | 53.8792 | 5788 | 311852.6938 | 5788 | 311852.6938
2 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1091.69 | 12 | 13100.28 | 12 | 13100.28
3 | Back Clamp for Cross Arm | 7130810361 | Pair | 319.69 | 12 | 3836.28 | 12 | 3836.28
4 | 11 kV Top clamp | 7130810679 | No | 306.26 | 12 | 3675.12 | 12 | 3675.12
5 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 118.52 | 12 | 1422.24 | 12 | 1422.24
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 132.09 | 36 | 4755.24 | 36 | 4755.24
7 | ACSR Raccoon conductor with 3% sag | 7130830060 | Mtr | 51.3096 | 3100 | 159059.667
8 | ACSR Dog conductor with 3% sag | 7130830063 | Mtr | 67.4322 |  |  | 3100 | 209039.944
9 | Jointing Sleeves suitable for Raccoon / Dog ACSR Conductor | 7130830051 | No | 145.57 | 6 | 873.42 | 6 | 873.42
10 | (i) Stay set 20 mm | 7130860033 | No | 829.62 | 4 | 3318.48 | 4 | 3318.48
| (ii) Stay Wire 7/8 SWG @ 8.5 Kg per stay | 7130860076 | Kg | 71.9816 | 34 | 2447.3758 | 34 | 2447.3758
(iii) Stay Clamp
| (I) Stay Clamp for "H" Beam | 7130810692 | Pair | 333.29 | 4 | 1333.16 | 4 | 1333.16
11 | Concreting of support @ 0.6 Cmt/pole, @ 0.2 Cmt/stay & base padding @ 0.05 Cmt /pole (1:3:6) | 7130200202 | Cmt | 2970 | 9 | 26730 | 9 | 26730 | Material cost including GST and labour.
12 | Red Oxide paint | 7130211158 | Ltr | 151.45 | 2 | 302.9 | 2 | 302.9
13 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 2 | 676.8 | 2 | 676.8
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 78.5018 | 24 | 1884.0439 | 24 | 1884.0439
15 | Danger Board | 7130880041 | Each | 92.6 | 12 | 1111.2 | 12 | 1111.2
16 | Binding wire and tape | 7130830006 | Kg | 160.41 | 6 | 962.46 | 6 | 962.46
17 | MS Nuts and Bolts |  | Kg |  | 24 |  | 24
| 16x40 mm | 7130620609 | Kg | 71.59 | 1 | 71.59 | 1 | 71.59
| 16x65 mm | 7130620614 | Kg | 70.4 | 12 | 844.8 | 12 | 844.8
| 16x140 mm | 7130620625 | Kg | 69.2 | 11 | 761.2 | 11 | 761.2
18 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 539018.9505 |  | 588999.2275
19 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 456795.7208 |  | 499151.8877 | NEW ROW ADDED
20 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 40426.4213 |  | 44174.9421 | Earlier name was - Incidental Charges @ 9%
21 | Labour charges for concreting |  | Cmt | 609.1748 | 9 | 5482.5731 | 9 | 5482.5731
22 | Labour charges as per Sch No. CL-4 |  |  |  |  | 59068.09 |  | 60891.38
23 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  | 9624.6692 |  | 9624.6692 |  | 9624.6692
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 18, 20, 21, 22, 23 |  |  |  |  | 81702.588 |  | 88646.599
25 | Total Estimated Cost excluding GST (Row 19, 20, 21, 22, 23, 24) |  |  |  |  | 653100.0625 |  | 707972.0512
26 | Applicable CGST @ 9% on Row 25 |  |  | 0.09 |  | 58779.0056 |  | 63717.4846
27 | Applicable SGST @ 9% on Row 25 |  |  | 0.09 |  | 58779.0056 |  | 63717.4846
28 | Total Estimated Cost including GST (Row 25+26+27) |  |  |  |  | 770658.0737 |  | 835407.0204
29 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 770658 |  | 835407
Note: All the rates are with considering price variation clause.
Note on B33: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D22: Barun Chakraborty: Earlier unit was - No.

## C-9 (A)
COST SCHEDULE C-9 (A)
2019-20
ADDITIONAL (MID SPAN) POLES FOR NEW 11 kV LINE WITH RACCOON CONDUCTOR
S. No. | PARTICULARS | New SAP Bin Code | Unit | H BEAM 152X152 MM 37.10 KG / MTR 13.0 MTR LONG
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm; 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole | 7130601958 | kg | 482.3 | 53.8792 | 25985.9285
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 1 | 1091.69 | 1091.69
3 | Cross Arm Clamp
| (i) Stay Clamp For "H" Beam | 7130810692 | Pair | 1 | 333.29 | 333.29
4 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 1 | 306.26 | 306.26
5 | Earthing Set (Coil earth as per Drawing No:-G/007 | 7130870013 | No | 1 | 118.52 | 118.52
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 132.09 | 396.27
7 | Concreting of supports H-Beam @ 0.6 Cmt. Per Pole & @ 0.2 Cmt. Per Stay and 0.05 Cmt per pole for base padding (1:3:6) | 7130200202 | Cmt. | 0.65 | 2970 | 1930.5 | Material cost including GST and labour.
8 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 78.5018 | 157.0037
9 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6
10 | MS Nuts and Bolts
| 16x40 mm | 7130620609 | Kg | 0.25 | 71.59 | 17.8975
| 16x65 mm | 7130620614 | Kg | 0.6 | 70.4 | 42.24
| 16x140 mm | 7130620625 | Kg | 0.55 | 69.2 | 38.06
11 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 30510.2597
12 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 25856.1523 | NEW ROW ADDED
13 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 2288.2695 | Earlier name was - Incidental Charges @ 9%
14 | Labour charges for concreting |  | Cmt | 0.65 | 609.1748 | 395.9636
15 | Labour charges as per Sch No.- CL-4 (revised based on one pole) |  |  |  |  | 2831.7851
16 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) - Taken 5% of |  |  |  |  | 481.3222
17 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 11, 13, 14, 15, 16 |  |  |  |  | 4563.45
18 | Total Estimated Cost excluding GST (Row 12, 13, 14, 15, 16, 17) |  |  |  |  | 36416.9426
19 | Applicable CGST @ 9% on Row 18 |  |  |  | 0.09 | 3277.5248
20 | Applicable SGST @ 9% on Row 18 |  |  |  | 0.09 | 3277.5248
21 | Total Estimated Cost including GST (Row 18+19+20) |  |  |  |  | 42971.9923
22 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 42972
Note on B22: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D11: Barun Chakraborty: Earlier unit was - No.

## C-10
COST SCHEDULE C-10
AUGMENTATION OF 11/0.4 kV SUB-STATION CAPACITY (ASSUMING 25 YEARS OF LIFE & 10 YEARS IN SERVICE)
2019-20
S. No. | PARTICULARS | Bin CodeNo. | New SAP Bin Code | Unit | Rate | 25 kVA to 63 kVA |  | 63 kVA to 100 kVA |  | 100 kVA to 200 kVA
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 11/0.4 kV 63 kVA X-mer (LEVEL-2) * |  | 7132210019 | Each | 98272.48 | 1 | 98272.48
2 | 11/0.4 kV 100 kVA X-mer (LEVEL-2) * |  | 7132210020 | Each | 129355.28 |  |  | 1 | 129355.28
3 | 11/0.4 kV 200 kVA X-mer (LEVEL-2) * |  | 7132210021 | Each | 243208.4 |  |  |  |  | 1 | 243208.4
4 | R.S. Joist (175X85) mm 11 Mtr. Long i.e. 19.495 kg/mtr x 11 mtr = 214.44 kg x 4 No = 857.8 Kgs |  | 7130600675 | Kg | 44.9155 |  |  | 857.8 | 38528.5331 | 857.8 | 38528.5331
5 | (i) Stay set 16 mm | 7130860032201 | 7130860032 | No | 455.31 |  |  | 4 | 1821.24 | 4 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077103 | 7130860077 | Kg | 72.6867 |  |  | 22 | 1599.1067 | 22 | 1599.1067
| (iii) Stay Clamp for R.S. Joist | 7130810026301 | 7130810216 | Pair | 319.69 |  |  | 4 | 1278.76 | 4 | 1278.76
6 | Concreting of support @ 0.3 Cmt/pole, @ 0.2 Cmt/stay & base padding @ 0.05 Cmt/pole (1:3:6) |  | 7130200202 | Cmt | 2970 |  |  | 1.5 | 4455 | 1.5 | 4455 | Material cost including GST and labour.
7 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013401 | 7130870013 | No | 118.52 |  |  | 1 | 118.52 | 1 | 118.52
8 | Red Oxide Paint | 7130211158904 | 7130211158 | Ltr | 151.45 |  |  | 1 | 151.45 | 1 | 151.45
9 | Aluminium Paint | 7130210809004 | 7130210809 | Ltr | 338.4 |  |  | 1 | 338.4 | 1 | 338.4
10 | Barbed Wire [@ 2 Kg/Pole] | 7130407183901 | 7130610206 | Kg | 78.5018 |  |  | 8 | 628.0146 | 8 | 628.0146
11 | MS Nuts & Bolts |  |  | Kg |  | 14 |  | 14 |  | 14
| 16x40 mm | 7130620609003 | 7130620609 | Kg | 71.59 | 1 | 71.59 | 1 | 71.59 | 1 | 71.59
| 16x65 mm | 7130620614003 | 7130620614 | Kg | 70.4 | 4 | 281.6 | 4 | 281.6 | 4 | 281.6
| 16x140 mm | 7130620625403 | 7130620625 | Kg | 69.2 | 4 | 276.8 | 4 | 276.8 | 4 | 276.8
| 16x200 mm | 7130620631603 | 7130620631 | Kg | 69.2 | 5 | 346 | 5 | 346 | 5 | 346
12 | 70 Sqmm Single core XLPE insulated unarmoured Al. Conductor cable |  | 7130310007 | Mtr | 56.4044 | 120 | 6768.5292 | 120 | 6768.5292 | 120 | 6768.5292
13 | 150 Sqmm Single core XLPE insulated unarmoured Al. Conductor cable |  | 7130310041 | Mtr | 109.4763 |  |  |  |  | 40 | 4379.052
14 | 11 kV A.B. Switch |  | 7131930221 | Each | 8496 |  |  |  |  | 1 | 8496
15 | LT Distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950063801 | 7131950065 | No | 15779.98 | 1 | 15779.98
ii | 100 kVA | 7131950105901 | 7131950105 | No | 19725.8 |  |  | 1 | 19725.8
iii | 200 kVA | 7131950200001 | 7131950200 | No | 39449.95 |  |  |  |  | 1 | 39449.95
16 | SUB TOTAL-1 (Material cost including GST) | [5 empty] | 121796.9792 |  | 205744.6236 |  | 352196.9456
17 | Material cost excluding GST (Sub Total-1/1.18) | [5 empty] | 103217.779 |  | 174359.8505 |  | 298471.9878 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 |  | 9134.7734 |  | 15430.8468 |  | 26414.7709 | Earlier name was - Incidental Charges @ 9%
19 | Labour charges as per Sch. CL-10(B) | [5 empty] | 19735.81 |  | 22516.3 |  | 25046.45
20 | Labour charges for concreting |  |  | Cmt | 609.1748 |  |  | 1.5 | 913.7622 | 1.5 | 913.7622
21 | Transportation charges | [5 empty] | 5537.2746 |  | 6130.1531 |  | 6130.1531
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 16, 18, 19, 20, 21 | [5 empty] | 19525.6047 |  | 31341.9607 |  | 51337.7602
23 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22) | [5 empty] | 157151.2416 |  | 250692.8733 |  | 408314.8843
24 | Applicable CGST @ 9% on Row 23 |  |  |  | 0.09 |  | 14143.6117 |  | 22562.3586 |  | 36748.3396
25 | Applicable SGST @ 9% on Row 23 |  |  |  | 0.09 |  | 14143.6117 |  | 22562.3586 |  | 36748.3396
26 | Total Estimated Cost including GST (Row 23+24+25) | [5 empty] | 185438.4651 |  | 295817.5905 |  | 481811.5634
27 | Cost of X-mer (Cost of X-mer to be taken at the time of procurement i.e before 10 years)
| (i) 25 kVA |  |  | No |  | 1 | 49500
| (ii) 63 kVA |  |  | No |  |  |  | 1 | 67965.1
| (iii) 100 kVA |  |  | No | [5 empty] | 1 | 86809.66
28 | (-) 10% Irreducible cost | [5 empty] | 4950 |  | 6796.51 |  | 8680.966
29 | (-) 10 year life @ 4% per year | [5 empty] | 17820 |  | 24467.436 |  | 31251.4776
30 | Depreciated cost of X-mer after addition to 10% irreducible cost | [5 empty] | 31680 |  | 43497.664 |  | 55558.1824
31 | (-) Cost of old X-mer assuming 25 years of life & 10 years in service | [5 empty] | 31680 |  | 43497.664 |  | 55558.1824
32 | Net cost of augmentation | [5 empty] | 153758.4651 |  | 252319.9265 |  | 426253.381
33 | Net cost of augmentation (R/Off) | [5 empty] | 153758 |  | 252320 |  | 426253
All the rates are with considering price variation clause.
* | ISI Marked Energy Efficiency level-2 transformer
Note on B34: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on B46: Barun Chakraborty: Rate in 2008-09
Note on B47: Barun Chakraborty: Rate in 2008-09
Note on B48: Barun Chakraborty: Rate in 2008-09

## C-11
COST SCHEDULE C-11
11/0.4 kV OUT DOOR SUB-STATION (16 kVA TRANSFORMER)
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | 16 kVA, 11/.4 kV X' MER
|  |  |  | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient) 16 kVA (LEVEL-2) * Aluminium Wound | 7132210017 | No | 1 | 48638.84 | 48638.84
2 | 140 Kg 8.0 Mtr. long PCC Pole | 7130800012 | No | 3 | 2255.2 | 6765.6
3 | DC Cross arm of 100x50x6 mm 8' Center 2.7 Mtr. long | 7130810517 | Set | 1 | 4736.61 | 4736.61
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 119.1 | 357.3
5 | 11 kV Strain H/W | 7130820241 | Set | 3 | 123.43 | 370.29
6 | 11 kV D.O. Fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 1730.26 | 1730.26
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1177.88 | 3533.64
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 43.1218 | 862.4364
9 | (i) Stay set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067
| (iii) Stay Clamp | 7130810026 | Pair | 4 | 160.97 | 643.88
10 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base pad @ 0.05 Cmt/pole (1:3:6) | 7130200202 | Cmt | 1.85 | 2970 | 5494.5 | Material cost including GST and labour.
11 | Transformer belting with 50x50x6 mm angle with 2 Cross fixing channel. | 7130600023 | Kg | 34 | 43.1218 | 1466.1419
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 4736.61 | 4736.61
13 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 78.5018 | 471.011
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 151.45 | 151.45
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 328.57 | 985.71
19 | MS Nuts & Bolts |  | Kg | 14
| 16x40 mm | 7130620609 | Kg | 1 | 71.59 | 71.59
| 16x65 mm | 7130620614 | Kg | 4 | 70.4 | 281.6
| 16x140 mm | 7130620625 | Kg | 4 | 69.2 | 276.8
| 16x200 mm | 7130620631 | Kg | 5 | 69.2 | 346
20 | TPN switch fuse unit (32 Amps) | 7131920253 | No | 1 | 779.71 | 779.71
21 | 16 Sqmm single core PVC insulated Cable | 7130311008 | Mtr | 120 | 14.1956 | 1703.466
22 | CT operated electronic static meters 100/5 Amp. With data storage. | 7131310997 | No | 1 | 1805 | 1805 | Name changed
23 | LT CT 50/5 Amp. | 7132230016 | No | 4 | 356.08 | 1424.32
24 | Meter Box (GI plain sheet) for 3 Phase LT CT operated meter. | 7132406420 | No | 1 | 2662.68 | 2662.68
25 | Copper control cable 4 core 2.5 sq.mm Unarmoured | 7130310654 | Mtr | 12 | 68.1431 | 817.7167
26 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 97938.3736
27 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 82998.6217 | NEW ROW ADDED
28 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 7345.378 | Earlier name was - Incidental Charges @ 9%
29 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 311.3185 | 933.9555
30 | Service in lieu of Earthing Coal & Sand etc. |  | No | 1 | 8297.6833 | 8297.6833
31 | Labour charges as per Sch. CL-3 |  |  |  |  | 12048.82
32 | Labour charges for concreting |  | Cmt | 1.85 | 609.1748 | 1126.9734
33 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) |  |  |  |  | 5537.2746
34 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 26, 28, 29, 30, 31, 32, 33 |  |  |  |  | 16653.5573
35 | Total Estimated Cost excluding GST (Row 27, 28, 29, 30, 31, 32, 33, 34) |  |  |  |  | 134942.2638
36 | Applicable CGST @ 9% on Row 35 |  |  |  | 0.09 | 12144.8037
37 | Applicable SGST @ 9% on Row 35 |  |  |  | 0.09 | 12144.8037
38 | Total Estimated Cost including GST (Row 35+36+37) |  |  |  |  | 159231.8713
39 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 159232
Note: (1) All the rates are with considering price variation clause.
Note on B39: Barun Chakraborty: Earlier name was - CT operated electronic static meter 100/5 Amp.
Note on B43: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D12: Barun Chakraborty: Earlier unit was - No.
Note on D20: 89326879: Earlier unit was - No.

## C-12
COST SCHEDULE C-12
SCHEDULE FOR 11 kV UNDERGROUND CABLE CROSSING UNDER EXISTING RAILWAY TRACK / ROAD FOR 60 MTR. LONG RAIL / ROAD CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | Using HDD Technique (for Railway works) on 3x240 sq.mm UG XLPE Cable | Using HDD Technique (for Road crossing works) on 3x240 sq.mm UG XLPE Cable
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD; 6 Mtr long | 7132461004 | Mtr | 1183.33 | 120 | 141999.6 | 141999.6
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 430.3 | 18 | 7745.4 | 7745.4
3 | 11 kV XLPE 240 sqmm 3 core UG Cable | 7130310079 | Mtr | 990.668 | 180 | 178320.2454 | 178320.2454
4 | End terminating jointing kit for 240 sqmm XLPE cable | 7130352041 | Set | 20551.36 | 4 | 82205.44 | 82205.44
5 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1113.58 | 24 | 26725.92 | 26725.92
6 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
7 | M.S.Flat (50x6) mm | 7130600173 | kg | 46.9271 | 100 | 4692.714 | 4692.714
8 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No. | 556 | 4 | 2224 | 2224
9 | Cable covering tiles 250x250x40 mm | 7130201343 | Each | 33 | 80 | 2640 | 2640
10 | Sand | 7132498006 | Cmt | 892.5 | 1.2 | 1071 | 1071
11 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 328.57 | 6 | 1971.42 | 1971.42
12 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 51.3096 | 18 | 923.5723 | 923.5723
13 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 275.5 | 6 | 1653 | 1653
14 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 876.17 | 10 | 8761.7 | 8761.7
15 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Railway authorities including liaisoning work etc. |  | LS | LS | LS | 25000
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 491934.0117 | 466934.0117
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 416893.2302 | 395706.7895 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 36895.0509 | 35020.0509 | Earlier name was - Incidental Charges @ 9%
19 | Service in lieu of Earthing Coal & Sand etc |  | No | 2765.8829 | 10 | 27658.8289 | 27658.8289
20 | Labour Charges for laying of HDPE Pipe (using HDD Technique ** ) as per Revised Labour Schedule AL-5 |  |  |  |  | 357953 | 357953
21 | Labour Charges for excavation of cable trench beyond the length of HDPE Pipe upto DP Structure |  | Cmt | 267.4136 | 12 | 3208.9636 | 3208.9636 |  | (20 Mx1 Mx0.6 M)
22 | Transportation Charges |  |  |  |  | 80692.9991 | 80692.9991
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 16, 18, 19, 20, 21, 22 |  |  |  |  | 124792.8568 | 121433.4818
24 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22, 23) |  |  |  |  | 1048094.9295 | 1021674.1139
25 | Applicable CGST @ 9% on Row 24 |  |  | 0.09 |  | 94328.5437 | 91950.6702
26 | Applicable SGST @ 9% on Row 24 |  |  | 0.09 |  | 94328.5437 | 91950.6702
27 | Charges payable to Railway including supervision charges etc. | 15% |  |  |  | 157214.2394 |  | Name Changed Earlier-Way leave charges payable to Railway including supervision
28 | Municipality Charges payable to Local bodies as per Demand note |  | LS
29 | Total Estimated Cost per 60 Mtr including GST [Row 24+25+26+(27or 28)] |  |  |  |  | 1393966.2563 | 1205575.4544
30 | Total Estimated Cost per 60 Mtr including GST (Rounded off) |  |  |  |  | 1393966 | 1205575
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
** | Horizontal Directional Drilling (HDD) Technique
The rates mentioned at S.No.1, 2 & 3 are applicable for 60 Mtr Corridor of Railway crossing. Estimate may be prepared based on actual length of corridor.
*** | The charges to be paid for according railway permission shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note on B24: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D17: 89326879: Earlier unit was - No.
Note on E14: 89326879: Assuming 2 kg M-seal @ Rs 450/- per kg + PVC Plate 10 mm thick
***
Fill appropriate cost

## C-13
COST SCHEDULE C-13
SINGLE POLE MOUNTED LOW CAPACITY THREE PHASE 11/0.4 kV DISTRIBUTION TRANSFORMER SUB-STATION
2019-20
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | 16 kVA Three Phase
[5 empty] | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient) 16 kVA (LEVEL-2) * Aluminium Wound | 7132210017 | No. | 1 | 48638.84 | 48638.84
2 | 200 Kg 8.0 Meter long PCC Pole | 7130800033 | No. | 1 | 2552.95 | 2552.95
3 | 11 kV 'V' Cross arm with clamp (instead of DC Cross arm) | 7130810495 | No | 1 | 1091.69 | 1091.69
4 | 11 kV Top clamp with cleat | 7130810679 | No | 1 | 306.26 | 306.26
5 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 3 | 132.09 | 396.27
6 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 119.1 | 357.3
7 | 11 kV Strain Hardware | 7130820241 | No | 3 | 123.43 | 370.29
8 | 11 kV D.O. Fuse and L.A. mounting DC channel size 75x40x6 mm length 860 mm | 7130810509 | No | 1 | 1730.26 | 1730.26
9 | 11 kV D.O. Fuse unit for Three phase X-mer | 7131930412 | Each | 3 | 1177.88 | 3533.64
10 | MS angle for transformer clamping set size 50x50x6 mm | 7130600023 | Kg | 20 | 43.1218 | 862.4364
11 | (i) Stay set 16 mm | 7130860032 | No | 4 | 455.31 | 1821.24
| (ii) Stay wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 72.6867 | 1599.1067
| (iii) Stay clamp | 7130810026 | Pair | 4 | 160.97 | 643.88
12 | Concreting of supports @ 0.5 Cmt per pole and @ 0.2 Cmt per stay & base padding @ 0.05 Cmt/pole (1:3:6) | 7130200202 | Cmt | 1.35 | 2970 | 4009.5 | Material cost including GST and labour.
13 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | Set | 2 | 4736.61 | 9473.22
14 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 78.5018 | 157.0037
16 | Earthing set (pipe earth as per drawing)
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 9 | 222.08 | 1998.72
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 15 | 65.0097 | 975.1449
17 | Red Oxide Paint | 7130211158 | Ltr | 1 | 151.45 | 151.45
18 | Aluminium Paint | 7130210809 | Ltr | 1 | 338.4 | 338.4
19 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 328.57 | 985.71
20 | M.S. Nuts and Bolts
| (i) 16x40 mm | 7130620609 | Kg | 1 | 71.59 | 71.59
| (ii) 16x65 mm | 7130620614 | Kg | 4 | 70.4 | 281.6
| (iii) 16x140 mm | 7130620625 | Kg | 4 | 69.2 | 276.8
| (iv) 16x200 mm | 7130620631 | Kg | 5 | 69.2 | 346
21 | TPN switch fuse unit (32 Amps) | 7131920253 | No | 1 | 779.71 | 779.71
22 | XLPE insulated 4 core 16 sq mm armoured cable for 3 phase X-mer | 7130311084 | Mtr. | 30 | 60.69 | 1820.7012
23 | LT Feeder Piller box 1 phase 8 Way for distribution of service connection | 7130890004 | No. | 1 | 5315.68 | 5315.68
24 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 90977.9929
25 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 77099.994 | NEW ROW ADDED
26 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 6823.3495 | Earlier name was - Incidental Charges @ 9%
27 | Back filling of poles with boulders @ 0.3 Cmt per pole. |  | No. | 1 | 311.3185 | 311.3185
28 | Labour charges for concreting |  | Cmt | 1.35 | 609.1748 | 822.386
29 | Labour charges as per Schedule No. CL-8 (G-1) |  |  |  |  | 8329.34
30 | Transport charges upto 50 Kms. Average lead from area store to const. camping site transport |  |  |  |  | 3195.4418
31 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 24, 26, 27, 28, 29, 30 |  |  |  |  | 13807.4786
32 | Total Estimated Cost excluding GST (Row 25, 26, 27, 28, 29, 30, 31) |  |  |  |  | 110389.3083
33 | Applicable CGST @ 9% on Row 32 |  |  |  | 0.09 | 9935.0377
34 | Applicable SGST @ 9% on Row 32 |  |  |  | 0.09 | 9935.0377
35 | Total Estimated Cost including GST (Row 32+33+34) |  |  |  |  | 130259.3837
36 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 130259
* | ISI Marked Energy Efficiency level-2 transformer
Note on B23: 89326879: Earlier name was - Transformer mounting DC Cross arm size 65x65x6 channel length 800 mm
Note on B40: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D23: Barun Chakraborty: Earlier unit was - No.

## C-14
COST SCHEDULE C-14
2019-20
PLINTH MOUNTED 11/0.4 kV OUTDOOR SUB-STATION
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | 63 kVA X-MER |  | 100 kVA X-MER |  | 200 kVA X-MER
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | RS Joist (175X85) mm 11 Mtr Long i.e. 19.495 Kg/mtr x 11 mtr. = 214.44 kg x 2 No = 428.89 Kgs | 7130600675 | Kg | 44.9155 | 429 | 19268.7581 | 429 | 19268.7581
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole x 2 Nos = 964.6 Kgs | 7130601958 | Kg | 53.8792 |  |  |  |  | 964.6 | 51971.857
3 | Transformer 11/0.4 kV (Energy efficient)
| 63 kVA (LEVEL-2) * | 7132210019 | Each | 98272.48 | 1 | 98272.48
| 100 kVA (LEVEL-2) * | 7132210020 | Each | 129355.28 |  |  | 1 | 129355.28
| 200 kVA (LEVEL-2) * | 7132210021 | Each | 243208.4 |  |  |  |  | 1 | 243208.4
4 | DC Cross arm 100x50 mm 8' Centre | 7130810517 | Set | 4736.61 | 1 | 4736.61 | 1 | 4736.61 | 1 | 4736.61
5 | 11 kV Polymer Disc Insulator | 7130820010 | No | 119.1 | 3 | 357.3 | 3 | 357.3 | 3 | 357.3
| 11 kV H.W. | 7130820241 | No | 123.43 | 3 | 370.29 | 3 | 370.29 | 3 | 370.29
6 | 11 kV DO fuse & LA mounting DC cross arm (75 x 40 mm) | 7130810509 | No | 1730.26 | 1 | 1730.26 | 1 | 1730.26 | 1 | 1730.26
7 | 11 kV DO Fuse Unit | 7131930412 | Each | 1177.88 | 3 | 3533.64 | 3 | 3533.64 | 3 | 3533.64
8 | M.S. Angle 50x50x6 mm | 7130600023 | Kg | 43.1218 | 20 | 862.4364 | 20 | 862.4364 | 20 | 862.4364
9 | (i) Stay set 16 mm | 7130860032 | No | 455.31 | 4 | 1821.24 | 4 | 1821.24 | 4 | 1821.24
| (ii) Stay wire 7/10 SWG (7.5 Kg each) | 7130860077 | Kg | 72.6867 | 30 | 2180.6001 | 30 | 2180.6001 | 30 | 2180.6001
| (iii) Stay clamp for R.S.Joist | 7130810216 | Pair | 319.69 | 4 | 1278.76 | 4 | 1278.76
| (iv) Stay clamp for H-Beam | 7130810692 | Pair | 333.29 |  |  |  |  | 4 | 1333.16
10 | Concreting of support [0.3 Cmt per RSJ, 0.5 Cmt per H-Beam, 0.2 Cmt per stay, 9 cub.m. (1.5x1.5x4 m) for X-mer plinth] (1:3:6) | 7130200202 | Kg. | 2970 | 10.4 | 30888 | 10.4 | 30888 | 10.8 | 32076 | Material cost including GST and labour.
11 | Danger Board | 7130880041 | Each | 92.6 | 1 | 92.6 | 1 | 92.6 | 1 | 92.6
12 | Earthing set pipe carth
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 222.08 | 9 | 1998.72 | 9 | 1998.72 | 9 | 1998.72
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 65.0097 | 15 | 975.1449 | 15 | 975.1449 | 15 | 975.1449
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 78.5018 | 4 | 314.0073 | 4 | 314.0073 | 4 | 314.0073
14 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 2 | 302.9 | 2 | 302.9 | 2 | 302.9
15 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 2 | 676.8 | 2 | 676.8 | 2 | 676.8
16 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 328.57 | 3 | 985.71 | 3 | 985.71 | 3 | 985.71
17 | M.S. Nuts & Bolts |  |  |  | 14 |  | 14 |  | 17
| 16x40 mm | 7130620609 | Kg | 71.59 | 1 | 71.59 | 1 | 71.59 | 1 | 71.59
| 16x65 mm | 7130620614 | Kg | 70.4 | 4 | 281.6 | 4 | 281.6 | 4 | 281.6
| 16x140 mm | 7130620625 | Kg | 69.2 | 4 | 276.8 | 4 | 276.8 | 5 | 346
| 16x200 mm | 7130620631 | Kg | 69.2 | 5 | 346 | 5 | 346 | 7 | 484.4
18 | PVC insulated Single Core Armoured cable
| 70 Sqmm | 7130311010 | Mtr | 51.4677 | 160 | 8234.8352 | 120 | 6176.1264
| 150 sqmm | 7130311011 | Mtr | 101.1857 |  |  | 40 | 4047.4264 | 120 | 12142.2792
| 300 sqmm | 7130311012 | Mtr | 200.8365 |  |  |  |  | 40 | 8033.4592
19 | LT Distribution Box for X-mer
| 63 kVA | 7131950065 | No. | 15779.98 | 1 | 15779.98
| 100 kVA | 7131950105 | No. | 19725.8 |  |  | 1 | 19725.8
| 200 kVA | 7131950200 | No. | 39449.95 |  |  |  |  | 1 | 39449.95
20 | Stay Clamp for (i) R.S.Joist 175x85 mm | 7130810216 | Pair | 319.69 | 14 | 4475.66 | 14 | 4475.66
| (ii) Stay clamp for H-Beam | 7130810692 | Pair | 333.29 |  |  |  |  | 14 | 4666.06
21 | 11 kV AB Switch | 7131930221 | Each | 8496 |  |  | 1 | 8496 | 1 | 8496
22 | ACSR Conductor Rabbit | 7130830057 | Mtr | 34.7014 | 30 | 1041.0411 | 30 | 1041.0411 | 30 | 1041.0411
23 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 201153.7631 |  | 246667.1007 |  | 424540.0552
24 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 170469.2908 |  | 209039.9158 |  | 359779.7078 | NEW ROW ADDED
25 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 15086.5322 |  | 18500.0326 |  | 31840.5041 | Earlier name was - Incidental Charges @ 9%
26 | Labour Charges as per Sch. CL-9. |  |  |  |  | 26078.47 |  | 28790.73 |  | 31598.57
27 | Labour charges for concreting |  | Cmt | 609.1748 | 10.4 | 6335.4179 | 10.4 | 6335.4179 | 10.8 | 6579.0878
28 | Transportation Charges |  |  |  |  | 7669.0665 |  | 7669.0665 |  | 8947.239
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 23, 25, 26, 27, 28 |  |  |  |  | 32040.4062 |  | 38495.2934 |  | 62938.182
30 | Total Estimated Cost excluding GST (Row 24, 25, 26, 27, 28, 29) |  |  |  |  | 257679.1835 |  | 308830.4562 |  | 501683.2908
31 | Applicable CGST @ 9% on Row 30 |  |  | 0.09 |  | 23191.1265 |  | 27794.7411 |  | 45151.4962
32 | Applicable SGST @ 9% on Row 30 |  |  | 0.09 |  | 23191.1265 |  | 27794.7411 |  | 45151.4962
33 | Total Estimated Cost including GST (Row 30+31+32) |  |  |  |  | 304061.4365 |  | 364419.9383 |  | 591986.2831
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 304061 |  | 364420 |  | 591986
* | ISI Marked Energy Efficiency level-2 transformer
Note on B50: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D14: Barun Chakraborty: Earlier unit was - No.
Note on D23: Barun Chakraborty: Earlier unit was - No.
Note on D47: Barun Chakraborty: Earlier unit was - No.

## C-15
COST SCHEDULE C-15
SCHEDULE FOR LAYING OF 1 kM 11 kV CABLE DIRECT IN GROUND SINGLE CABLE LINE USING OPEN TRENCH METHOD
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x95 sq.mm AB XLPE Cable | 3x240 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 11 kV XLPE 95 sqmm 3 core UG Cable | 7130310077 | Mtr | 548.3137 | 1040 | 570246.2272
2 | 11 kV XLPE 240 sqmm 3 core UG Cable | 7130310079 | Mtr | 990.668 | 1040 |  | 1030294.7512
3 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 95 sq.mm., 11 kV Underground XLPE cable | 7130352039 | Set | 14192.35 | 2 | 28384.7
4 | Straight through heat shrinkable cable jointing kit with lugs for 3 Core 240 sq.mm., 11 kV Underground XLPE cable | 7130352041 | Set | 20551.36 | 2 |  | 41102.72
5 | End terminating jointing kit upto 95 sqmm XLPE cable | 7130352043 | Set | 7377.45 | 2 | 14754.9
6 | End terminating jointing kit for 240 sqmm XLPE cable | 7130352044 | Set | 8905.83 | 2 |  | 17811.66
7 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 1113.58 | 10 | 11135.8 | 11135.8
8 | G.I.Wire 8 SWG (for earthing connect to LA & cable) | 7130870043 | Kg | 65.0097 | 5 | 325.0483 | 325.0483
9 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 20 | 11120 | 11120
10 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 33 | 4000 | 132000 | 132000
11 | River Sand (For 10 cm. base & 10 cm. filling of trench above cable & then cable covering tiles over complete length of trench) | 7132498006 | Cmt | 892.5 | 150 | 133875 | 133875
12 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 328.57 | 6 | 1971.42 | 1971.42
13 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 51.3096 | 18 | 923.5723 | 923.5723
14 | Aluminium T-clamp suitable for Dog / Raccoon conductor for connecting L.A. | 7130830585 | No. | 275.5 | 6 | 1653 | 1653
15 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. | 7130642039 | No | 876.17 | 2 | 1752.34 | 1752.34
16 | M.S. Nuts & Bolts | Fill the appropriate Bin Code | Kg | 72.78 | 3 | 218.34 | 218.34
17 | Bhatta brick | 7132498054 | No | 6.09 | 4400 | 26796 | 26796
18 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Road constructing authorities including liaisoning work etc. [ To be provisioned as per actual requirement ] |  | LS | LS | LS | 25000 | 25000
19 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 960156.3478 | 1435979.6518
20 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 813691.8201 | 1216931.9083 | NEW ROW ADDED
21 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 72011.7261 | 107698.4739 | Earlier name was - Incidental Charges @ 9%
22 | Service in lieu of Earthing Coal & Sand etc |  | No | 2765.8829 | 10 | 27658.8289 | 27658.8289
23 | Labour Charges - |  | Mtr |  |  | 355189.8884 | 355189.8884
i | Cable trench excavation [(1.0 Mx0.75 Mx1.2 M) LxWxD] |  | Cmt | 267.4139 | 900 | 240672.51 | 240672.51
ii | Spreading of sand for base pad of cable (10 cm thick & 10 cm. above cable) |  | Mtr | 14.112 | 1000 | 14112 | 14112
iii | Laying of XLPE Cable in open trench & rising on pole through GI pipe & back filling of cable trench with excavated soil |  | Mtr | 69.603 | 1040 | 72387.12 | 72387.12
iv | Laying of GI pipe |  | Mtr | 69.8923 | 10 | 698.9228 | 698.9228
v | Fixing of rising pipe with clamps |  | Mtr | 390.2362 | 10 | 3902.362 | 3902.362
vi | Fixing of 11 kV lightning arrestor including earthing, jumpering and fixing of aluminium clamp |  | Set | 227.9096 | 2 | 455.8192 | 455.8192
vii | Providing earthing (earthing pit digging and laying of earthing pipe complete) |  | Set | 1063.5782 | 2 | 2127.1564 | 2127.1564
viii | Covering of cable with tiles |  | Mtr | 3.8836 | 1000 | 3883.6 | 3883.6
ix | Making of Straight jointing of XLPE Cable |  | No | 4591.619 | 2 | 9183.238 | 9183.238
x | Making of End jointing of XLPE Cable |  | No | 3883.58 | 2 | 7767.16 | 7767.16
24 | Transportation Charges |  |  |  |  | 80692.994 | 80692.994
25 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 19, 21, 22, 23, 24 |  |  |  |  | 186963.7231 | 250902.4796
26 | Total Estimated Cost excluding GST (Row 20, 21, 22, 23, 24, 25) |  |  |  |  | 1536208.9806 | 2039074.573
27 | Applicable CGST @ 9% on Row 26 |  |  | 0.09 |  | 138258.8083 | 183516.7116
28 | Applicable SGST @ 9% on Row 26 |  |  | 0.09 |  | 138258.8083 | 183516.7116
29 | Charges payable to Nagar Nigam / Nagar Palika / Nagar Panchayat / Gram Panchayat including supervision charges etc.
30 | Total Estimated Cost including GST (Row 26+27+28+29) |  |  |  |  | 1812726.5971 | 2406107.9962
31 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1812727 | 2406108
(a) | Cable and accessories size can be replaced as per actual requirement
(b) | When multiple cables have to be laid in the common trench, the following excavation is to be followed-- (i) 0.75 Mtr width x 1.2 Mtr depth for laying of 02 cables; (ii) 1.0 Mtr width x 1.2 Mtr depth for laying of 03 cables; (iii) 1.25 Mtr width x 1.2 Mtr depth for laying of 04 cables and so on.
(c) | Between two cables, fly ash brick is to be provided as separator
(d) | All other items are to be changed as per size of trench and number of cables in a trench.
ACTIVITY OF Col. 21 (xi) INCLUDED in (vi)
xi | Jumpering of Lightning arrestor and fixing of aluminium clamps |  | Set | 291.28 | 2 | 582.56 | 582.56
Note on B28: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on E33: 89326879: As per CL-10
Note on E34: 89326879: As per schedule CL-10
Note on E35: 89326879: As per schedule CL-10
Note on E36: 89326879: As per schedule CL-10
Note on E37: 89326879: As per Labour Schedule AL-6
Note on E38: 89326879: As per Labour Schedule BL-1
Note on E39: 89326879: As per Labour Schedule AL-6
Note on E40: 89326879: As per schedule AL-6
Note on E41: Barun Chakraborty: As per schedule CL-10
Note on E42: Barun Chakraborty: As per schedule CL-10
Note on E83: 89326879: As per Labour Schedule AL-6
Fill appropriate charges

## C-16
COST SCHEDULE C-16
D.T. CAPACITORS ON EXISTING DTR's OTHER THAN INDUSTRIAL (RETAINED & SHIFTED)
2019-20
S. No. | PARTICULARS | New SAP Bin code No. | Capacitor Rating - KVAR | Capacitor cost | Incidental Charges | Labour Charge per Capacitor Bank | Cost per Package | Cost per Package Round Off
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT Capacitor for 25 kVA DT | 7132200812 | 5 | 1611.53 | 120.8648 | 200 | 1932.3947 | 1932
2 | LT Capacitor for 63 kVA DT | 7132200813 | 10 | 3222.06 | 241.6545 | 200 | 3663.7145 | 3664
3 | LT Capacitor for 100 kVA DT | 7132200814 | 12 | 3871.51 | 290.3632 | 200 | 4361.8732 | 4362
4 | LT Capacitor for 200 kVA DT | 7132200814 | 12 | 3871.51 | 290.3632 | 200 | 4361.8732 | 4362
5 | LT Capacitor for 315 kVA DT | 7132200814 | 12 | 3871.51 | 290.3632 | 200 | 4361.8732 | 4362
| Incidental Charges @ 7.5% : - |  |  | 7.5% |  |  |  |  | Earlier name was - Incidental Charges @ 9%

## C-17
COST SCHEDULE C-17
11 kV MEDP STRUCTURE ON H-BEAM POLE, 11 METER LONG (TO BE SUPPLEMENTED FOR H.T. CONNECTION)
2019-20
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 53.8792 | 43976.1867
2 | DC Cross Arm of 100x50 mm channel (2.7 Mtr. Long) | 7130810512 | Set | 2 | 4104.29 | 8208.58
3 | 11 kV Polymer Disc Insulator | 7130820010 | No | 6 | 119.1 | 714.6
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 123.43 | 740.58
5 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 6 | 132.09 | 792.54
6 | (I) Stay set 16 mm | 7130860032 | No | 2 | 455.31 | 910.62
| (II) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 17 | 72.6867 | 1235.6734
(III) Stay Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 333.29 | 1333.16
7 | Concreting of pole @ 0.6 Cmt and 0.2 Cmt per stay and 0.05 Cmt for base padding (1:3:6) | 7130200202 | Cmt | 1.7 | 2970 | 5049 | Material cost including GST and labour.
8 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 118.52 | 237.04
9 | Red Oxide Paint | 7130211158 | Ltr | 2 | 151.45 | 302.9
10 | Aluminium Paint | 7130210809 | Ltr | 2 | 338.4 | 676.8
11 | Barbed wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 78.5018 | 314.0073
12 | Danger Board | 7130880041 | Each | 1 | 92.6 | 92.6
13 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 71.59 | 35.795
| 16x200 mm | 7130620631 | Kg | 5.5 | 69.2 | 380.6
14 | GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | 7130642039 | No | 2 | 876.17 | 1752.34
15 | G.I.Bend of 40 mm dia. | 7130640171 | Each | 1 | 107.48 | 107.48
16 | 11 kV Polymer type Lightning Arrestor | 7130840029 | Each | 3 | 328.57 | 985.71
17 | 11 kV CTPT unit of appropriate capacity |  | No
18 | Copper control cable 10 Core 2.5 Sqmm. (armoured) | 7130310660 | Mtr | 10 | 200.541 | 2005.41
19 | H.T. Static Trivector Meter 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 1 | 3611.89 | 3611.89 | Name changed
20 | Universal Meter Box for HT meters. | 7132406425 | Each | 1 | 3232.14 | 3232.14
21 | Test terminal Box (TTB) | 7131310037 | Each | 1 | 923.52 | 923.52
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 77619.1724
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 65778.9597 | NEW ROW ADDED
24 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 5821.4379 | Earlier name was - Incidental Charges @ 9%
25 | Labour charges for concreting |  | Cmt | 1.7 | 609.1748 | 1035.5972
26 | Labour charges as per Sch No.- CL-5 |  |  |  |  | 10568.93
27 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 3653.2451
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 22, 24, 25, 26, 27 |  |  |  |  | 12337.2978
29 | Total Estimated Cost excluding GST (Row 23, 24, 25, 26, 27, 28) |  |  |  |  | 99195.4677
30 | Applicable CGST @ 9% on Row 29 |  |  |  | 0.09 | 8927.5921
31 | Applicable SGST @ 9% on Row 29 |  |  |  | 0.09 | 8927.5921
32 | Total Estimated Cost including GST (Row 29+30+31) |  |  |  |  | 117050.6518
33 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 117051
Note:- All the rates are with considering price variation clause.
Note on B31: Barun Chakraborty: Earlier name was - 3 Ø 4 Wire 0.5S with DLMS Protocol category A
Note on B34: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D16: Barun Chakraborty: Earlier unit was - No.

## C-18
COST SCHEDULE C-18
2019-20
SCHEDULE FOR NEW AUTOMATED 11 KV CAPACITOR BANK AT 33/11 KV SUB-STATIONS
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank |  | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank
[5 empty] | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. Bank shall be complete with Capacitor units of 121 KVAr at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin/Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Botls etc. | 7132200826 | Nos | 192879.89 | 1 | 192879.89
2 | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . Bank shall be complete with Capacitor units of 121 kVAr at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin/Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Bolts etc. | 7132200014 | Nos | 145864.88 |  |  | 1 | 145864.88
3 | 11 kV, Aluminium Wound, Dry type Series reactors
4 | 0.2% Reactor suitable for 363 Kvar step | 7132210106 | Set | 7083.36 | 3 | 21250.08 | 3 | 21250.08
5 | 0.2% Reactor suitable for 726 Kvar step | 7132210108 | Set | 8647.51 | 6 | 51885.06 | 3 | 25942.53
6 | 11 kV, 3-Phase Oil-Cooled RVT | 7132230471 | No. | 34386.84 | 1 | 34386.84 | 1 | 34386.84
7 | 12 kV, Outdoor type Vacuum Capacitor switches | 7131980001 | Nos. | 69897.89 | 3 | 209693.67 | 2 | 139795.78
8 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure | 7131931091 | Set | 28693.62 | 1 | 28693.62 | 1 | 28693.62
9 | Mounting GI structure for above isolator | 7131931095 | Set | 14679.61 | 1 | 14679.61 | 1 | 14679.61
10 | 9 KV, 10 KA, Station Class, Polymer Lightning Arrestors | 7130840029 | set of 3 | 985.71 | 1 | 985.71 | 1 | 985.71
| Indoor Type Automatic Control Unit along with APFC Relay | 7131940871 | No. | 48181.89 | 1 | 48181.89 | 1 | 48181.89
11 | GI Structure for complete Equipment | 7130850198 | Kgs. | 84.87 | 1000 | 84870 | 800 | 67896
12 | Unarmoured Control cable 8Cx2.5 Sqmm and junction box | 7130310658 | Mtr | 129.5439 | 120 | 15545.2716 | 120 | 15545.2716
13 | Unarmoured Control cable 10Cx2.5 Sqmm | 7130310681 | Mtr | 161.8413 | 60 | 9710.4756 | 60 | 9710.4756
14 | Unarmoured Control cable 2Cx2.5 Sqmm | 7130310652 | Mtr | 39.1091 | 60 | 2346.5442 | 60 | 2346.5442
15 | 11 KV VCB , 630 A, suitable for Capacitor Switching | 7131941762 | Nos. | 119502.62 | 1 | 119502.62
16 | 11 KV VCB , 400 A, suitable for Capacitor Switching | 7131941762 | Nos. | 119502.62 |  |  | 1 | 119502.62
17 | 11 kV Control & Relay Panel for Capacitor Bank | 7131960010 | Nos. | 86141.15 | 1 | 86141.15 | 1 | 86141.15
18 | 11 KV Power Cable, HT XLPE, 120 Sq MM | 7130310078 | Mtr | 817.6462 | 15 | 12264.6928
19 | 11 KV Power Cable, HT XLPE, 95 Sq MM | 7130310077 | Mtr | 548.3137 |  |  | 15 | 8224.7052
20 | 11 kV C.T. 200-100/5 Amps. | 7132230185 | Nos. | 13709.83 | 3 | 41129.49 | 3 | 41129.49
21 | Earthing through
(i) | 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 4453.22 | 3 | 13359.66 | 3 | 13359.66
(ii) | M.S.Flat 50 x 6 mm | 7130600173 | Kg | 46.9271 | 100 | 4692.714 | 100 | 4692.714
22 | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2970 | 9.9 | 29403 | 9.9 | 29403 | Material cost including GST and labour.
23 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1021601.9883 |  | 857732.5706
24 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 865764.3968 |  | 726892.009 | NEW ROW ADDED
25 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 76620.1491 |  | 64329.9428 | Earlier name was - Incidental Charges @ 9%
26 | Labour Charges |  |  |  |  | 51080.0994 |  | 42886.6285
27 | Transport Charges |  |  |  |  | 30648.0596 |  | 25731.9771
28 | Labour charges for concreting |  | Cmt | 609.1748 | 9.9 | 6030.8305 | 9.9 | 6030.8305 | OK UPTO HERE
29 | Service in lieu of Earthing Coal & Salt etc |  | No | 2765.8829 | 1 | 2765.8829 | 1 | 2765.8829
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 23, 25, 26, 27, 28, 29, |  |  |  |  | 148593.3762 |  | 124934.729
31 | Total Estimated Cost excluding GST (Row 24, 25, 26, 27, 28, 29, 30) |  |  |  |  | 1181502.7946 |  | 993571.9998
32 | Applicable CGST @ 9% on Row 31 |  |  | 0.09 |  | 106335.2515 |  | 89421.48
33 | Applicable SGST @ 9% on Row 31 |  |  | 0.09 |  | 106335.2515 |  | 89421.48
34 | Total Estimated Cost including GST (Row 31+32+33) |  |  |  |  | 1394173.2976 |  | 1172414.9598
35 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1394173 |  | 1172415
Note on B25: 89326879: Earlier name was - C & R Panel for VCB
Note on B33: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## C-19
COST SCHEDULE C-19
SCHEDULE FOR INSTALLATION OF COMPACT R.M.U. 11 kV CLASS SF6 / VCB TYPE (1 INCOMING + 2 BREAKER + 1 OUTGOING)
2019-20
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RMU (4 Way), One Incoming + Two Breakers + One Outgoing (2OD + 2 VL), 350 MVA, 650 Amps. | 7131941764 | No | 1114574.84 | 1 | 1114574.84
2 | Concreting of RMU Bed with CC 1:3:6 as per Labour Charges | 7130200202 | Cmt | 2970 | 0.37 | 1098.9 | Material cost including GST and labour.
3 | Concreting of Foundation with Reinforcement CC 1:3:6 as per Labour Charges | 7130200202 | Cmt | 2970 | 1.44 | 4276.8
4 | M.S.Strip 25 x 3 mm for earthing (of length 2 x 5 = 10 Mtr.) | 7130640039 | Kg | 39.17 | 6 | 235.02 | NEW BIN CODE ALLOTED
| GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 876.17 | 2 | 1752.34
5 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1121937.9
6 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 950794.8305 | NEW ROW ADDED
7 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 84145.3425 | Earlier name was - Incidental Charges @ 9%
8 | Labour Charges as per Sch. CL-11. |  |  |  |  | 8693
9 | Labour charges for concreting |  | Cmt | 609.1748 | 1.81 | 1102.6064
10 | Transportation Charges |  |  |  |  | 7669.0561
11 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 05, 07, 08, 09, 10 |  |  |  |  | 152943.4881
12 | Total Estimated Cost excluding GST (Row 06, 07, 08, 09, 10, 11) |  |  |  |  | 1205348.3236
13 | Applicable CGST @ 9% on Row 12 |  |  | 0.09 |  | 108481.3491
14 | Applicable SGST @ 9% on Row 12 |  |  | 0.09 |  | 108481.3491
15 | Total Estimated Cost including GST (Row 12+13+14) |  |  |  |  | 1422311.0218
16 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1422311
Note on B13: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## C-20
COST SCHEDULE C-20
SCHEDULE FOR CHEMICAL EARTHING OF METERING EQUIPMENT INSTALLED IN THE PREMISES OF HT CONSUMERS IN NORMAL / HARD ROCK SOIL
2019-20
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | M.S.Strip 25x3 mm (0.6 kg/Mtr.) | 7130640039 | Kg | 39.17 | 10 | 391.7 | NEW BIN CODE ALLOTED
2 | Chem Rod Earthing electrode (Chemical Earthing) | 7132486843 | Job | 9231.08 | 1 | 9231.08 | RATE EXCLUDING G.S.T.
3 | G.I. Nuts & Bolts 16x40 mm | 7130620133 | Kg | 99.03 | 1.5 | 148.545
4 | G.I. Nuts & Bolts 16x65 mm | 7130620140 | Kg | 99.03 | 1.5 | 148.545
5 | G.I. Spring Washer | 7130622922 | Kg | 153.83 | 1 | 153.83
6 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 10073.7
7 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 8537.0339 | NEW ROW ADDED
8 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 755.5275 | Earlier name was - Incidental Charges @ 9%
9 | Labour Charges |  | No. | 1063.5729 | 1 | 1063.5729
10 | Transportation Charges |  |  |  |  | 1070.6422
11 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 06, 08, 09, 10 |  |  |  |  | 1620.4303
12 | Total Estimated Cost excluding GST (Row 07, 08, 09, 10, 11) |  |  |  |  | 13047.2069
13 | Applicable CGST @ 9% on Row 12 |  |  | 0.09 |  | 1174.2486
14 | Applicable SGST @ 9% on Row 12 |  |  | 0.09 |  | 1174.2486
15 | Total Estimated Cost including GST (Row 12+13+14) |  |  |  |  | 15395.7041
16 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 15396
Note:- | Chemical Earthing consists of Galvanized Mild Steel pipe of size 2000 mm x 50 mm Outer diameter or higher size as per site conditions, filled with a highly conductive material and a GI Strip minimum 16 mm x 3 mm covering total of pipe, forming the electrode for obtaining earth resistance less than 1 ohm.
Note on B12: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D8: Barun Chakraborty: Earlier unit was -No.

## C-21
COST SCHEDULE C-21
2019-20
SCHEDULE FOR 11 kV CAPACITOR BANK TO BE INSTALLED AT 11 kV LINE D.P. STRUCTURE
S. No. | PARTICULARS | Bin Code No | Unit | Rate | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 Meter long PCC Pole | 7130800012 | No | 2255.2 | 2 | 4510.4
2 | 11 kV 'V' Cross arm with clamp (instead of DC Cross arm) | 7130810495 | No | 1091.69 | 0 | 0
3 | 11 kV Top clamp with cleat | 7130810679 | No | 306.26 | 0 | 0
4 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 132.09 | 3 | 396.27
5 | 11 kV A.B. Switch | 7131930221 | Set | 8496 | 1 | 8496
6 | 11 kV Polymer Disc insulator | 7130820010 | No | 119.1 | 3 | 357.3
7 | 11 kV Strain Hardware | 7130820241 | No | 123.43 | 3 | 370.29
8 | 11 kV D.O. Fuse and L.A. mounting DC channel size 75x40x6 mm length | 7130810509 | No | 1730.26 | 1 | 1730.26
9 | 11 kV D.O. Fuse unit | 7131930412 | Each | 1177.88 | 3 | 3533.64
10 | (i) Stay set 16 mm | 7130860032 | No | 455.31 | 4 | 1821.24
| (ii) Stay wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 72.6867 | 22 | 1599.1067
| (iii) Stay clamp | 7130810026 | Pair | 160.97 | 4 | 643.88
11 | Concreting of supports @ 0.5 Cmt per pole and @ 0.2 Cmt per stay & base padding @ 0.05 Cmt/pole (1:3:6) | 7130200202 | Cmt | 2970 | 1.9 | 5643 | Material cost including GST and labour.
12 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | Set | 4736.61 | 2 | 9473.22
13 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 4736.61 | 1 | 4736.61
14 | Danger Board | 7130880041 | Each | 92.6 | 1 | 92.6
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 78.5018 | 2 | 157.0037
16 | Earthing set (pipe earth as per drawing) - 2 sets
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 222.08 | 18 | 3997.44
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 65.0097 | 30 | 1950.2898
17 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 1 | 151.45
18 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 1 | 338.4
19 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 328.57 | 3 | 985.71
20 | M.S. Nuts and Bolts
| (i) 16x40 mm | 7130620609 | Kg | 71.59 | 1 | 71.59
| (ii) 16x65 mm | 7130620614 | Kg | 70.4 | 4 | 281.6
| (iii) 16x140 mm | 7130620625 | Kg | 69.2 | 4 | 276.8
| (iv) 16x200 mm | 7130620631 | Kg | 69.2 | 5 | 346
21 | 11 kV Capacitor Unit with Expulsion Tube | 7132200004 | Each | 106.2 | 6 | 637.2 | Cost per kVAR
22 | Sundries (including Board for Safety Instructions) |  |  |  | LS | 1000
23 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 53597.3002
24 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 45421.4408
25 | Incidental Charges @ 7.5% on Sub Total -1 : - |  |  |  | 0.075 | 4019.7975
26 | Back filling of poles with boulders @ 0.3 Cmt per pole. |  | No. |  | 311.3185 | 622.637
27 | Labour charges for concreting |  | Cmt |  | 609.1748 | 1157.4321
28 | Labour charges as per Schedule No. CL-3 |  |  |  |  | 12048.82
29 | Transport charges upto 50 Kms. Average lead from area store to const. camping site transport |  |  |  |  | 3195.4418
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 23, 25, 26, 27, 28, 29 |  |  |  | 0.125 | 9330.1786
31 | Total Estimated Cost excluding GST (Row 24, 25, 26, 27, 28, 29, 30) |  |  |  |  | 75795.7478
32 | Applicable CGST @ 9% on Row 31 |  |  |  |  | 6821.6173
33 | Applicable SGST @ 9% on Row 31 |  |  |  |  | 6821.6173
34 | Total Estimated Cost including GST (Row 31+32+33) |  |  |  |  | 89438.9824
35 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 89439
Remarks- The schedule is to be prepared based on actual site requirement and labour / transport charges may be substituted accordingly.

## D-1
COST SCHEDULE D-1
2019-20
LT LINE 3 PHASE 5 WIRE ON PCC SUPPORTS USING RABBIT / WEASEL / SQUIRREL CONDUCTORS WITH MAXIMUM SPAN OF 60 METERS
S. No. | PARTICULARS | New Bin Code | Unit | Rate | Using 50 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 3 Wires of 50 Sqmm ACSR & 2 Wires of 20 Sqmm |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 3 Wires of 30 Sqmm ACSR & 2 Wires of 20 Sqmm ACSR |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
1 | 140 Kg, 8.0 Mtr. long PCC support | 7130800012 | No | 2255.2 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4
2 | LT Five Pin Cross arm | 7130810461 | No | 889.61 | 22 | 19571.42 | 22 | 19571.42 | 22 | 19571.42 | 22 | 19571.42 | 22 | 19571.42
3 | LT Shackle insulator (90x75 mm) including cut point / angle location | 7130820106 | No | 13.06 | 88 | 1149.28 | 88 | 1149.28 | 88 | 1149.28 | 88 | 1149.28 | 88 | 1149.28
4 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 41.94 | 30 | 1258.2 | 30 | 1258.2 | 30 | 1258.2 | 30 | 1258.2 | 30 | 1258.2
5 | Earth knob (Aluminium bobbin) | 7130820201 | No | 36.74 | 17 | 624.58 | 17 | 624.58 | 17 | 624.58 | 17 | 624.58 | 17 | 624.58
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 34.7014 | 4120 | 142969.6444 | 3090 | 107227.2333 | -- |  | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 21.0579 | -- |  | -- |  | 4120 | 86758.4244 | 3090 | 65068.8183 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.289 | 1030 | 14717.6803 | 2060 | 29435.3606 | 1030 | 14717.6803 | 2060 | 29435.3606 | 5150 | 73588.4015
7 | (i) Stay set 16 mm | 7130860032 | No | 455.31 | 9 | 4097.79 | 9 | 4097.79 | 9 | 4097.79 | 9 | 4097.79 | 9 | 4097.79
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 54 | 3925.0802 | 54 | 3925.0802 | 54 | 3925.0802 | 54 | 3925.0802 | 54 | 3925.0802
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 9 | 1448.73 | 9 | 1448.73 | 9 | 1448.73 | 9 | 1448.73 | 9 | 1448.73
| (iv) Stay Insulator | 7130820117 | No | 11.13 | 9 | 100.17 | 9 | 100.17 | 9 | 100.17 | 9 | 100.17 | 9 | 100.17
8 | Split insulator for guarding | 7130820018 | Pair | 4.18 | 44 | 183.92 | 44 | 183.92 | 44 | 183.92 | 44 | 183.92 | 44 | 183.92
9 | Binding wire and tape | 7130830006 | Kg | 160.41 | 3.5 | 561.435 | 3.5 | 561.435 | 3.5 | 561.435 | 3.5 | 561.435 | 3.5 | 561.435
10 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 26 |  | 26 |  | 26 |  | 26 |  | 26
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 35 | 5530 | 35 | 5530 | 35 | 5530 | 35 | 5530 | 35 | 5530 | Material cost including GST and labour.
11 | Nuts and Bolts |  | Kg |  | 35 |  | 35 |  | 35 |  | 35 |  | 35
| 12x100 mm | 7130620573 | Kg | 71.59 | 10 | 715.9 | 10 | 715.9 | 10 | 715.9 | 10 | 715.9 | 10 | 715.9
| 16x40 mm | 7130620609 | Kg | 71.59 | 5 | 357.95 | 5 | 357.95 | 5 | 357.95 | 5 | 357.95 | 5 | 357.95
| 16x140 mm | 7130620625 | Kg | 69.2 | 20 | 1384 | 20 | 1384 | 20 | 1384 | 20 | 1384 | 20 | 1384
12 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 5 | 592.6 | 5 | 592.6 | 5 | 592.6 | 5 | 592.6 | 5 | 592.6
13 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 2 | 302.9 | 2 | 302.9 | 2 | 302.9 | 2 | 302.9 | 2 | 302.9
14 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 2 | 676.8 | 2 | 676.8 | 2 | 676.8 | 2 | 676.8 | 2 | 676.8
15 | G.I. Wire 8 SWG for guarding | 7130870043 | Kg | 65.0097 | 6 | 390.058 | 6 | 390.058 | 6 | 390.058 | 6 | 390.058 | 6 | 390.058
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 238896.5378 |  | 217871.807 |  | 182685.3178 |  | 175713.392 |  | 154797.6146
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 202454.6931 |  | 184637.1246 |  | 154818.066 |  | 148909.6543 |  | 131184.4192 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 17917.2403 |  | 16340.3855 |  | 13701.3988 |  | 13178.5044 |  | 11609.8211 | Earlier name was - Incidental Charges @ 9%
19 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 210.0559 | 17 | 3570.951 | 17 | 3570.951 | 17 | 3570.951 | 17 | 3570.951 | 17 | 3570.951
20 | Labour charges as per Sch No. DL-1 |  |  |  |  | 57284.21 |  | 57284.21 |  | 57284.21 |  | 57284.21 |  | 57284.21
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 10924.5762 |  | 10924.5762 |  | 10924.5762 |  | 10924.5762 |  | 10924.5762
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row -16, 18, 19, 20, 21 |  |  |  |  | 41074.1894 |  | 38248.9912 |  | 33520.8067 |  | 32583.9542 |  | 29773.3966
23 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22) |  |  |  |  | 333225.8601 |  | 311006.2386 |  | 273820.0088 |  | 266451.8501 |  | 244347.3741
24 | Applicable CGST @ 9% on Row 23 |  |  | 0.09 |  | 29990.3274 |  | 27990.5615 |  | 24643.8008 |  | 23980.6665 |  | 21991.2637
25 | Applicable SGST @ 9% on Row 23 |  |  | 0.09 |  | 29990.3274 |  | 27990.5615 |  | 24643.8008 |  | 23980.6665 |  | 21991.2637
26 | Total Estimated Cost including GST (Row 23+24+25) |  |  |  |  | 393206.5149 |  | 366987.3616 |  | 323107.6104 |  | 314413.1831 |  | 288329.9015
27 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 393207 |  | 366987 |  | 323108 |  | 314413 |  | 288330
Note :- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B33: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D21: 89326879: Earlier unit was - No.

## D-2
COST SCHEDULE D-2
2019-20
1 Km LT LINES 3 Phase 4 Wire USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON 140 Kg; 8.0 Mtr. LONG PCC SUPPORTS WITH MAXIMUM SPAN OF 60 METERS
S. NO. | PARTICULARS | New Bin Code | Unit | Rate | Using 50 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | PCC Pole 140 Kg, 8.0 Mtr long | 7130800012 | No | 2255.2 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4
2 | LT Four Pin cross arm | 7130810441 | No | 766.7 | 22 | 16867.4 | 22 | 16867.4 | 22 | 16867.4
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 13.06 | 66 | 861.96 | 66 | 861.96 | 66 | 861.96
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 36.74 | 17 | 624.58 | 17 | 624.58 | 17 | 624.58
5 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 41.94 | 25 | 1048.5 | 25 | 1048.5 | 25 | 1048.5
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 34.7014 | 3090 | 107227.2333 | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 21.0579 | -- |  | 3090 | 65068.8183 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.289 | 1030 | 14717.6803 | 1030 | 14717.6803 | 4120 | 58870.7212
7 | (i) Stay set 16 mm | 7130860032 | No | 455.31 | 9 | 4097.79 | 9 | 4097.79 | 9 | 4097.79
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 54 | 3925.0802 | 54 | 3925.0802 | 54 | 3925.0802
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 9 | 1448.73 | 9 | 1448.73 | 9 | 1448.73
| (iv) Stay Insulator | 7130820117 | No | 11.13 | 9 | 100.17 | 9 | 100.17 | 9 | 100.17
8 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. /pole and for stay set @ 02 Nos. per stay set. |  |  |  | 26 |  | 26 |  | 26
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 35 | 5530 | 35 | 5530 | 35 | 5530 | Material cost including GST and labour.
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 5 | 592.6 | 5 | 592.6 | 5 | 592.6
10 | Split insulator for guarding | 7130820018 | Pair | 4.18 | 44 | 183.92 | 44 | 183.92 | 44 | 183.92
11 | M.S. Nuts and Bolts |  | Kg |  | 35 |  | 35 |  | 35
| 12x100 mm | 7130620573 | Kg | 71.59 | 10 | 715.9 | 10 | 715.9 | 10 | 715.9
| 16x40 mm | 7130620609 | Kg | 71.59 | 5 | 357.95 | 5 | 357.95 | 5 | 357.95
| 16x140 mm | 7130620625 | Kg | 69.2 | 20 | 1384 | 20 | 1384 | 20 | 1384
12 | Binding wire and tape | 7130830006 | Kg | 160.41 | 3.5 | 561.435 | 3.5 | 561.435 | 3.5 | 561.435
13 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 2 | 676.8 | 2 | 676.8 | 2 | 676.8
14 | Red Oxide paint | 7130211158 | Ltr | 151.45 | 2 | 302.9 | 2 | 302.9 | 2 | 302.9
15 | GI wire 8 SWG for guarding | 7130870043 | Kg | 65.0097 | 6 | 390.058 | 6 | 390.058 | 6 | 390.058
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 199953.0867 |  | 157794.6717 |  | 136878.8943
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 169451.7684 |  | 133724.2981 |  | 115999.063 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 14996.4815 |  | 11834.6004 |  | 10265.9171 | Earlier name was - Incidental Charges @ 9%
19 | Back filling of pole pit with boulder @ 0.25 Cmt |  | No | 210.0559 | 17 | 3570.951 | 17 | 3570.951 | 17 | 3570.951
20 | Labour charges as per Sch. No. DL-1 |  |  |  |  | 53885.23 |  | 53885.23 |  | 53885.23
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 10924.5762 |  | 10924.5762 |  | 10924.5762
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row -16, 18, 19, 20, 21 |  |  |  |  | 35416.2907 |  | 29751.2537 |  | 26940.6961
23 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22) |  |  |  |  | 288245.2979 |  | 243690.9094 |  | 221586.4334
24 | Applicable CGST @ 9% on Row 23 |  |  | 0.09 |  | 25942.0768 |  | 21932.1818 |  | 19942.779
25 | Applicable SGST @ 9% on Row 23 |  |  | 0.09 |  | 25942.0768 |  | 21932.1818 |  | 19942.779
26 | Total Estimated Cost including GST (Row 23+24+25) |  |  |  |  | 340129.4515 |  | 287555.2731 |  | 261471.9914
27 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 340129 |  | 287555 |  | 261472
Note:- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B33: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-3
COST SCHEDULE D-3
2019-20
1 Km LT LINE 1 PHASE 3 WIRE USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON 140 Kg; 8.0 Mtr. LONG PCC SUPPORTS WITH MAXIMUM SPAN OF 60 METERS
S. No. | PARTICULARS | New Bin Code | Unit | Rate | Using one wire of 50 Sqmm, one wire of 30 Sqmm ACSR and one wire of 20 Sqmm ACSR Conductor |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | PCC Pole 140 Kg, 8.0 Mtr long | 7130800012 | No | 2255.2 | 17 | 38338.4 | 17 | 38338.4 | 17 | 38338.4
2 | LT Three Pin cross arm | 7130810413 | No | 643.77 | 22 | 14162.94 | 22 | 14162.94 | 22 | 14162.94
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 13.06 | 44 | 574.64 | 44 | 574.64 | 44 | 574.64
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 36.74 | 22 | 808.28 | 22 | 808.28 | 22 | 808.28
5 | Hardware for 90x75 mm Shackle insu. | 7130820216 | No | 41.94 | 25 | 1048.5 | 25 | 1048.5 | 25 | 1048.5
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 34.7014 | 1030 | 35742.4111 | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 21.0579 | 1030 | 21689.6061 | 2060 | 43379.2122 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.289 | 1030 | 14717.6803 | 1030 | 14717.6803 | 3090 | 44153.0409
7 | (i) Stay set 16 mm | 7130860032 | No | 455.31 | 9 | 4097.79 | 9 | 4097.79 | 9 | 4097.79
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 54 | 3925.0802 | 54 | 3925.0802 | 54 | 3925.0802
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 9 | 1448.73 | 9 | 1448.73 | 9 | 1448.73
| (iv) Stay Insulator | 7130820117 | No | 11.13 | 9 | 100.17 | 9 | 100.17 | 9 | 100.17
8 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 26 |  | 26 |  | 26
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 35 | 5530 | 35 | 5530 | 35 | 5530 | Material cost including GST and labour.
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 5 | 592.6 | 5 | 592.6 | 5 | 592.6
10 | Split insulator for guarding | 7130820018 | Pair | 4.18 | 44 | 183.92 | 44 | 183.92 | 44 | 183.92
11 | M.S. Nuts and Bolts |  | Kg |  | 16 |  | 16 |  | 16
| 12x100 mm | 7130620573 | Kg | 71.59 | 3.5 | 250.565 | 3.5 | 250.565 | 3.5 | 250.565
| 16x40 mm | 7130620609 | Kg | 71.59 | 1.5 | 107.385 | 1.5 | 107.385 | 1.5 | 107.385
| 16x140 mm | 7130620625 | Kg | 69.2 | 11 | 761.2 | 11 | 761.2 | 11 | 761.2
12 | Binding wire and tape | 7130830006 | Kg | 160.41 | 3.5 | 561.435 | 3.5 | 561.435 | 3.5 | 561.435
13 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 1.5 | 507.6 | 1.5 | 507.6 | 1.5 | 507.6
14 | Red Oxide paint | 7130211158 | Ltr | 151.45 | 1.5 | 227.175 | 1.5 | 227.175 | 1.5 | 227.175
15 | GI wire 4 mm for guarding | 7130870043 | Kg | 65.0097 | 6 | 390.058 | 6 | 390.058 | 6 | 390.058
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 145766.1656 |  | 131713.3606 |  | 117769.509
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 123530.6488 |  | 111621.4921 |  | 99804.6687 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 10932.4624 |  | 9878.502 |  | 8832.7132 | Earlier name was - Incidental Charges @ 9%
19 | Back filling of pole pit with boulder @ 0.25 Cmt |  | No | 210.0559 | 17 | 3570.951 | 17 | 3570.951 | 17 | 3570.951
20 | Labour charges as per Sch No. DL-1 |  |  |  |  | 49935.36 |  | 49935.36 |  | 49935.36
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 11561.847 |  | 11561.847 |  | 11561.847
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row -16, 18, 19, 20, 21 |  |  |  |  | 27720.8483 |  | 25832.5026 |  | 23958.7975
23 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22) |  |  |  |  | 227252.1175 |  | 212400.6547 |  | 197664.3374
24 | Applicable CGST @ 9% on Row 23 |  |  | 0.09 |  | 20452.6906 |  | 19116.0589 |  | 17789.7904
25 | Applicable SGST @ 9% on Row 23 |  |  | 0.09 |  | 20452.6906 |  | 19116.0589 |  | 17789.7904
26 | Total Estimated Cost including GST (Row 23+24+25) |  |  |  |  | 268157.4987 |  | 250632.7725 |  | 233243.9181
27 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 268157 |  | 250633 |  | 233244
Note: | All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B23: 89326879: Earlier name was - Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad
Note on B35: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-4
COST SCHEDULE D-4
2019-20
1 KM OF 3 PHASE 5 WIRE LT LINE ON R.S. JOIST WITH ACSR CONDUCTOR FOR URBAN AREAS
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 3 Ph, 5 Wire line on RSJ 125x70 mm 9.3 Mtr long with max. span 45 Mtrs for size of conductor upto 3x50 Sqmm + 2x30 Sqmm ACSR |  | 3 Ph, 5 Wire line on RSJ 175x85 mm 9.3 Mtr long with max. span 65 Mtrs for size of conductor upto 3x80 Sqmm + 2x30 Sq mm ACSR
[5 empty] | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | (i) R.S. Joist (125x70 mm) 9.3 Mtr long @13.198 Kg = 122.74 kg/pole x 22 No = 2700.28 Kgs | 7130600635 | Kg | 39.5051 | 2700.28 | 106674.9394 | -- | --
| (ii) R.S. Joist (175x85 mm) 9.3 Mtr long @ 19.495 Kg per mtr x 9.3 mtr = 181.3 Kg/pole x 15 No = 2719.55 Kgs | 7130600675 | Kg | 44.9155 | -- | -- | 2719.55 | 122150.0024
2 | LT Five Pin Cross arm | 7130810461 | No | 889.61 | 27 | 24019.47 | 20 | 17792.2
3 | LT Shackle Insulator (90x75 mm) including cut point/angle location | 7130820106 | No | 13.06 | 108 | 1410.48 | 80 | 1044.8
4 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 41.94 | 35 | 1467.9 | 35 | 1467.9
5 | Earth knob (Aluminium bobbin) | 7130820201 | No | 36.74 | 27 | 991.98 | 20 | 734.8
6 | ACSR conductor including 3% sag
| (i) 80 Sqmm Al. Eq (Raccoon) | 7130830060 | Mtr | 51.3096 | -- |  | 3090 | 158546.5713
| (ii) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 34.7014 | 3090 | 107227.2333 | --
| (iii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 21.0579 | 2060 | 43379.2122 | 2060 | 43379.2122
7 | (i) Stay set 16 mm | 7130860032 | No | 455.31 | 12 | 5463.72 | 12 | 5463.72
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 72 | 5233.4402 | 72 | 5233.4402
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 12 | 1931.64 | 12 | 1931.64
8 | Split insulator for guarding | 7130820018 | Pair | 4.18 | 60 | 250.8 | 40 | 167.2
9 | Binding wire and tape | 7130830006 | Kg | 160.41 | 3.5 | 561.435 | 3 | 481.23
10 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad & support @ 0.3 Cmt (1:3:6) | 7130200202 | Cmt | 2970 | 10.1 | 29997 | 7.65 | 22720.5 | Material cost including GST and labour.
11 | M.S. Nuts and Bolts |  | Kg |  | 44 |  | 30
| 12x100 mm | 7130620573 | Kg | 71.59 | 17 | 1217.03 | 12 | 859.08
| 16x40 mm | 7130620609 | Kg | 71.59 | 8 | 572.72 | 5 | 357.95
| 16x65 mm | 7130620614 | Kg | 70.4 | 19 | 1337.6 | 13 | 915.2
12 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 118.52 | 7 | 829.64 | 5 | 592.6
13 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 5 | 757.25 | 5 | 757.25
14 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 5 | 1692 | 5 | 1692
15 | G.I. Wire 4 mm for guarding | 7130870043 | Kg | 65.0097 | 7.5 | 487.5725 | 5 | 325.0483
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 335503.0626 |  | 386612.3445
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 284324.6293 |  | 327637.58 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 25162.7297 |  | 28995.9258 | Earlier name was - Incidental Charges @ 9%
19 | Labour charges for concreting |  | Cmt | 609.1748 | 10.1 | 6152.6654 | 7.65 | 4660.1872
20 | Labour charges as per Sch. No. DL-2 |  |  |  |  | 74185.63 |  | 63225.16
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 10530.8973 |  | 10530.8973
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row -16, 18, 19, 20, 21 |  |  |  |  | 56441.8731 |  | 61753.0644
23 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22) |  |  |  |  | 456798.4249 |  | 496802.8147
24 | Applicable CGST @ 9% on Row 23 |  |  | 0.09 |  | 41111.8582 |  | 44712.2533
25 | Applicable SGST @ 9% on Row 23 |  |  | 0.09 |  | 41111.8582 |  | 44712.2533
26 | Total Estimated Cost including GST (Row 23+24+25) |  |  |  |  | 539022.1414 |  | 586227.3214
27 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 539022 |  | 586227
Note:- All the rates are with considering price variation clause.
Note on B32: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-5
COST SCHEDULE D-5
2019-20
1 Km. LT LINE 1 PHASE 3 WIRE USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON R.S.JOIST SUPPORTS WITH MAXIMUM SPAN OF 45 METERS FOR URBAN AREAS
S. No. | PARTICULARS | New Bin Code | Unit | Rate | Using one wire of 50 Sqmm, one wire of 30 Sqmm ACSR and one wire of 20 Sqmm ACSR Conductor |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 125x70 mm 9.3 Mtr long RSJ supports @ 13.198 Kg/mtr = 122.74 Kg/pole x 22 Nos = 2700.28 Kgs. | 7130600635 | Kg | 39.5051 | 2700.28 | 106674.9394 | 2700.28 | 106674.9394 | 2700.28 | 106674.9394
2 | LT Three Pin cross arm | 7130810413 | No | 643.77 | 22 | 14162.94 | 22 | 14162.94 | 22 | 14162.94
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 13.06 | 54 | 705.24 | 54 | 705.24 | 54 | 705.24
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 36.74 | 22 | 808.28 | 22 | 808.28 | 22 | 808.28
5 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 41.94 | 22 | 922.68 | 22 | 922.68 | 22 | 922.68
6 | ACSR Conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 34.7014 | 1030 | 35742.4111 | -- | -- | -- | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 21.0579 | 1030 | 21689.6061 | 2060 | 43379.2122 | -- | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 14.289 | 1030 | 14717.6803 | 1030 | 14717.6803 | 3090 | 44153.0409
7 | (i) Stay set 16 mm | 7130860032 | No | 455.31 | 9 | 4097.79 | 9 | 4097.79 | 9 | 4097.79
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 54 | 3925.0802 | 54 | 3925.0802 | 54 | 3925.0802
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 9 | 1448.73 | 9 | 1448.73 | 9 | 1448.73
8 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad & concreting of support @ 0.3 Cmt.per pole (1:3:6) | 7130200202 | Cmt | 2970 | 9.5 | 28215 | 9.5 | 28215 | 9.5 | 28215 | Material cost including GST and labour.
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 7 | 829.64 | 7 | 829.64 | 7 | 829.64
10 | Split insulator for guarding | 7130820018 | Pair | 4.18 | 60 | 250.8 | 60 | 250.8 | 60 | 250.8
11 | M.S.Nuts and Bolts |  | Kg |  | 20 |  | 20 |  | 20
| 12x100 mm | 7130620573 | Kg | 71.59 | 7 | 501.13 | 7 | 501.13 | 7 | 501.13
| 16x40 mm | 7130620609 | Kg | 71.59 | 3 | 214.77 | 3 | 214.77 | 3 | 214.77
| 16x65 mm | 7130620614 | Kg | 70.4 | 10 | 704 | 10 | 704 | 10 | 704
12 | Binding wire and tape | 7130830006 | Kg | 160.41 | 3 | 481.23 | 3 | 481.23 | 3 | 481.23
13 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 5 | 1692 | 5 | 1692 | 5 | 1692
14 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 5 | 757.25 | 5 | 757.25 | 5 | 757.25
15 | G.I. Wire 8 SWG for guarding | 7130870043 | Kg | 65.0097 | 5 | 325.0483 | 5 | 325.0483 | 5 | 325.0483
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 238866.2454 |  | 224813.4404 |  | 210869.5888
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 202429.0215 |  | 190519.8648 |  | 178703.0414 | NEW ROW ADDED
18 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 17914.9684 |  | 16861.008 |  | 15815.2192 | Earlier name was - Incidental Charges @ 9%
19 | Labour charges for concreting |  | Cmt | 609.1748 | 9.5 | 5787.1605 | 9.5 | 5787.1605 | 9.5 | 5787.1605
20 | Labour charges as per Sch. No. DL-1 |  |  |  |  | 49935.36 |  | 49935.36 |  | 49935.36
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 10530.8973 |  | 10530.8973 |  | 10530.8973
22 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row -16, 18, 19, 20, 21 |  |  |  |  | 40379.329 |  | 38490.9833 |  | 36617.2782
23 | Total Estimated Cost excluding GST (Row 17, 18, 19, 20, 21, 22) |  |  |  |  | 326976.7368 |  | 312125.274 |  | 297388.9566
24 | Applicable CGST @ 9% on Row 23 |  |  | 0.09 |  | 29427.9063 |  | 28091.2747 |  | 26765.0061
25 | Applicable SGST @ 9% on Row 23 |  |  | 0.09 |  | 29427.9063 |  | 28091.2747 |  | 26765.0061
26 | Total Estimated Cost including GST (Row 23+24+25) |  |  |  |  | 385832.5494 |  | 368307.8233 |  | 350918.9688
27 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 385833 |  | 368308 |  | 350919
Note on B33: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-6 (1)
COST SCHEDULE -- D-6 (1)
2019-20
1 KM OF 3 PHASE 5 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS. AND R.S. JOIST / H-BEAM POLE SUPPORT USING AB XLPE CABLE WITH MAXIMUM SPAN 50 METER URBAN AREA
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support |  | RS Joist (175X85) mm 9.3 Mtr Long i.e. 19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No =3626.07 Kgs |  | H-BEAM 152x152 mm 37.1 Kg/Mtr 9.0 Mtr long i.e. 408.1 Kg/pole x10 Nos= 4081 Kgs
[5 empty] | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm. |  | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm. |  | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm.
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 6 | 7 | 6 | 7
1(a) | RS Joist (175X85) mm 9.3 Mtr Long i.e.19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No = 3626.07 Kgs | 7130600675 | Kg | 44.9155 |  |  | 3626.07 | 162866.8196
(b) | H-BEAM 152x152 mm 37.1 Kg /Mtr 9.0 Mtr long i.e. 333.9 Kg/pole x 20 Nos = 6678 Kgs | 7130601958 | Kg | 53.8792 |  |  |  |  | 6678 | 359805.164
(c) | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 2255.2 | 20 | 45104
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 442.63 | 15 | 6639.45 | 15 | 6639.45 | 15 | 6639.45
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 86.99 | 20 | 1739.8 | 20 | 1739.8 | 20 | 1739.8
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 113.32 | 45 | 5099.4 | 45 | 5099.4 | 45 | 5099.4
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 157.95 | 15 | 2369.25 | 15 | 2369.25 | 15 | 2369.25 |  | Max. possibility of 5 Nos tapping in per km line
4 | Universal distribution connector | 7130390006 | Each | 123.62 | 28 | 3461.36 | 28 | 3461.36 | 28 | 3461.36
5 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 609.82 | 14 | 8537.48 | 14 | 8537.48 | 14 | 8537.48
6 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3x25 + 1x16 + 1x25 sqmm. (6% sag) | 7130310032 | Mtr | 83.0779 | 1100 | 91385.69 | 1100 | 91385.69 | 1100 | 91385.69
7 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 455.31 | 12 | 5463.72 | 12 | 5463.72 | 12 | 5463.72
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 72 | 5233.4402 | 72 | 5233.4402 | 72 | 5233.4402
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 12 | 1931.64 | 12 | 1931.64 | 12 | 1931.64
8 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole and @ 0.05 Cmt per pole for base padding of R.S.Joist / H-Beam pole i.e. 9.4 Cmt for RSJ & 13.4 Cmt for H-Beam pole (1:3:6) | 7130200202 | Cmt | 2970 |  |  | 9.4 | 27918 | 13.4 | 39798 | Material cost including GST and labour.
9 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 |  |  |  |  | Material cost including GST and labour.
10 | M.S. Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30
| 12x100 mm | 7130620573 | Kg | 71.59 | 2 | 143.18 | 2 | 143.18 | 2 | 143.18
| 16x40 mm | 7130620609 | Kg | 71.59 | 14 | 1002.26 | 14 | 1002.26 | 14 | 1002.26
| 16x65 mm | 7130620614 | Kg | 70.4 | 14 | 985.6 | 14 | 985.6 | 14 | 985.6
11 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 118.52 | 20 | 2370.4 | 20 | 2370.4 | 20 | 2370.4
12 | Distribution box 3 phase 5 connectors | 7131950012 | No | 1231.19 | 15 | 18467.85 | 15 | 18467.85 | 15 | 18467.85
13 | Stainless steel strap with buckle for installation of Service Distribution Box. | 7130890973 | Set | 60.83 | 15 | 912.45 | 15 | 912.45 | 15 | 912.45
14 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 0 | 0 | 10 | 1514.5 | 10 | 1514.5
15 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 0 | 0 | 10 | 3384 | 10 | 3384
16 | Service Ring | 7130810102 | No | 355.82 | 20 | 7116.4 | 20 | 7116.4 | 20 | 7116.4
17 | PVC insulated single core 16 sq.mm. cable @ 6 mtr. per 3 phase box | 7130311008 | Mtr | 14.1956 | 90 | 1277.5995 | 90 | 1277.5995 | 90 | 1277.5995
18 | Straight through joints | 7130390007 | No | 174.7 | 4 | 698.8 | 4 | 698.8 | 4 | 698.8
19 | End cap for 50/70 Sq.mm | 7130390019 | No | 29.86 | 14 | 418.04 | 14 | 418.04 | 14 | 418.04
20 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.56 | 530 | 2946.8 | 530 | 2946.8 | 530 | 2946.8
21 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 78.5018 | 40 | 3140.0732 | 40 | 3140.0732 | 40 | 3140.0732
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 223396.6829 |  | 367024.0025 |  | 575842.347
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 189319.2228 |  | 311037.2903 |  | 488001.989 | NEW ROW ADDED
24 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 16754.7512 |  | 27526.8002 |  | 43188.176 | Earlier name was - Incidental Charges @ 9%
25 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 210.0559 | 20 | 4201.1188
26 | Labour charges for concreting |  | Cmt | 609.1748 |  |  | 9.4 | 5726.2431 | 13.4 | 8162.9422
27 | Labour charges as per Sch. No.- DL-7 |  |  |  |  | 60994.69 |  | 70232.62 |  | 73660.38
28 | Transportation charges |  |  |  |  | 12852.4377 |  | 14041.193 |  | 14041.193
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 22, 24, 25, 26, 27, 28 |  |  |  |  | 39774.9601 |  | 60568.8573 |  | 89361.8798
30 | Total Estimated Cost excluding GST (Row 23, 24, 25, 26, 27, 28, 29) |  |  |  |  | 323897.1807 |  | 489133.0039 |  | 716416.56
31 | Applicable CGST @ 9% on Row 30 |  |  | 0.09 |  | 29150.7463 |  | 44021.9703 |  | 64477.4904
32 | Applicable SGST @ 9% on Row 30 |  |  | 0.09 |  | 29150.7463 |  | 44021.9703 |  | 64477.4904
33 | Total Estimated Cost including GST (Row 30+31+32) |  |  |  |  | 382198.6732 |  | 577176.9446 |  | 845371.5408
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 382199 |  | 577177 |  | 845372
Note :- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B40: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-6 (2)
COST SCHEDULE -- D-6 (2)
2019-20
1 KM OF 3 PHASE 5 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS. AND R.S. JOIST/H-BEAM POLE SUPPORT USING AB XLPE CABLE WITH MAXIMUM SPAN 50 METER URBAN AREA
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | RS Joist (175X85) mm 9.3 Mtr Long i.e. 19.495 kg/mtr x 9.3 mtr = 181.30 kg x 20 No = 3626.07 Kgs Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | H-BEAM 152x152 mm 37.1 Kg/Mtr 9.0 Mtr long i.e. 408.1 Kg/pole x10 Nos = 4081 Kgs Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | Reason
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 6 | 7 | 6 | 7
1(a) | RS Joist (175X85) mm 9.3 Mtr Long i.e.19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No = 3626.07 Kgs | 7130600675 | Kg | 44.9155 |  |  | 3626.07 | 162866.8196
(b) | H-BEAM 152x152 mm 37.1 Kg /Mtr 9.0 Mtr long i.e. 333.9 Kg/pole x 20 Nos = 6678 Kgs | 7130601958 | Kg | 53.8792 |  |  |  |  | 6678 | 359805.164
(c) | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 2255.2 | 20 | 45104
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 442.63 | 15 | 6639.45 | 15 | 6639.45 | 15 | 6639.45
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 86.99 | 20 | 1739.8 | 20 | 1739.8 | 20 | 1739.8
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 113.32 | 45 | 5099.4 | 45 | 5099.4 | 45 | 5099.4
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 157.95 | 15 | 2369.25 | 15 | 2369.25 | 15 | 2369.25
4 | Universal distribution connector | 7130390006 | Each | 123.62 | 28 | 3461.36 | 28 | 3461.36 | 28 | 3461.36
5 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 609.82 | 14 | 8537.48 | 14 | 8537.48 | 14 | 8537.48
6 | LT 3 phase 5 Wire Aerial Bunched Cable of Size
(a) | 3x70 + 1x16 + 1x50 sqmm. (6% sag) | 7130300025 | Mtr | 180.0798 | 1100 | 198087.78 | 1100 | 198087.78 | 1100 | 198087.78
7 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 455.31 | 12 | 5463.72 | 12 | 5463.72 | 12 | 5463.72
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 72 | 5233.4402 | 72 | 5233.4402 | 72 | 5233.4402
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 12 | 1931.64 | 12 | 1931.64 | 12 | 1931.64
8 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole and @ 0.05 Cmt per pole for base padding of R.S.Joist / H-Beam pole i.e. 9.4 Cmt for RSJ & 13.4 Cmt for H-Beam pole (1:3:6) | 7130200202 | Cmt | 2970 |  |  | 9.4 | 27918 | 13.4 | 39798 | Material cost including GST and labour.
9 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 |  |  |  |  | Material cost including GST and labour.
10 | M.S. Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30
| 12x100 mm | 7130620573 | Kg | 71.59 | 2 | 143.18 | 2 | 143.18 | 2 | 143.18
| 16x40 mm | 7130620609 | Kg | 71.59 | 14 | 1002.26 | 14 | 1002.26 | 14 | 1002.26
| 16x65 mm | 7130620614 | Kg | 70.4 | 14 | 985.6 | 14 | 985.6 | 14 | 985.6
11 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 20 | 2370.4 | 20 | 2370.4 | 20 | 2370.4
12 | Distribution box 3 phase 5 connectors | 7131950012 | No | 1231.19 | 15 | 18467.85 | 15 | 18467.85 | 15 | 18467.85
13 | Stainless steel strap with buckle for installation of Service Distribution Box. | 7130890973 | Set | 60.83 | 15 | 912.45 | 15 | 912.45 | 15 | 912.45
14 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 0 | 0 | 10 | 1514.5 | 10 | 1514.5
15 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 0 | 0 | 10 | 3384 | 10 | 3384
16 | Service Ring | 7130810102 | No | 355.82 | 20 | 7116.4 | 20 | 7116.4 | 20 | 7116.4
17 | PVC insulated single core 16 sq.mm. cable @ 6 mtr. per 3 phase box | 7130311008 | Mtr | 14.1956 | 90 | 1277.5995 | 90 | 1277.5995 | 90 | 1277.5995
18 | Straight through joints | 7130390007 | No | 174.7 | 4 | 698.8 | 4 | 698.8 | 4 | 698.8
19 | End cap for 50/70 Sq.mm | 7130390019 | No | 29.86 | 14 | 418.04 | 42 | 1254.12 | 42 | 1254.12
20 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.56 | 530 | 2946.8 | 530 | 2946.8 | 530 | 2946.8
21 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 78.5018 | 40 | 3140.0732 | 40 | 3140.0732 | 40 | 3140.0732
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 330098.7729 |  | 474562.1725 |  | 683380.517
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 279744.7228 |  | 402171.3327 |  | 579136.0313 | NEW ROW ADDED
24 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 24757.408 |  | 35592.1629 |  | 51253.5388 | Earlier name was - Incidental Charges @ 9%
25 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 210.0559 | 20 | 4201.1188
26 | Labour charges for concreting |  | Cmt | 609.1748 |  |  | 9.4 | 5726.2431 | 13.4 | 8162.9422
27 | Labour charges as per Sch. No.- DL-7 |  |  |  |  | 60994.69 |  | 70232.62 |  | 73660.38
28 | Transportation charges |  |  |  |  | 12852.4377 |  | 14041.193 |  | 14041.193
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 22, 24, 25, 26, 27, 28 |  |  |  |  | 54113.0534 |  | 75019.2989 |  | 103812.3214
30 | Total Estimated Cost excluding GST (Row 23, 24, 25, 26, 27, 28, 29) |  |  |  |  | 436663.4308 |  | 602782.8506 |  | 830066.4067
31 | Applicable CGST @ 9% on Row 30 |  |  | 0.09 |  | 39299.7088 |  | 54250.4566 |  | 74705.9766
32 | Applicable SGST @ 9% on Row 30 |  |  | 0.09 |  | 39299.7088 |  | 54250.4566 |  | 74705.9766
33 | Total Estimated Cost including GST (Row 30+31+32) |  |  |  |  | 515262.8484 |  | 711283.7637 |  | 979478.3599
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 515263 |  | 711284 |  | 979478
Note:- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B40: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-6 (3)
COST SCHEDULE -- D-6 (3)
2019-20
1 KM OF 1 PHASE 3 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS.
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support Using 1100 V grade AB Cable 1x25 + 1x16 + 1x25 sqmm.
[5 empty] | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 2255.2 | 20 | 45104
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 442.63 | 15 | 6639.45
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 86.99 | 20 | 1739.8
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 113.32 | 40 | 4532.8
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 157.95 | 10 | 1579.5
4 | Distribution box 1 phase 9 connectors | 7131950010 | Each | 1022.07 | 20 | 20441.4
5 | Universal distribution connector | 7130390006 | No | 123.62 | 33 | 4079.46
6 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 609.82 | 14 | 8537.48
7 | LT 1 phase 3 Wire AB XLPE Cable 1x25 + 1x16 + 1x25 sqmm. (6% sag) | 7130310063 | Mtr | 45.8253 | 1100 | 50407.83
8 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 455.31 | 12 | 5463.72
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 72 | 5233.4402
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 12 | 1931.64
9 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 | Material cost including GST and labour.
10 | M.S. Nuts and Bolts |  | Kg |  | 30
| 12x100 mm | 7130620573 | Kg | 71.59 | 2 | 143.18
| 16x40 mm | 7130620609 | Kg | 71.59 | 14 | 1002.26
| 16x65 mm | 7130620614 | Kg | 70.4 | 14 | 985.6
11 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 20 | 2370.4
12 | Stainless steel strap with buckle for installation of Service Distribution Box. | 7130890973 | Set | 60.83 | 20 | 1216.6
13 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 3 | 454.35
14 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 3 | 1015.2
15 | Service Ring | 7130810102 | No | 355.82 | 20 | 7116.4
16 | PVC insulated single core 16 sq.mm. cable @ 3 mtr. per 1 phase box | 7130311008 | Mtr | 14.1956 | 60 | 851.733
17 | Straight through joints | 7130390007 | No | 174.7 | 4 | 698.8
18 | End cap for 50/70 Sq.mm | 7130390019 | No | 29.86 | 14 | 418.04
19 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.56 | 530 | 2946.8
20 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 78.5018 | 40 | 3140.0732
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 185001.9564
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 156781.319 | NEW ROW ADDED
23 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 13875.1467 | Earlier name was - Incidental Charges @ 9%
24 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 210.0559 | 20 | 4201.1188
25 | Labour charges as per schedule DL-8 |  |  |  |  | 54309
26 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 12852.4377
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 21, 23, 24, 25, 26 |  |  |  |  | 33779.9575
28 | Total Estimated Cost excluding GST (Row 22, 23, 24, 25, 26, 27) |  |  |  |  | 275798.9798
29 | Applicable CGST @ 9% on Row 28 |  |  | 0.09 |  | 24821.9082
30 | Applicable SGST @ 9% on Row 28 |  |  | 0.09 |  | 24821.9082
31 | Total Estimated Cost including GST (Row 28+29+30) |  |  |  |  | 325442.7962
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 325443
Note:- All the rates are with considering price variation clause.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B36: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-6 (4)
COST SCHEDULE -- D-6 (4)
2019-20
1 Km. OF 3 PHASE 4 WIRE LT LINE WITH AERIAL BUNCH CABLE FOR PUMP CONNECTION UPTO 5 HP & 5 CONNECTION PER KM. WITH MAXIMUM SPAN 50 MTRS.
Sl. No. | Particulars | New Bin Code | Unit | Rate (Rs.) | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3x16 + 1x25 sqmm.
[5 empty] | Qty. | Amt (Rs.)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg., 8.0 Mtrs. long PCC Poles | 7130800012 | No. | 2255.2 | 20 | 45104
2 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No. | 118.52 | 6 | 711.12
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No. | 86.99 | 30 | 2609.7
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 113.32 | 15 | 1699.8
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 157.95 | 24 | 3790.8
4 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3x16 + 1x25 sqmm. (6% sag) | 7130310070 | Mtr | 55.224 | 1100 | 60746.4
5(i) | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet | 7130890007 | Each | 15936.05 | 1 | 15936.05
(ii) | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | 7131950012 | Each | 1231.19 | 5 | 6155.95
6 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 455.31 | 12 | 5463.72
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 72.6867 | 72 | 5233.4402
| (iii) Stay Clamp | 7130810026 | Pair | 160.97 | 12 | 1931.64
7 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 32
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 158 | 44 | 6952 | Material cost including GST and labour.
8 | Concreting of piller box @ 0.5 Cmt per box (1:3:6) | 7130200202 | Cmt | 2970 | 0.5 | 1485 | Material cost including GST and labour.
9 | M.S. Nuts and Bolts
| 12x100 mm | 7130620573 | Kg | 71.59 | 2 | 143.18
| 16x40 mm | 7130620609 | Kg | 71.59 | 14 | 1002.26
| 16x65 mm | 7130620614 | Kg | 70.4 | 14 | 985.6
10 | Universal distribution connector | 7130390006 | Each | 123.62 | 41 | 5068.42
11 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 442.63 | 22 | 9737.86
12 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 609.82 | 22 | 13416.04
13 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 1 | 151.45
14 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 1 | 338.4
15 | Pole Clamp | 7130810077 | No | 447.76 | 44 | 19701.44
16 | Eye Hook | 7130893004 | No | 182.42 | 44 | 8026.48
17 | Service Ring | 7130810102 | No | 355.82 | 30 | 10674.6
18 | Straight through joints | 7130390007 | No | 174.7 | 6 | 1048.2
19 | End cap for 50/70 Sq.mm | 7130390019 | No | 29.86 | 20 | 597.2
20 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5.56 | 530 | 2946.8
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 231657.5502
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 196319.9578 | NEW ROW ADDED
23 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 17374.3163 | Earlier name was - Incidental Charges @ 9%
24 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 210.0559 | 20 | 4201.1188
25 | Labour charges for concreting |  | Cmt | 609.1748 | 0.5 | 304.5874
26 | Labour charges as per Sch. No.- DL-9 |  |  |  |  | 61986
27 | Transportation charges |  |  |  |  | 12852.4377
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 21, 23, 24, 25, 26, 27 |  |  |  |  | 41047.0013
29 | Total Estimated Cost excluding GST (Row 22, 23, 24, 25, 26, 27, 28) |  |  |  |  | 334085.4194
30 | Applicable CGST @ 9% on Row 29 |  |  | 0.09 |  | 30067.6877
31 | Applicable SGST @ 9% on Row 29 |  |  | 0.09 |  | 30067.6877
32 | Total Estimated Cost including GST (Row 29+30+31) |  |  |  |  | 394220.7949
33 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 394221
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B37: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-6 (B)
COST SCHEDULE -- D-6 (B)
2019-20
COST SCHEDULE FOR ADDITIONAL POLES (MID SPAN) FOR LT LINE WITH AB CABLE
S. No. | PARTICULARS | New Bin Code | Unit | Qnty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RSJ (125x70 mm) 9.3 Mtr long @ 13.198 kg | 7130600635 | Kg | 122.74 | 39.5051 | 4848.8609
2 | Concreting of Pole @ 0.05 Cmt for base pad and support @ 0.3 Cmt per pole (1:3:6) | 7130200202 | Cmt | 0.35 | 2970 | 1039.5 | Material cost including GST and labour.
3 (i) | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 1 | 442.63 | 442.63
(ii) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 4 | 86.99 | 347.96
(iii) | Universal distribution connector (1 No. per pole) | 7130390006 | No | 1 | 123.62 | 123.62
4 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | 7131950012 | No | 1 | 1231.19 | 1231.19
5 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 1 | 118.52 | 118.52
6 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 8152.2809
7 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 6908.7126 | NEW ROW ADDED
8 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 611.4211 | Earlier name was - Incidental Charges @ 9%
9 | Labour charges for concreting |  | Cmt | 0.35 | 609.1748 | 213.2112
10 | Labour charges [as per Sch. No.- DL-6(B)] |  |  |  |  | 2002.57
11 | Transportation charges |  |  |  |  | 642.6032
12 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 06, 08, 09, 10, 11 |  |  |  |  | 1452.7608
13 | Total Estimated Cost excluding GST (Row 07, 08, 09, 10, 11, 12) |  |  |  |  | 11831.2789
14 | Applicable CGST @ 9% on Row 13 |  |  |  | 0.09 | 1064.8151
15 | Applicable SGST @ 9% on Row 13 |  |  |  | 0.09 | 1064.8151
16 | Total Estimated Cost including GST (Row 13+14+15) |  |  |  |  | 13960.9091
17 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 13961
Note on B14: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-7
COST SCHEDULE D-7
2019-20
HVDS SYSTEM OF 200 kVA PARENT DTR TAKING 4 Km. LT. TO BE CONVERTED.
S. No. | PARTICULARS | Bin Code | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient)
(i) | 25 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210018 | No | 54301.19 | 5 | 271505.95
(ii) | 16 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210017 | No | 48638.84 | 4 | 194555.36
2 | 140 Kg 8 Mtr. Long PCC Pole (for mid span) | 7130800012 | No | 2255.2 | 10 | 22552
3 | (i) Stay Set 16 mm | 7130860032 | No | 455.31 | 40 | 18212.4
| (ii) Stay Wire 7/10 SWG (5.5 Kg/stay) | 7130860077 | Kg | 72.6867 | 220 | 15991.0674
| (iii) Stay Clamp for 140 kg PCC | 7130810026 | Pair | 160.97 | 40 | 6438.8
4 | Transformer mounting cross arm DC channel 100x50x6 mm. 2.7 mtr long 8' Centre | 7130850201 | Set | 4736.61 | 11 | 52102.71
5 | D.O. Mounting Channel | 7130810509 | Set | 1730.26 | 11 | 19032.86
6 | DC Channel 100x50x6 mm | 7130850201 | Set | 4736.61 | 11 | 52102.71
7 | 11 kV Single pole cut point fitting | 7130810681 | Set | 3361.56 | 10 | 33615.6
8 | 11 kV Strain Hardware set | 7130820241 | No | 123.43 | 60 | 7405.8
9 | 11 kV Polymer Disc Insulator | 7130820010 | No | 119.1 | 60 | 7146
10 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 328.57 | 33 | 10842.81
11 | 11 kV D.O. Fuse Unit | 7131930412 | No | 1177.88 | 33 | 38870.04
12 | Protection cum metering box with 40 amp. MCCB & 4 No. 3 phase meter. |  | No | 16000 | 7 | 112000
13 | Protection cum metering box with 25 amp. MCCB & 3 No. 3 phase meter. |  | No | 13000 | 4 | 52000
14 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 29.2318 | 220 | 6430.9894
15 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 57.6755 | 10400 | 599824.992
16 | G.I. Pipe 40 mm (9 Mtr. per sub-station) | 7130641396 | Mtr | 222.08 | 99 | 21985.92
17 | G.I. Wire 8 SWG | 7130870043 | Kg | 65.0097 | 660 | 42906.3756
18 | 11 kV 'V' Cross arm | 7130810495 | No | 1091.69 | 65 | 70959.85
19 | 11 kV Top Clamp | 7130810679 | No | 306.26 | 65 | 19906.9
20 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 132.09 | 195 | 25757.55
21 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 118.52 | 65 | 7703.8
22 | M.S. Nuts and Bolts |  | Kg |  | 320
| 16x40 mm | 7130620609 | Kg | 71.59 | 50 | 3579.5
| 16x65 mm | 7130620614 | Kg | 70.4 | 100 | 7040
| 16x90 mm | 7130620619 | Kg | 70.4 | 20 | 1408
| 16x140 mm | 7130620625 | Kg | 69.2 | 50 | 3460
| 16x160 mm | 7130620627 | Kg | 69.2 | 50 | 3460
| 16X200 mm | 7130620631 | Kg | 69.2 | 50 | 3460
23 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 50
| RCC Block (with 6 mm MS Bar) ** | 7130640008 | Each | 158 | 90 | 14220 | Material cost including GST and labour.
24 | I- Bolt 16 mm | 7130860017 | No | 108.55 | 77 | 8358.35
25 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 21.0579 | 1200 | 25269.444
26 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1780105.7784
27 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1508564.219 | NEW ROW ADDED
28 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 133507.9334 | Earlier name was - Incidental Charges @ 9%
29 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 210.0559 | 10 | 2100.5594
30 | Labour charges [as per Sch. No.- DL-10] |  |  |  |  | 216311.55
31 | Transportation charges |  |  |  |  | 10924.5762
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 26, 28, 29, 30, 31 |  |  |  |  | 267868.7997
33 | Total Estimated Cost excluding GST (Row 27, 28, 29, 30, 31, 32) |  |  |  |  | 2139277.6377
34 | Applicable CGST @ 9% on Row 33 |  |  | 0.09 |  | 192534.9874
35 | Applicable SGST @ 9% on Row 33 |  |  | 0.09 |  | 192534.9874
36 | Total Estimated Cost including GST (Row 33+34+35) |  |  |  |  | 2524347.6125
37 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 2524348
Note: All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
* | ISI Marked Energy Efficiency level-2 transformer
** | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B43: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-8
COST SCHEDULE D-8
2019-20
HVDS SYSTEM OF 100 kVA PARENT DTR TAKING 3 KM. LT TO BE CONVERTED
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient)
(i) | 25 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210018 | No. | 54301.19 | 2 | 108602.38
(ii) | 16 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210017 | No. | 48638.84 | 3 | 145916.52
2 | 140 Kg 8 Mtr. Long PCC pole (for mid span) | 7130800012 | No. | 2255.2 | 8 | 18041.6
3 | (i) Stay Set 16 mm | 7130860032 | No. | 455.31 | 30 | 13659.3
| (ii) Stay Wire 7/10 (5.5 kg/stay) | 7130860077 | Kg | 72.6867 | 165 | 11993.3005
| (iii) Stay Clamp for 140 kg PCC | 7130810026 | Pair | 160.97 | 30 | 4829.1
4 | Transformer mounting cross arm DC channel 100x50x6 mm. 2.7 mtr long 8' centre | 7130850201 | Set | 4736.61 | 7 | 33156.27
5 | DC Cross arm 100x50x6 mm 8 ' centre 2.7 mtr long | 7130850201 | Set | 4736.61 | 7 | 33156.27
6 | D.O. Mounting Channel | 7130810509 | Set | 1730.26 | 11 | 19032.86
7 | 11 kV Single pole cut point channel | 7130810681 | Set | 3361.56 | 10 | 33615.6
8 | 11 kV Strain Hardware set | 7130820241 | No | 123.43 | 48 | 5924.64
9 | 11 kV Polymer Disc Insulator | 7130820010 | No | 119.1 | 48 | 5716.8
10 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 328.57 | 21 | 6899.97
11 | 11 kV D.O. Set | 7131930412 | No | 1177.88 | 21 | 24735.48
12 | Protection cum metering box with 40 amp. MCCB & 4 No. 3 phase meter for 25 kVA X-mer |  | No | 16000 | 3 | 48000
13 | Protection cum metering box with 25 amp. MCCB & 3 No. 3 phase meter for 16 kVA X-mer |  | No | 13000 | 4 | 52000
14 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 29.2318 | 140 | 4092.4478
15 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 57.6755 | 1820 | 104969.3736
16 | G.I. Pipe 40 mm (5 Mtr. per substation) | 7130641396 | Mtr | 222.08 | 63 | 13991.04
17 | G.I. Wire 8 SWG | 7130870043 | Kg | 65.0097 | 180 | 11701.7388
18 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1091.69 | 45 | 49126.05
19 | 11 kV Top clamp | 7130810679 | No | 306.26 | 45 | 13781.7
20 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 132.09 | 135 | 17832.15
21 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 45 | 5333.4
22 | M.S. Nuts and Bolts |  | Kg |  | 250
| 16x40 mm | 7130620609 | Kg | 71.59 | 40 | 2863.6
| 16x65 mm | 7130620614 | Kg | 70.4 | 80 | 5632
| 16x90 mm | 7130620619 | Kg | 70.4 | 10 | 704
| 16x140 mm | 7130620625 | Kg | 69.2 | 40 | 2768
| 16x160 mm | 7130620627 | Kg | 69.2 | 40 | 2768
| 16X200 mm | 7130620631 | Kg | 69.2 | 40 | 2768
23 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 38
| RCC Block (with 6 mm MS Bar) ** | 7130640008 | Each | 158 | 68 | 10744 | Material cost including GST and labour.
24 | I - Bolt 16 mm | 7130860017 | No | 108.55 | 21 | 2279.55
25 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 21.0579 | 900 | 18952.083
26 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 835587.2238
27 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 708124.7659 | NEW ROW ADDED
28 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 62669.0418 | Earlier name was - Incidental Charges @ 9%
29 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 210.0559 | 8 | 1680.4475
30 | Labour charges [as per Sch. No.- DL-11] |  |  |  |  | 158745.17
31 | Transportation charges |  |  |  |  | 8739.6568
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 26, 28, 29, 30, 31 |  |  |  |  | 133427.6925
33 | Total Estimated Cost excluding GST (Row 27, 28, 29, 30, 31, 32) |  |  |  |  | 1073386.7745
34 | Applicable CGST @ 9% on Row 33 |  |  | 0.09 |  | 96604.8097
35 | Applicable SGST @ 9% on Row 33 |  |  | 0.09 |  | 96604.8097
36 | Total Estimated Cost including GST (Row 33+34+35) |  |  |  |  | 1266596.3939
37 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1266596
Note: All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
* | ISI Marked Energy Efficiency level-2 transformer
** | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B43: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-9
COST SCHEDULE D-9
2019-20
HVDS SYSTEM OF 63 kVA PARENT DTR TAKING 2 KM. LT TO BE CONVERTED
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Energy efficient)
(i) | 25 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210018 | No | 54301.19 | 1 | 54301.19
(ii) | 16 kVA TRANSFORMER (LEVEL-2) * Aluminium Wound | 7132210017 | No | 48638.84 | 2 | 97277.68
2 | 140 Kg 8 Mtr. Long PCC Pole (for mid span) | 7130800012 | No | 2255.2 | 6 | 13531.2
3 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 455.31 | 25 | 11382.75
| (ii) Stay Wire 7/10 SWG (5.5 kg/stay) | 7130860077 | Kg | 72.6867 | 137.5 | 9994.4171
| (iii) Stay Clamp for 140 kg PCC Pole | 7130810026 | Pair | 160.97 | 25 | 4024.25
4 | Transformer mounting arrangement DC cross arm 100x50x6 mm. 2.7 mtr long 8' Centre | 7130850201 | Set | 4736.61 | 5 | 23683.05
5 | DC cross arm 100x50x6 mm 8 ' Centre 2.7 mtr long | 7130850201 | Set | 4736.61 | 5 | 23683.05
6 | DO Mounting Channel | 7130810509 | Set | 1730.26 | 5 | 8651.3
7 | 11 kV Single Pole cut point channel | 7130810681 | Set | 3361.56 | 10 | 33615.6
8 | 11 kV Strain Hardware set | 7130820241 | Set | 123.43 | 36 | 4443.48
9 | 11 kV Polymer Disc Insulator | 7130820010 | No | 119.1 | 36 | 4287.6
10 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 328.57 | 15 | 4928.55
11 | 11 kV D.O. Set | 7131930412 | No | 1177.88 | 15 | 17668.2
12 | Protection cum metering box with 40 Amp. MCCB & 4 No. 3 phase meter for 25 kVA X-mer |  | No | 16000 | 2 | 32000
13 | Protection cum metering box with 25 Amp. MCCB & 3 No. 3 phase meter for 16 kVA X-mer |  | No | 13000 | 3 | 39000
14 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 29.2318 | 100 | 2923.177
15 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 57.6755 | 1300 | 74978.124
16 | G.I. Pipe 40 mm (5 Mtr. per Sub-station) | 7130641396 | Mtr | 222.08 | 45 | 9993.6
17 | G.I. Wire 8 SWG | 7130870043 | Kg | 65.0097 | 130 | 8451.2558
18 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1091.69 | 45 | 49126.05
19 | 11 kV Top clamp | 7130810679 | No | 306.26 | 45 | 13781.7
20 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 132.09 | 135 | 17832.15
21 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 118.52 | 45 | 5333.4
22 | M.S. Nuts and Bolts |  | Kg |  | 190
| 16x40 mm | 7130620609 | Kg | 71.59 | 30 | 2147.7
| 16x65 mm | 7130620614 | Kg | 70.4 | 60 | 4224
| 16x90 mm | 7130620619 | Kg | 70.4 | 10 | 704
| 16x140 mm | 7130620625 | Kg | 69.2 | 30 | 2076
| 16x160 mm | 7130620627 | Kg | 69.2 | 30 | 2076
| 16X200 mm | 7130620631 | Kg | 69.2 | 30 | 2076
23 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  |  | 31
| RCC Block (with 6 mm MS Bar) ** | 7130640008 | Each | 158 | 56 | 8848 | Material cost including GST and labour.
24 | I - Bolt 16 mm | 7130860017 | No | 108.55 | 10 | 1085.5
25 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 21.0579 | 600 | 12634.722
26 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 600763.6959
27 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 509121.7762 | NEW ROW ADDED
28 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 45057.2772 | Earlier name was - Incidental Charges @ 9%
29 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 210.0559 | 6 | 1260.3357
30 | Labour charges [as per Sch. No.- DL-12] |  |  |  |  | 119916.36
31 | Transportation charges |  |  |  |  | 6554.7478
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 26, 28, 29, 30, 31 |  |  |  |  | 96694.0521
33 | Total Estimated Cost excluding GST (Row 27, 28, 29, 30, 31, 32) |  |  |  |  | 778604.5489
34 | Applicable CGST @ 9% on Row 33 |  |  | 0.09 |  | 70074.4094
35 | Applicable SGST @ 9% on Row 33 |  |  | 0.09 |  | 70074.4094
36 | Total Estimated Cost including GST (Row 33+34+35) |  |  |  |  | 918753.3677
37 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 918753
Note:- | All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
* | ISI Marked Energy Efficiency level-2 transformer
** | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B43: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-10
COST SCHEDULE D-10
2019-20
CONVERSION OF 1 KM LT LINE INTO 11 kV LINE
S. No. | PARTICULARS | New Bin Code | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Poles (for where ever required ) | 7130800012 | No | 1 | 2255.2 | 2255.2
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 17 | 1091.69 | 18558.73
3 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 17 | 306.26 | 5206.42
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 17 | 118.52 | 2014.84
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 51 | 132.09 | 6736.59
6 | Jointing sleeves suitable for Weasel/ Rabbit conductor | 7130830854 | No | 6 | 30.07 | 180.42
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 151.45 | 454.35
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 338.4 | 1015.2
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 17 | 78.5018 | 1334.5311
10 | Danger Board | 7130880041 | No | 17 | 92.6 | 1574.2
11 | Binding wires & tape | 7130830006 | Kg | 5 | 160.41 | 802.05
12 | Nuts and bolts
| 16x90 mm | 7130620619 | Kg | 2 | 70.4 | 140.8
| 16x160 mm | 7130620627 | Kg | 17 | 69.2 | 1176.4
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | Set | 1 | 2588.62 | 2588.62
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 65.0097 | 2275.3381
| (iii) Stay clamp (Pair) H.T. | 7130810026 | No | 2 | 300.41 | 600.82
| (iv) Stay wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 72.6867 | 799.5534
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 455.31 | 910.62
| (vi) I - Bolt big size. | 7130620013 | No | 4 | 128.08 | 512.32
14 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  | 3
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 5 | 158 | 790 | Material cost including GST and labour.
15 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 49927.0026
16 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 42311.0191 | NEW ROW ADDED
17 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 3744.5252 | Earlier name was - Incidental Charges @ 9%
18 | Back filling of poles with boulders @ of 0.3 Cmt per pole |  | No | 1 | 210.0559 | 210.0559
19 | Labour charges as per Schedule No. DL-3 (E-1) |  |  |  |  | 35110.23
20 | Transport charges upto 50 Kms. Average lead from area store to const. camping site transport |  |  |  |  | 4260.5856
21 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 15, 17,18, 19, 20 |  |  |  |  | 11656.5499
22 | Total Estimated Cost excluding GST (Row 16, 17, 18, 19, 20, 21) |  |  |  |  | 97292.9657
23 | Applicable CGST @ 9% on Row 22 |  |  |  | 0.09 | 8756.3669
24 | Applicable SGST @ 9% on Row 22 |  |  |  | 0.09 | 8756.3669
25 | Total Estimated Cost including GST (Row 22+23+24) |  |  |  |  | 114805.6996
26 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 114806
Note:- | (i) Three wire LT line will be utilized for converting into 11 kV line.
(ii) For replacement of deteriorated conductor of LT line suitable provision should be made while preparing the estimates
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B30: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D22: Barun Chakraborty Earlier unit was - No.

## D-11
COST SCHEDULE D-11
2019-20
LT LINE CONVERSION USING RABBIT CONDUCTOR MAXIMUM SPAN OF 45 MTRS.
S. No. | PARTICULARS | New Bin code | Unit | Rate | 1 Phase 2 Wire to 1 Phase 3 Wire Conversion |  | 1 Phase 2 Wire to 3 Phase 4 Wire Conversion |  | 1 Phase 3 Wire to 3 Phase 4 Wire Conversion |  | 1 Phase 3 Wire to 3 Phase 5 Wire Conversion
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | LT Three Pin cross arm | 7130810413 | No | 643.77 | 24 | 15450.48
2 | LT Four Pin cross arm | 7130810441 | No | 766.7 |  |  | 24 | 18400.8 | 24 | 18400.8
3 | LT Five Pin cross arm | 7130810461 | No | 889.61 | [6 empty] | 24 | 21350.64
4 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 13.06 | 24 | 313.44 | 48 | 626.88 | 24 | 313.44 | 48 | 626.88
5 | Hardware for Shackle Insulator | 7130820216 | No | 41.94 | 8 | 335.52 | 16 | 671.04 | 8 | 335.52 | 16 | 671.04
6 | ACSR RABBIT Conductor including 3% Sag | 7130830057 | Mtr | 34.7014 | 1030 | 35742.4111 | 2060 | 71484.8222 | 1030 | 35742.4111 | 2060 | 71484.8222
7 | Split insulator for guarding | 7130820018 | Pair | 4.18 | 40 | 167.2 | 40 | 167.2 | 40 | 167.2 | 40 | 167.2
8 | M.S. Nuts & bolts
| 12x100 mm | 7130620573 | Kg | 71.59 | 4 | 286.36 | 8 | 572.72 | 4 | 286.36 | 8 | 572.72
| 16x40 mm | 7130620609 | Kg | 71.59 | 4 | 286.36 | 6 | 429.54 | 4 | 286.36 | 6 | 429.54
| 16x140 mm | 7130620625 | Kg | 69.2 | 10 | 692 | 10 | 692 | 10 | 692 | 10 | 692
| 16x65 mm | 7130620614 | Kg | 70.4 | 6 | 422.4 | 6 | 422.4 | 6 | 422.4 | 6 | 422.4
9 | Red Oxide Paint | 7130211158 | Ltr | 151.45 | 1 | 151.45 | 1 | 151.45 | 1 | 151.45 | 1 | 151.45
10 | Aluminium Paint | 7130210809 | Ltr | 338.4 | 1 | 338.4 | 1 | 338.4 | 1 | 338.4 | 1 | 338.4
11 | G.I. Wire 4 mm for guarding | 7130870043 | Kg | 65.0097 | 6 | 390.058 | 7.5 | 487.5725 | 7.5 | 487.5725 | 7.5 | 487.5725
12 | Clamp for R.S. Joist or PCC 140 Kg./8 mtr long | 7130810216 | Pair | 319.69 | 20 | 6393.8 | 20 | 6393.8 | 20 | 6393.8 | 20 | 6393.8
13 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 60969.8791 |  | 100838.6246 |  | 64017.7136 |  | 103788.4646
14 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 51669.389 |  | 85456.4616 |  | 54252.2996 |  | 87956.326 | NEW ROW ADDED
15 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  | 0.075 |  | 4572.7409 |  | 7562.8968 |  | 4801.3285 |  | 7784.1348 | Earlier name was - Incidental Charges @ 9%
16 | Labour Charges as per DL-4. |  |  |  |  | 14264.1 |  | 20706.35 |  | 14264.1 |  | 20706.35
17 | Transportation Charges |  |  |  |  | 3408.4705 |  | 4047.5568 |  | 3408.4705 |  | 4047.5568
18 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 13, 15, 16, 17 |  |  |  |  | 10401.8988 |  | 16644.4285 |  | 10811.4516 |  | 17040.8133
19 | Total Estimated Cost excluding GST (Row 14, 15, 16, 17, 18) |  |  |  |  | 84316.5993 |  | 134417.6938 |  | 87537.6502 |  | 137535.1809
20 | Applicable CGST @ 9% on Row 19 |  |  | 0.09 |  | 7588.4939 |  | 12097.5924 |  | 7878.3885 |  | 12378.1663
21 | Applicable SGST @ 9% on Row 19 |  |  | 0.09 |  | 7588.4939 |  | 12097.5924 |  | 7878.3885 |  | 12378.1663
22 | Total Estimated Cost including GST (Row 19+20+21) |  |  |  |  | 99493.5872 |  | 158612.8786 |  | 103294.4273 |  | 162291.5135
23 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 99494 |  | 158613 |  | 103294 |  | 162292
Note on B24: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## D-12
COST SCHEDULE D-12 ( E-2)
2019-20
CONVERSION OF 1 KM 1 PHASE 3 WIRE LT LINE INTO 11 kV LINE
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Pole (for where ever required ) | 7130800012 | No | 1 | 2255.2 | 2255.2
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 22 | 1091.69 | 24017.18
3 | 11 kV Top clamp Angle type with cleat. | 7130810679 | No | 22 | 306.26 | 6737.72
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 22 | 118.52 | 2607.44
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 66 | 132.09 | 8717.94
6 | Jointing sleeves suitable for weasel / rabbit conductor | 7130830854 | No | 6 | 30.07 | 180.42
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 151.45 | 454.35
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 338.4 | 1015.2
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 22 | 78.5018 | 1727.0403
10 | Danger Board | 7130880041 | No | 22 | 92.6 | 2037.2
11 | Binding wire & tape | 7130830006 | Kg | 5 | 160.41 | 802.05
12 | Nuts and Bolts
| 16x90 mm | 7130620619 | Kg | 2 | 70.4 | 140.8
| 16x160 mm | 7130620627 | Kg | 17 | 69.2 | 1176.4
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | Set | 12 | 2588.62 | 31063.44
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 441 | 65.0097 | 28669.2601
| (iii) Stay Clamp (Pair) H.T. | 7130810026 | No | 2 | 300.41 | 600.82
| (iv) Stay Wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 72.6867 | 799.5534
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 455.31 | 910.62
| (vi) I- Bolt big size. | 7130620013 | No. | 4 | 128.08 | 512.32
14 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  | 3
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 5 | 158 | 790 | Material cost including GST and labour.
15 | PVC Insulated cable 16 sqmm 1 core unarmoured | 7130311008 | Mtr. | 2104 | 14.1956 | 29867.4372
16 | ACSR Conductor 20 sqmm. Al. Eq. for neutral | 7130830053 | Mtr | 1030 | 14.289 | 14717.6803
17 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 159800.0712
18 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 135423.7891 | NEW ROW ADDED
19 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 11985.0053 | Earlier name was - Incidental Charges @ 9%
20 | Back filling of pole with boulders @ 0.3 Cmt. per pole. |  | No. | 1 | 210.0559 | 210.0559
21 | Labour charges as per Schedule No. DL-5 ( E-2) |  |  |  |  | 51460.47
22 | Transport charges upto 50 Kms. Average lead from Area Store to construction camping site transport |  |  |  |  | 4260.5856
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 17, 19, 20, 21, 22 |  |  |  |  | 28464.5235
24 | Total Estimated Cost excluding GST (Row 18, 19, 20, 21, 22, 23) |  |  |  |  | 231804.4295
25 | Applicable CGST @ 9% on Row 24 |  |  |  | 0.09 | 20862.3987
26 | Applicable SGST @ 9% on Row 24 |  |  |  | 0.09 | 20862.3987
27 | Total Estimated Cost including GST (Row 24+25+26) |  |  |  |  | 273529.2268
28 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 273529
Note:- | (1) In 1 Phase 3 Wire L.T. three wire conductor will be reutilised.
(2) In Case of replacement of Old conductor, new conductor may be incorporated in the estimate and depreciated value will be accounted for in the estimate.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B32: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D22: Barun Chakraborty Earlier unit was - No.

## D-13
COST SCHEDULE D-13 (E-3)
2019-20
CONVERSION OF 1 kM 3 PHASE 5 WIRE LT LINE INTO 11 kV LINE
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Pole (for where ever required) | 7130800012 | No | 1 | 2255.2 | 2255.2
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 22 | 1091.69 | 24017.18
3 | 11 kV Top Clamp Angle type with cleat. | 7130810679 | No | 22 | 306.26 | 6737.72
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 22 | 118.52 | 2607.44
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 66 | 132.09 | 8717.94
6 | Jointing sleeves suitable for weasel / rabbit conductor | 7130830854 | No | 6 | 30.07 | 180.42
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 151.45 | 454.35
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 338.4 | 1015.2
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 22 | 78.5018 | 1727.0403
10 | Danger Board | 7130880041 | No | 22 | 92.6 | 2037.2
11 | Binding wire & tape | 7130830006 | Kg | 5 | 160.41 | 802.05
12 | Nuts and Bolts
| 16x90 mm | 7130620619 | kg | 2 | 70.4 | 140.8
| 16x160 mm | 7130620627 | kg | 17 | 69.2 | 1176.4
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | Set | 23 | 2588.62 | 59538.26
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 441 | 65.0097 | 28669.2601
| (iii) Stay Clamp (Pair) H.T. | 7130810026 | No | 2 | 300.41 | 600.82
| (iv) Stay Wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 72.6867 | 799.5534
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 455.31 | 910.62
| (vi) I-Bolt big size. | 7130620013 | No. | 4 | 128.08 | 512.32
14 | Use of R.C.C. Block for base padding of PCC pole @ 01 No. / pole and for stay set @ 02 Nos. per stay set. |  |  | 3
| RCC Block (with 6 mm MS Bar) * | 7130640008 | Each | 5 | 158 | 790 | Material cost including GST and labour.
15 | PVC insulated cable 16 sqmm 1 core unarmoured | 7130311008 | Mtr. | 2104 | 14.1956 | 29867.4372
16 | ACSR Conductor 20 sqmm. Al. Eq. for neutral | 7130830053 | Mtr | 1030 | 14.289 | 14717.6803
17 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 188274.8912
18 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 159554.9925 | NEW ROW ADDED
19 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 14120.6168 | Earlier name was - Incidental Charges @ 9%
20 | Back filling of pole with boulders @ 0.3 Cmt. per pole. |  | No. | 1 | 210.0559 | 210.0559
21 | Labour charges as per Schedule No. DL-6 (E-3) |  |  |  |  | 53738.45
22 | Transport charges upto 50 Kms. Average lead from Area Store to construction camping site transport |  |  |  |  | 4260.5856
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 17, 19, 20, 21, 22 |  |  |  |  | 32575.5749
24 | Total Estimated Cost excluding GST (Row 18, 19, 20, 21, 22, 23) |  |  |  |  | 264460.2758
25 | Applicable CGST @ 9% on Row 24 |  |  |  | 0.09 | 23801.4248
26 | Applicable SGST @ 9% on Row 24 |  |  |  | 0.09 | 23801.4248
27 | Total Estimated Cost including GST (Row 24+25+26) |  |  |  |  | 312063.1255
28 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 312063
Note:- | (1) In 3 Phase 5 Wire LT system, 5th conductor i.e. neutral conductor and 4th conductor will be returned to Area Stores and depreciated value of neutral conductor will be accounted for at the time of estimate framing. L.T. Phase conductor will be reutilised.
(2) In case of replacement of Old conductor, new conductor may be incorporated in the estimate and depreciated value will be accounted for in the estimate.
* | One No. RCC Block for base padding and two numbers for stay set (except DP Structure)
Note on B32: Barun Chakraborty: Earlier name was - SUB TOTAL-1
Note on D22: Barun Chakraborty Earlier unit was - No.

## D-14
COST SCHEDULE -- D-14
DISTRIBUTION BOX ON EXISTING LT LINES FOR SERVICE CONNECTIONS
2019-20
S. No. | DESCRIPTION | Bin Code No | Unit | Rate per Distribution Box including GST | Rate per Distribution Box excluding GST [Col. 5/1.18] | Incidental Charges (7.5%) on Col. 5 | Labour Charges per Distribution Box | Total Cost per Distribution Box excluding GST [Col. 6+7+8] | Applicable CGST @ 9% on Col. 9 | Applicable SGST @ 9% on Col. 9 | Total Cost per Distribution Box including GST [ Col. 9+10+11] | Total Cost per Distribution Box including GST Rounded Off
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | Single phase Distribution box for 9 connections | 7131950010 | Nos. | 1022.07 | 866.161 | 76.6552 | 142.4097 | 1085.226 | 97.6703 | 97.6703 | 1280.5667 | 1281
2 | Three phase Distribution box for 5 connections | 7131950012 | Nos. | 1231.19 | 1043.3814 | 92.3393 | 142.4097 | 1278.1303 | 115.0317 | 115.0317 | 1508.1938 | 1508
| Incidental Charges @ 7.5% : - |  |  | 7.5% | [8 empty] | Earlier name was - Incidental Charges @ 9%
Note on E8: Barun Chakraborty: Earlier name was - Rate per Distribution Box
Note on G8: Barun Chakraborty: Earlier name was - Incidental Charges (9%)
Note on I8: Barun Chakraborty: Earlier name was - Cost per Distribution Box

## E-1
COST SCHEDULE -- E-1
METERING OF 11/0.4 kV DISTRIBUTION TRANSFORMER (TO BE SUPPLEMENTED WITH COST SCHEDULE C-7 (A1, A2, B1, B2, C1, C2)
2019-20
S. No. | PARTICULARS | Bin Code No | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1(a) | Poly phase static energy meter 10-60 Amp. with meter box | 7131300046 | No | 1 | 1778 | --
1(b) | CT operated electronic static meters 100/5 Amp. With data storage. | 7131310997 | No | 1 | 1805 | 1805 | 1 | 1805 | 1805 | 1 | 1805 | 1805 | 1 | 1805 | 1805 | Name changed
2 | LT CT :-
| (i) 100/5 Amp. | 7132230016 | No | 4 | 356.08 | 1424.32 | 4 | 356.08 | 1424.32 | -- | -- | -- | -- | -- | --
| (ii) 200/5 Amp. | 7132230019 | No | -- | -- | -- | -- | -- | -- | 4 | 356.08 | 1424.32 | -- | -- | --
| (iii) 300/5 Amp. | 7132230021 | No | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | 285.09 | 1140.36
3 | Meter Box (G.I. Plain sheet) for 3 Phase LT CT operated meter. | 7132406420 | No | 1 | 2662.68 | 2662.68 | 1 | 2662.68 | 2662.68 | 1 | 2662.68 | 2662.68 | 1 | 2662.68 | 2662.68
4 | Copper control cable 4 core 2.5 sq.mm Unarmoured | 7130310654 | Mtr | 12 | 68.1431 | 817.7167 | 12 | 68.1431 | 817.7167 | 12 | 68.1431 | 817.7167 | 12 | 68.1431 | 817.7167
5 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 6709.7167 |  |  | 6709.7167 |  |  | 6709.7167 |  |  | 6425.7567
6 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 5686.2006 |  |  | 5686.2006 |  |  | 5686.2006 |  |  | 5445.5565 | NEW ROW ADDED
7 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 503.2288 |  | 0.075 | 503.2288 |  | 0.075 | 503.2288 |  | 0.075 | 481.9318 | Earlier name was - Incidental Charges @ 9%
8 | Labour & Transportation charges |  |  |  |  | 2577.6542 |  |  | 2577.6542 |  |  | 2577.6542 |  |  | 2577.6542
9 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 5, 7, 8 |  |  |  |  | 1223.825 |  |  | 1223.825 |  |  | 1223.825 |  |  | 1185.6678
10 | Total Estimated Cost excluding GST (Row 6,7,8, 9) |  |  |  |  | 9990.9085 |  |  | 9990.9085 |  |  | 9990.9085 |  |  | 9690.8103
11 | Applicable CGST @ 9% on Row 10 |  |  |  | 0.09 | 899.1818 |  | 0.09 | 899.1818 |  | 0.09 | 899.1818 |  | 0.09 | 872.1729
12 | Applicable SGST @ 9% on Row 10 |  |  |  | 0.09 | 899.1818 |  | 0.09 | 899.1818 |  | 0.09 | 899.1818 |  | 0.09 | 872.1729
13 | Total Estimated Cost including GST (Row 10+11+12) |  |  |  |  | 11789.2721 |  |  | 11789.2721 |  |  | 11789.2721 |  |  | 11435.1562
14 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 11789 |  |  | 11789 |  |  | 11789 |  |  | 11435
Note:- All the rates are with considering price variation clause.
38
Note on B11: Barun Chakraborty: Earlier name was - CT operated electronic static meter 100/5 Amp.
Note on B18: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## E-2
COST SCHEDULE -- E-2
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| SINGLE PHASE CONNECTION |  |  |  |  | 2019-20
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT Single Phase Static Meter 5-30 Amps. Pilfer Proof with transparent polycarbonate meter box | 7131300500 | No | 1 | 752.99 | 752.99 | 752.99 | 752.99
2 | Armoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130311025 | Mtr | 30 | 40.3 | 1209
3 | Unarmoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130310039 | Mtr | 30 |  |  | 30.01 | 900.3
4 | LT Shackle Insulator 65x50 mm | 7130820101 | No | 2 | 11.68 | 23.36 | 11.68 | 23.36
5 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No | 2 | 36.84 | 73.68 | 36.84 | 73.68
6 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | 7132406022 | No | 1 | 151.91 | 151.91 | 151.91 | 151.91
7 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.75 | 14.75 | 14.75 | 14.75 | RATE EXCLUDING G.S.T.
8 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 40 | 40 | 40 | 40
9 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
10 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 2295.69 |  | 1986.99
11 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1945.5 |  | 1683.8898 | NEW ROW ADDED
12 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 172.1767 | 0.075 | 149.0242 | Earlier name was - Incidental Charges @ 9%
13 | Labour Charges |  | Per Installation |  |  | 265.5939 |  | 265.5939
14 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 10, 12, 13 |  |  |  |  | 341.6826 |  | 300.201
15 | Total Estimated Cost excluding GST (Row 11, 12, 13, 14) |  |  |  |  | 2724.9532 |  | 2398.709
16 | Applicable CGST @ 9% on Row 15 |  |  |  | 0.09 | 245.2458 | 0.09 | 215.8838
17 | Applicable SGST @ 9% on Row 15 |  |  |  | 0.09 | 245.2458 | 0.09 | 215.8838
18 | Total Estimated Cost including GST (Row 15+16+17) |  |  |  |  | 3215.4448 |  | 2830.4766
19 | Cost for meter replacement of a Single Phase Consumer |  |  |  |  | 3215.4448 |  | 2830.4766
20 | Cost for meter replacement of a Single Phase Consumer (Round off) |  |  |  |  | 3215 |  | 2830
Note on B19: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## E-3
COST SCHEDULE -- E-3
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| THREE PHASE CONNECTION |  |  |  |  | 2019-20
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT 3 phase electronic energy meter 10-60 Amps. with poly carbonate meter box | 7131300046 | No. | 1 | 1778 | 1778 | 1778 | 1778
2 | Armoured Service Cable - Three Phase, 4 core-10 sq mm | 7130311028 | Mtr | 30 | 70.24 | 2107.2
3 | Unarmoured Service Cable - Three Phase, 4 core-10 sq mm | 7130310040 | Mtr | 30 |  |  | 62.18 | 1865.4
4 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 11.68 | 23.36 | 11.68 | 23.36
5 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 36.84 | 73.68 | 36.84 | 73.68
6 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | 7132455002 | Nos | 1 | 317.74 | 317.74 | 317.74 | 317.74
7 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.75 | 14.75 | 14.75 | 14.75 | RATE EXCLUDING G.S.T.
8 | Misc Items , e.g., Screw, cut-outs |  | Lot | 1 | 40 | 40 | 40 | 40
9 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
10 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 4384.73 |  | 4142.93
11 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 3715.8729 |  | 3510.9576 | NEW ROW ADDED
12 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 328.8548 | 0.075 | 310.7197 | Earlier name was - Incidental Charges @ 9%
13 | Labour Charges |  | Per Installation |  |  | 424.9502 |  | 424.9502
14 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 10, 12, 13 |  |  |  |  | 642.3169 |  | 609.825
15 | Total Estimated Cost excluding GST (Row 11, 12, 13, 14) |  |  |  |  | 5111.9947 |  | 4856.4525
16 | Applicable CGST @ 9% on Row 15 |  |  |  | 0.09 | 460.0795 | 0.09 | 437.0807
17 | Applicable SGST @ 9% on Row 15 |  |  |  | 0.09 | 460.0795 | 0.09 | 437.0807
18 | Total Estimated Cost including GST (Row 15+16+17) |  |  |  |  | 6032.1537 |  | 5730.614
19 | Cost for meter replacement of a Three Phase Consumer |  |  |  |  | 6032.1537 |  | 5730.614
20 | Cost for meter replacement of a Three Phase Consumer (Round Off) |  |  |  |  | 6032 |  | 5731
| No of Consumers for Meter Replacement |  |  | 100
| Total Cost |  |  |  |  | 603215.3712 |  | 573061.4
| Total Cost Round Off |  |  |  |  | 603215 |  | 573061
Note on B19: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## E-4
COST SCHEDULE -- E-4
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| THREE PHASE CONNECTION CT- OPERATED METERS |  |  |  |  | 2019-20
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Rate | Amount
1 | CT operated electronic static meters 100/5 Amp. With data storage. | 7131310997 | No. | 1 | 1805 | 1805 | Name changed
2 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.75 | 14.75 | RATE EXCLUDING G.S.T.
3 | Misc Items , e.g., Screw, cut-outs |  | Lot | 1 | 40 | 40
4 | M-Seal |  | Lot | 1 | 30 | 30
5 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1889.75
6 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1601.4831 | NEW ROW ADDED
7 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 141.7312 | Earlier name was - Incidental Charges @ 9%
8 | Labour Charges |  | Per Installation |  |  | 424.9502
9 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 5, 7, 8 |  |  |  |  | 307.0539
10 | Total Estimated Cost excluding GST (Row 11, 12, 13, 14) |  |  |  |  | 2475.2184
11 | Applicable CGST @ 9% on Row 10 |  |  |  | 0.09 | 222.7697
12 | Applicable SGST @ 9% on Row 10 |  |  |  | 0.09 | 222.7697
13 | Total Estimated Cost including GST (Row 10+11+12) |  |  |  |  | 2920.7577
14 | Cost for meter replacement of Three Phase Consumer CT Operated Meters |  |  |  |  | 2920.7577
15 | Cost for meter replacement of 3- Phase Consumer CT Operated Meters (Round Off) |  |  |  |  | 2921
Note on B8: Barun Chakraborty: Earlier name was - CT operated electronic static meter 100/5 Amp.
Note on B12: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## E-5
COST SCHEDULE -- E-5
METER SHIFTING OF SINGLE PHASE CONSUMER TO OUTSIDE OF PREMISES WITH NEW SERVICE CABLE
| SINGLE PHASE CONNECTION | [5 empty] | 2019-20
S. No. | PARTICULARS | Bin Code No. | Unit | Qty. | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Armoured Service Cable - Single Phase, 2 core- 6 sq. mm. | 7130311025 | Mtr | 30 | 40.3 | 1209
2 | Unarmoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130310039 | Mtr | 30 |  |  | 30.01 | 900.3
3 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 11.68 | 23.36 | 11.68 | 23.36
4 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 36.84 | 73.68 | 36.84 | 73.68
5 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | 7132406022 | Nos | 1 | 151.91 | 151.91 | 151.91 | 151.91
6 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.75 | 14.75 | 14.75 | 14.75 | RATE EXCLUDING G.S.T.
7 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 40 | 40 | 40 | 40
8 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
9 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1542.7 |  | 1234
10 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1307.3729 |  | 1045.7627 | NEW ROW ADDED
11 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 115.7025 | 0.075 | 92.55 | Earlier name was - Incidental Charges @ 9%
12 | Labour Charges |  | Per Installation |  |  | 265.5939 |  | 265.5939
13 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 9, 11, 12 |  |  |  |  | 240.4995 |  | 199.018
14 | Total Estimated Cost excluding GST (Row 10, 11, 12, 13) |  |  |  |  | 1929.1688 |  | 1602.9246
15 | Applicable CGST @ 9% on Row 14 |  |  |  | 0.09 | 173.6252 | 0.09 | 144.2632
16 | Applicable SGST @ 9% on Row 14 |  |  |  | 0.09 | 173.6252 | 0.09 | 144.2632
17 | Total Estimated Cost including GST (Row 14+15+16) |  |  |  |  | 2276.4192 |  | 1891.451
18 | Cost for meter shifting of a Single Phase Consumer |  |  |  |  | 2276.4192 |  | 1891.451
19 | Cost for meter shifting of a Single Phase Consumer (Round Off) |  |  |  |  | 2276 |  | 1891
Note on B18: Barun Chakraborty: Earlier name was - SUB TOTAL-1

## E-6
COST SCHEDULE -- E-6
METER SHIFTING OF THREE PHASE CONSUMER TO OUTSIDE OF PREMISES WITH NEW SERVICE CABLE
| THREE PHASE CONNECTION | [5 empty] | 2019-20
S. No. | PARTICULARS | Bin Code No. | Unit | Qty. | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Armoured Service Cable - Three Phase, 4 core-10 sq mm | 7130311028 | Mtr | 30 | 70.24 | 2107.2
2 | Unarmoured Service Cable - Three Phase, 4 core-10 sq mm | 7130310040 | Mtr | 30 |  |  | 62.18 | 1865.4
3 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 11.68 | 23.36 | 11.68 | 23.36
4 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 36.84 | 73.68 | 36.84 | 73.68
5 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | 7132455002 | Nos | 1 | 317.74 | 317.74 | 317.74 | 317.74
6 | PVC Insulation Tape | 7132476007 | Roll | 1 | 14.75 | 14.75 | 14.75 | 14.75 | RATE EXCLUDING G.S.T.
7 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 40 | 40 | 40 | 40
8 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
9 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 2606.73 |  | 2364.93
10 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 2209.0932 |  | 2004.178 | NEW ROW ADDED
11 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 195.5048 | 0.075 | 177.3698 | Earlier name was - Incidental Charges @ 9%
12 | Labour Charges |  | Per Installation |  |  | 424.9502 |  | 424.9502
13 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 9, 11, 12 |  |  |  |  | 403.3981 |  | 370.9062
14 | Total Estimated Cost excluding GST (Row 10, 11, 12, 13) |  |  |  |  | 3232.9463 |  | 2977.4041
15 | Applicable CGST @ 9% on Row 14 |  |  |  | 0.09 | 290.9652 | 0.09 | 267.9664
16 | Applicable SGST @ 9% on Row 14 |  |  |  | 0.09 | 290.9652 | 0.09 | 267.9664
17 | Total Estimated Cost including GST (Row 10+11+12) |  |  |  |  | 3814.8766 |  | 3513.3369
18 | Cost for meter shifting of a Three Phase Consumer |  |  |  |  | 3814.8766 |  | 3513.3369
19 | Cost for meter shifting of a Three Phase Consumer (Round Off) |  |  |  |  | 3815 |  | 3513
Note on B18: Barun Chakraborty: Earlier name was - SUB TOTAL-1